## Convert cfm50 to cfm75
Phius Airtightness Pressure Conversion Calculator: CFM50 Pa to CFM75 Pa |  | Required input cells. |  | Calculated. |  | Threshold
|  | Pressurization | Depressurization
CFM75 | Converted air leakage in cubic feet per minute at 75 Pascals. | 4236.7144 | 4135.8983
CFM50 | Measured air leakage in cubic feet per minute at 50 Pascals. | 3219.7 | 3259.9
h | Flow exponent (from test result) If unknown, use 0.7. | 0.677 | 0.587
Building Surface Area (sf) |  | 52867.3 | 52867.3
Threshold (<5 stories)
Results |  | Pressurization | Depressurization | Average Result | PHIUS+ 2015 | Performance Path: PHIUS+ 2018, Phius 2021/2024 | Prescriptive Path: Phius 2021/2024
CFM75/sf | Converted air leakage in cubic feet per minute at 75 Pascals per square foot of envelope area. | 0.080139 | 0.078232 | 0.079185 | 0.08 | 0.08 | 0.053
CFM50/sf | Measured air leakage in cubic feet per minute at 50 Pascals per square foot of envelope area. | 0.060902 | 0.061662 | 0.061282 | 0.05 | 0.06 | 0.04

## Convert cfm75 to cfm50
Phius Airtightness Pressure Conversion Calculator: CFM75 Pa to CFM50 Pa |  | Required input cells. |  | Calculated. |  | Threshold
|  | Pressurization | Depressurization
CFM75 | Measured air leakage in cubic feet per minute at 75 Pascals. | 4237 | 4136
CFM50 | Converted air leakage in cubic feet per minute at 50 Pascals. | 3219.917 | 3259.9802
h | Flow exponent (from test result) If unknown, use 0.7. | 0.677 | 0.587
Building Surface Area (sf) |  | 52867.3 | 52867.3
Threshold (<5 stories)
Results |  | Pressurization | Depressurization | Average Result | PHIUS+ 2015 | Performance Path: PHIUS+ 2018, Phius 2021/2024 | Prescriptive Path: Phius 2021/2024
CFM75/sf | Meausred air leakage in cubic feet per minute at 75 Pascals per square foot of envelope area. | 0.080144 | 0.078234 | 0.079189 | 0.08 | 0.08 | 0.053
CFM50/sf | Converted air leakage in cubic feet per minute at 50 Pascals per square foot of envelope area. | 0.060906 | 0.061663 | 0.061285 | 0.05 | 0.06 | 0.04