## Cover Sheet
PHIUS+ Quality Control Workbook for Nonresidential Projects (v1.0 November 2020)
[10 empty] | AL Alabama | United States
| Project Name |  | Project Permit Date | PHIUS+ Project Registration # | PHIUS+ Verifier Name | Verifier Company Name | CPHC Name | CPHC Company Name | Yes | AK Alaska | Canada
[9 empty] | No | AS American Samoa | Mexico
| Street Address | City | State/Province | Zip Code | Country | Architect Company Name | General Contractor / Builder Company Name | General Contractor / Builder responsible Individual |  | AZ Arizona | Afghanistan
[9 empty] | Yes | AR Arkansas | Albania
| Functional Testing Agent hired by project? | Functional Testing Agent responsible Individual |  | HVAC Company name | HVAC responsible Individual | Ducted heating/cooling systems? |  | Functional Testing Agent meets EPA MFNC Eligibility criteria? | Heating/Cooling Only | CA California | Andorra
[8 empty] | Select value I9 | No | CT Connecticut | Angola
| Total # Buildings | Total # Stories per Building |  |  |  |  | Does solar energy provide >50% of DWH load? |  |  | DE Delaware | Anguilla
[8 empty] | Select value F7 |  | DC District of Columbia | Antigua & Barbuda
[10 empty] | FM Fed. States of Micronesia | Argentina
Welcome to the PHIUS+ Quality Control Workbook for Nonresidential and Mixed-Use Projects! Certification Criteria The PHIUS+ Certification process for nonresidential projects includes energy modeling and design consulting performed by a Certified Passive House Consultant (CPHC) to demonstrate compliance with PHIUS program energy performance metrics, as well as on-site verification of all critical project energy features by a Certified PHIUS+ Verifier. Additionally, nonresidential projects shall use the eligibility criteria for the EPA ENERGY STAR MULTI-FAMILY NEW CONSTRUCTION PROGRAM (MFNCP), EPA INDOOR airPLUS and DOE ZERO ENERGY READY HOMES (ZERH) programs and follow checklist requirements those programs.(1)(2). Nonresidential Projects shall be exempt from certifying under those programs however, the certification checklist criteria for these programs shall still be achieved in order to help ensure that Nonresidential projects seeking PHIUS+ Certification are not only energy efficient, but also a durable, comfortable and healthy buildings. For full program requirements, and clarification on which ESTAR program your project is eligble for, please see the PHIUS+ Certification Guidebook. | [9 empty] | FL Florida | Armenia
Using This Workbook The goal of this workbook is to create a single, organized data collection form that shall be used by PHIUS+ Raters/Verifiers to document required on-site verification measures that are required for PHIUS+ Certification for nonresidentail projects. As such, the workbook incorporates the various program requirements of the PHIUS+ certification process, including the best practices for building envelope design/installation, HVAC design/installation, domestic hot water distribution, moisture durability management, and indoor air quality. In addition, information regarding testing protocols, exceptions to requirements and links to outside information are included throughout the document using the red "comments" flags that are embedded at the top right of various cells in the workbook. This workbook shall be used for all nonresidential projects, regardless of size. Nonresidential buildings are typically certified through PHIUS as a single project. Nonresidential projects shall also follow the ESTAR MFNCP, IAP and ZERH certification protocol for all spaces within the project. PHIUS+ Certification requires checklists be documented for each space. The PHIUS+ Rater/Verifier shall discuss checklist documentation requirements with their QA Provider to determine what the Provider will require. | [9 empty] | GU Guam | Australia
There are six worksheets to complete (see the green tabs below). | [9 empty] | HI Hawaii | Azerbaijan
| Responsible parties for completing each workbook are listed here. | [8 empty] | IN Indiana | Bahamas, The
| Building Envelope |  | PHIUS+ Verifier | [6 empty] | IA Iowa | Bahrain
| Compartmentalization |  | PHIUS+ Verifier | [6 empty] | KS Kansas
| Ventilation | Ventilation | PHIUS+ Verifier | [7 empty] | Bangladesh
| Heat + Cool | Heat + Cool | HVAC Designer/Contractor, PHIUS+ Verifier | [6 empty] | KY Kentucky | Barbados
| DHW + Lights | DHW + Lights | PHIUS+ Verifier | [6 empty] | LA Louisiana | Belgium
| Appliances | Appliances | PHIUS+ Verifier | [6 empty] | ME Maine | Belize
| IAQ | IAQ | PHIUS+ Verifier | [6 empty] | MH Marshall Islands | Benin
Each checklist includes a column off to the right that is designed to assist Passive House designers and Certified Passive House Consultants. This area calls to attention in red with an exclamation mark ! particular requirements that must be considered during the design phase of a project. | [9 empty] | MA Massachusetts | Bhutan
Data entry cells (for the Rater, builder, HVAC contractor, or designer are in green. Calculation cells are in purple. Do not change the calculation cells! | [9 empty] | MI Michigan | Bolivia
PHIUS+ Raters are welcome to add their own custom sheets to this workbook for instance, to track project notes. | [9 empty] | MN Minnesota | Bosnia & Herzegovina
Questions regarding particular checklist items should be directed first to the PHIUS+ Rater for the project. For questions on the nuances of certifying mixed-use buildings under ESTAR, please contact the PHIUS+ QA/QC Manager at QA@passivehouse.us. For any and all question regarding the certification process for any project, please contact certification@passivehouse.us. | [9 empty] | MS Mississippi | Botswana
Workbook updates: | [9 empty] | MO Missouri | Brazil
DRAFT - August 2020, V1.0 - November 2020
[10 empty] | MT Montana | British Virgin Is.
Footnotes (1) Projects located outside of the United States, or in California or Alaska, will need to meet the same critieria, regardless of their configuration. | [10 empty] | Brunei
(2) Nonresidential Projects with a Building Permit date after 7-1-2021 will be required to follow the EPA Energy Star Multi-Family New Construction Program Certification Criteria.
[10 empty] | NE Nebraska | Bulgaria
[10 empty] | NV Nevada | Burkina Faso
[10 empty] | NH New Hampshire | Burma
[10 empty] | NJ New Jersey | Burundi
[10 empty] | NM New Mexico | Cambodia
[10 empty] | NY New York | Cameroon
[10 empty] | NC North Carolina | Cape Verde
[10 empty] | ND North Dakota | Cayman Islands
[10 empty] | MP Northern Mariana Is. | Central African Rep.
[10 empty] | OH Ohio | Chad
[10 empty] | OK Oklahoma | Chile
[10 empty] | OR Oregon | China
[10 empty] | PW Palau | Colombia
[10 empty] | PA Pennsylvania | Comoros
[10 empty] | PR Puerto Rico | Congo, Dem. Rep.
[10 empty] | RI Rhode Island | Congo, Repub. of the
[10 empty] | SC South Carolina | Cook Islands
[10 empty] | SD South Dakota | Costa Rica
[10 empty] | TN Tennessee | Cote d'Ivoire
[10 empty] | TX Texas | Croatia
[10 empty] | UT Utah | Cuba
[10 empty] | VT Vermont | Cyprus
[10 empty] | VA Virginia | Czech Republic
[10 empty] | VI Virgin Islands | Denmark
[10 empty] | WA Washington | Djibouti
[10 empty] | WV West Virginia | Dominica
[10 empty] | WI Wisconsin | Dominican Republic
[10 empty] | WY Wyoming | East Timor
[10 empty] | AB Alberta | Ecuador
[10 empty] | BC British Columbia | Egypt
[10 empty] | MB Manitoba | El Salvador
[10 empty] | NB New Brunswick | Equatorial Guinea
[10 empty] | NF Newfoundland | Eritrea
[10 empty] | NT Northwest Territories | Estonia
[10 empty] | NS Nova Scotia | Ethiopia
[10 empty] | ON Ontario | Faroe Islands
[10 empty] | PE Prince Edward Island | Fiji
[10 empty] | QC Quebec | Finland
[10 empty] | SK Saskatchewan | France
[10 empty] | YT Yukon | French Guiana
French Polynesia
Gabon
Gambia, The
Gaza Strip
Georgia
Germany
Ghana
Gibraltar
Greece
Greenland
Grenada
Guadeloupe
Guam
Guatemala
Guernsey
Guinea
Guinea-Bissau
Guyana
Haiti
Honduras
Hong Kong
Hungary
Iceland
India
Indonesia
Iran
Iraq
Ireland
Isle of Man
Israel
Italy
Jamaica
Japan
Jersey
Jordan
Kazakhstan
Kenya
Kiribati
Korea, North
Korea, South
Kuwait
Kyrgyzstan
Laos
Latvia
Lebanon
Lesotho
Liberia
Libya
Liechtenstein
Lithuania
Luxembourg
Macau
Macedonia
Madagascar
Malawi
Malaysia
Maldives
Mali
Malta
Marshall Islands
Martinique
Mauritania
Mauritius
Mayotte
Micronesia, Fed. St.
Moldova
Monaco
Mongolia
Montserrat
Morocco
Mozambique
Namibia
Nauru
Nepal
Netherlands
Netherlands Antilles
New Caledonia
New Zealand
Nicaragua
Niger
Nigeria
N. Mariana Islands
Norway
Oman
Pakistan
Palau
Panama
Papua New Guinea
Paraguay
Peru
Philippines
Poland
Portugal
Puerto Rico
Qatar
Reunion
Romania
Russia
Rwanda
Saint Helena
Saint Kitts & Nevis
Saint Lucia
St Pierre & Miquelon
Saint Vincent and the Grenadines
Samoa
San Marino
Sao Tome & Principe
Saudi Arabia
Senegal
Serbia
Seychelles
Sierra Leone
Singapore
Slovakia
Slovenia
Solomon Islands
Somalia
South Africa
Spain
Sri Lanka
Sudan
Suriname
Swaziland
Sweden
Switzerland
Syria
Taiwan
Tajikistan
Tanzania
Thailand
Togo
Tonga
Trinidad & Tobago
Tunisia
Turkey
Turkmenistan
Turks & Caicos Is
Tuvalu
Uganda
Ukraine
United Arab Emirates
United Kingdom
Uzbekistan
Vanuatu
Venezuela
Vietnam
Virgin Islands
Wallis and Futuna
West Bank
Western Sahara
Yemen
Zambia
Zimbabwe
Note on K11: AUTO-CALCULATED
Note on C18: In case of mixed-use projects

## Building Envelope
Building Envelope PHIUS+ On-site Quality Control
The Verifier is responsible for verifying all items on this worksheet For projects with multiple buildings that differ in their envelope configurations, please create a duplicate worksheet for each building in the project.
# | Item |  |  | Rater Verified | N/A
1 | Take as many exterior photos as needed to appropriately depict all building elevations and significant architectural features of building for documentation folder
2 | Take pictures of surrounding site on all sides of building
3 | Take representative pictures of all unique insulated assemblies and window/door installations
4 | Perform thorough IR scan of entire building from interior and exterior, including all common spaces, and document representative photos
5 | If installed, describe operable shading. Include photo/s in documentation folder
Verifier Notes:
6.1 | Drawings check - describe any significant variations in construction from the construction drawings and specifications (insulation, window sizes, window performance, fixed shading etc.)
Verifier Notes:
6.2 | Insulation R-value: All insulation R-values match those listed on architectural plans. If not, please describe in notes section below.
Verifier Notes:
7 | All insulated assemblies have achieved a RESNET Grade I cavity insulation level, or alternatively GII with continuous insulation.
8 | Framing inspection: Framing matches architectural plans. If not, please describe in notes section below.
Verifier Notes:
9 | Optional whole building preliminary blower door test (manual or automated test)
Square Footage of the Building Envelope
Building Net Volume
CFM50 test result - depressurization
CFM50/Shell area
ACH50 - depressurization
CFM50 test result - pressurization
CFM50/Shell area
ACH50 - pressurization
Average CFM50
Average CFM50/Shell area
Average ACH50
10 | Final whole building blower door test Multi-point test in accordance with ANSI/RESNET/ICC 380-2019 or ASTM E-779*
| Building is 5+ stories in height, of non-combustible construction (YES/NO) |  |  | NO |  | YES
| Square Footage of the Building Envelope |  |  |  |  | NO
Target Value (CFM50)
| Target Value (CFM50/Shell Area) |  |  | 0.06
Building Net Volume
CFM50 test result - depressurization (multi-point test)
CFM50/Shell area
ACH50 - depressurization
CFM50 test result - pressurization (multi-point test)
CFM50/Shell area
ACH50 - pressurization
Average CFM50
Average CFM50/Shell area
Average ACH50
*Note- Identify individual zones within building that are tested, if applicable. Use additional copies of this worksheet as needed to describe individual zones.
Note- Configuration of building tested and /or individual zones shall be described with respect to test setu-up. For example if any intentional or unintentiional openings are temporaily sealed for the test, please ensure they are in line with
the PHIUS+ Guidebook and air tightness testing procedures outlined in ANSI/RESNET/ICC 380-2019 or ASTM E-779
Note on D9: These photos are used to help verify the site shading reduction factors used by the CPHC
Note on D11: Follow RESNET Infrared inspection guidelines for minimum delta-T. Images should include walls, insulated ceilings, slabs, windows. Use picture in picture if camera has the capability. Enter "n/a" if conditions do not allow the minimum delta-T
Note on D18: Please see RESNET Standards Appendix A for information on insulation Grading
Note on D34: Automated multi-point testing using RESNET testing protocol, set up building according to RESNET standard, Chapter 8. See PHIUS+ Certification Packet, section 3.3. Include testing report/s in documentation folder
Note on D35: Non-combustible in this sense is construction that is not subject to mold and rot. This would mean no wood-based framing members or sheet goods, and no wood-based or paper-based insulation.

## Compartmentalization
Unit Compartmentalization PHIUS+ On-site Quality Control
Dwelling Unit Compartmentalization Test: Compartmentalization testing shall be performed to test air tightness of individual dwelling units. The test threshold shall be 0.3 CFM50 / sqft unit shell area, otherwise known as Envelope Leakage Ratio (ELR). Testing may be performed using RESNET Chapter 6 Sampling protocols, and may be performed in either depressurization or pressurization mode. Sampling is typically appropriate for projects of at least 30 or more dwelling units. Please discuss with your RESNET QA Provider and/or PHIUS to ensure they will support Sampling being applied to the project. Please document compartmentalization results below.
Testing protocol
Testing shall be performed following RESNET/ANSI Standard 380-2019 and RESNET Standards for Multifamily Energy Ratings.
| RESNET Standards: |  | https://www.resnet.us/wp-content/uploads/ANSIRESNETICC_380-2019_vf1.24.19_cover%5E0TOC-2.pdf
| RESNET MF Guidelines: |  | http://www.resnet.us/wp-content/uploads/archive/resblog/2019/01/ANSIRESNETICC301-2019_vf1.23.19.pdf
Sampling Documentation
| Total project dwelling units |  |  |  | # Units Initial Sampling qualifying set |  |  | 7 |  | # Sampling sets
Initial Sampling Qualifying Set
Unit 1 |  | Unit 2 |  | Unit 3 | Unit 4 |  | Unit 5 |  | Unit 6 |  | Unit 7
Unit # |  | Unit # |  | Unit # | Unit # |  | Unit # |  | Unit # |  | Unit #
Unit SFBE |  | Unit SFBE |  | Unit SFBE | Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE
CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa
ELR |  | ELR |  | ELR | ELR |  | ELR |  | ELR |  | ELR
Did any units fail (and had to be corrected) during Initial Sampling Qualifying Set? | [5 empty] | Yes | If yes, how many additional units were tested in Qualifying Set?
Unit X
Unit #
Unit SFBE
CFM@50 Pa
ELR
Based on number of Sample Sets listed above, create documentation of compartmentalization testing for each sample set. Typical Sampling Sets are comprised of 7 units. One unit is chosen at random within that Set to serve as the tested unit. If that unit passes the program threshold value, the entire Sample Set passes. If the initial tested unit does not pass, it must be corrected, and one additional unit within the Sample Set must be tested. If the 2nd tested unit passes, the remaining units pass. If the 2nd tested unit does not pass, it must be corrected and all additional units within the Sample Set must be tested. If any additional failure is observed within the Sample Set, sampling must be discontinued until an analysis is performed to determine the root cause. After the root-cause analysis, is performed, seven more units must be tested consecutively without incidence of failure to re-commence sampling. Please copy and paste the example Sample Set documentation sequentially below.
Sample Set 1
Unit 1 |  | Unit 2 |  | Unit 3 | Unit 4 |  | Unit 5 |  | Unit 6 |  | Unit 7
Unit # |  | Unit # |  | Unit # | Unit # |  | Unit # |  | Unit # |  | Unit #
Unit SFBE |  | Unit SFBE |  | Unit SFBE | Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE
CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa
ELR |  | ELR |  | ELR | ELR |  | ELR |  | ELR |  | ELR

## Ventilation
Ventilation PHIUS+ On-site Quality Control
The Verifier is responsible for verifying all ventilation items on this worksheet. Ventilation air volume measurements may be verified by a third-party air balancing contractor so long as the Verifier verifies a minimum of 10%, or 10 outlets, whichever is lower (but no less than 3). The items on this worksheet that pertain to commercial space ventilation & must be verified with an individual worksheet for each space. Alternatively, the Verifier has the option to use a Sampling protocol to verify ventilation criteria with prior approval from PHIUS Staff. Verifier shall be responsible for collecting air balance documentation for all ventilation systems, documenting the design ventilation rate and the final verified air balance rate.
1 | Ventilation System Installation | [9 empty] | Rater Verified | N/A
1.1 | System Type |  | Space specific, or shared? |  |  | Manufacturer |  | Model #
If shared, list units shared with
1.2 | Take photos of equipment for documentation folder | [15 empty] | HRV | Dwelling unit
1.3 | All ventilation air inlets located at least 10' ("stretched-string distance") from known contamination sources | [15 empty] | ERV | Shared
1.4 | Ventilation air inlets are at least 2' above grade and/or roof deck in climate zones 1-3 and at least 4' above grade and/or roof deck in climate zones 4-8, and are not obstructed by snow, plantings, outdoor equipment, or other material at the time of inspection | [15 empty] | Exhaust Only
1.5 | Ventilation air comes directly from outdoors, not from adjacent spaces, common spaces, garages, crawlspaces or attics | [15 empty] | Supply Only
1.6 | Outside air passes through a minimum MERV 8 filter prior to distribution | [15 empty] | Air Cycler
1.7 | Outside air filter is located to facilitate regular service
1.8 | Air-sealed, class 1 vapor retarder shall be installed over all air-permeable insulation (such as fiberglass duct wrap) on ventilation ducts connected to outside (Enter R-value)
1.9 | Provision must be made to supply fresh air to all critical interior areas. Dedicated ventilation ductwork is best practice. In the case of ventilation ductwork integrated with heating/cooling ducts, ERV should remain in balance under all fan speeds of the heating/cooling air handler, and said air handler fan must be designed to run continuously by default.
1.9a | Bedrooms are pressure balanced to achieve a Rater-measured pressure difference of no more than 1Pa with respect to the main body of the house/apartment when all bedroom doors are closed and just the ventilation system is operating at design speed
1.1 | Verifierr-measured bathroom exhaust rates meets one of the following: >=20cfm continuous or 50 cfm intermittent
1.11 | Verifier-measured kitchen exhaust rates meets one of the following: >=25cfm continuous, 100cfm intermittent for range hoods, or 5ACH based on kitchen volume
1.12 | If kitchen exhaust connected to ERV/HRV, register is min. 6' from cooktop, MERV 3 or washable mesh filter for trapping grease, and recirc hood over range
1.13 | Clothes dryer is a condensing dryer, heat pump dryer, or exhaust dryer with exhaust ducted to the outside
2 | Ventilation system airflow testing verification: Where ventilation system has independent ductwork for supply and/or exhaust, branch airflow testing is to be performed by PHIUS+ Verifier. | [5 empty] | Design (cfm) | Verified (cfm) | % +/- Design | +/- cfm Design | OK? | Room pressure difference | OK?
2.1 | "Design Airflow Rate - Maximum" supply at HRV/ERV
2.2 | "Design Airflow Rate - Maximum" exhaust at HRV/ERV
2.3 | Total supply and exhaust are at least 100% of design values and within 10% of each other?
2.4 | enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
Total of supply branches (for reference only)
2.5 | enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
Total of exhaust branches (for reference only)
2.6 | "Design Airflow Rate - Typical 24/7 operation" supply at HRV/ERV
2.7 | "Design Airflow Rate - Typical 24/7 operation" exhaust at HRV/ERV
2.8 | Total supply and exhaust are +/- 15% or 15 CFM design values and within 10% of each other?
2.9 | Measure power input (Watts) at typical 24/7 airflow setting
2.10 | Watt/cfm for final input into consultant's energy model
3 | Ventilation - Auxiliary Systems | [9 empty] | Rater Verified | N/A
3.1 | If installed, enter type of ERV/HRV defrost - electric, hot water loop from DHW tank, ground loop
3.2 | Project team has demonstrated the defrost control logic is set up properly
3.3 | Is there a ground loop ("brine loop") or earth tube installed?
| A | Enter loop length and approximate depth
| B | Measure loop pump power
| C | Project team has demonstrated the ground loop / earth tube control logic is set up properly
4 | Common Space Ventilation System Installation | [9 empty] | Rater Verified | N/A
4.1 | Verifier performed common space ventilation testing on all common space ventilation systems, or alternatively has collected air balancing documentation from HVAC Contractor or certified air balancing professional which documents the design and verified rate, runtime, and wattage.
4.2 | Verifier documented common space ventilation system information (List all installed ventilation systems)
| Common Space zone |  |  | System type | Manufacturer |  |  | Model #
| Common Space zone |  |  | System type | Manufacturer |  |  | Model #
| Common Space zone |  |  | System type | Manufacturer |  |  | Model #
| Common Space zone |  |  | System type | Manufacturer |  |  | Model #
| Common Space zone |  |  | System type | Manufacturer |  |  | Model #
| Common Space zone |  |  | System type | Manufacturer |  |  | Model #
| Common Space zone |  |  | System type | Manufacturer |  |  | Model #
| Common Space zone |  |  | System type | Manufacturer |  |  | Model #
(copy above line if more required to be documented)
Note on C10: examples of contamination sources include: plumbing vents, exhaust vents, combustion exhaust, vehicle exhaust. Exception: ventilation air inlets in the wall at least 3 ft. from clothes dryer exhaust or contamination sources exiting through the roof.
Note on AB23: Must be +/- 20% of design value or 5cfm, whichever is greater
Note on AD23: Must be no more than 3Pa pressure difference
Note on X24: This is typically the "Design Air Flow Rate" from cell G21 of the PHPP Ventilation sheet or from WUFI Passive
Note on X25: This is typically the "Design Air Flow Rate" from cell G21 of the PHPP Ventilation sheet or from WUFI Passive
Note on C28: Enter additional rows as needed
Note on C37: Enter additional rows as needed
Note on C54: This is to ensure the defrost system does not operate unnecessarily. This should be a simple check. If the ERV/HRV calls for defrost below 25F, then the project team should be able to show the Rater that the system is set up correctly.

## Heat + Cool
Heating + Cooling PHIUS+ On-site Quality Control
Complete form for each piece of heating/cooling equipment with air distribution. Additional heating/cooling checks listed for items 4 and beyond. For example, if each space has its own heat pump, complete one form for each system. Copy and past additional forms/sheets into this workbook as needed. Ducted heating/cooling air volume measurements may be verified by a third-party air balancing contractor so long as the Verifier verifies a minimum of 10% of or 10, outlets, whichever is lower (but no less than 3). The items on this worksheet that pertain to heating/cooling systems must be verified with an individual worksheet for each individual system (Example- roof top, central air handler). Alternatively, the Verifier has the option to use the RESNET Sampling protocol to verify the dwelling unit heating/cooling air volume measurement criteria. For common spaces,Verifier shall be responsible for collecting air balance documentation for all ventilation systems, documenting the design ventilation rate and the final verified air balance rate.
# | Item | [7 empty] | PHIUS+ Verifier Verified | HVAC Contractor Verified | N/A
1 | Heating/cooling equipment
1.1 | System type (split heat pump, water source heat pump, fan coil, furnace, hydronic, etc.)
1.2 | "Central" or "Per Apartment" distribution, ducted or ductless?
1.3 | Manufacturer + model #
1.4 | AHRI certificate and/or manufacturer's detailed specs for heating/cooling equipment are included in documentation folder
1.5 | Photos of equipment (including model numbers) are included in documentation folder
2 | Heating/Cooling Distribution - for ducted systems only
2.1 | Duct layout drawing, total system design airflow and branch design airflows are included in documentation folder
2.2 | Rater review of duct installation:
| A | Duct installation reasonably matches design layout
| B | Building cavities not used as supply or return ducts
2.3 | All return air passes through a minimum MERV 8 filter
2.4 | Filter access panel includes a gasket or comparable sealing mechanism
2.5 | Verifier has measured and documented the branch airflow balancing to be within specifications (the greater of +/- 20% or 25cfm of design value)
2.6 | Bedrooms are pressure balanced (N/A)
2.7 | Total system and branch airflow testing - to be performed by PHIUS+ Rater. Rater-conducted balancing is optional. |  | Design (cfm) | Verified (cfm) | % +/- Design | cfm +/- Design | OK? | Room pressure difference |  | OK?
|  | TOTAL System Airflow |  |  |  |  | NO
|  | enter supply branch name here |  |  |  | 0 | YES |  |  | YES |  | 0 | 25 | 25 | -25
|  | enter supply branch name here |  |  |  | 0 | YES |  |  | YES |  | 0 | 25 | 25 | -25
|  | enter supply branch name here |  |  |  | 0 | YES |  |  | YES |  | 0 | 25 | 25 | -25
|  | enter supply branch name here |  |  |  | 0 | YES |  |  | YES |  | 0 | 25 | 25 | -25
|  | enter supply branch name here |  |  |  | 0 | YES |  |  | YES |  | 0 | 25 | 25 | -25
|  | enter supply branch name here |  |  |  | 0 | YES |  |  | YES |  | 0 | 25 | 25 | -25
|  | enter supply branch name here |  |  |  | 0 | YES |  |  | YES |  | 0 | 25 | 25 | -25
3 | Controls + Electrical Measurements
3.1 | Fan - air flow is produced when thermostat is set to "fan on"
3.2 | Heated air flow is produced when thermostat is set to "heat"
3.3 | Cooling air flow is produced when thermostat is set to "cool"
4 | Combustion furnaces, boilers and/or water heaters located within the buildings' pressure boundary are sealed combustion appliances with both flue and combustion air pipes routed directly to building exteror
5 | Natural draft fireplaces are not installed
6 | Installed woodstoves have a combustion air inlet connected to the firebox
7 | Corrosion-resistant drain pan, properly sloped to drainage system is included with each HVAC component that produces condensate
8 | Heating/Cooling Distribution - Hydronics
8.1 | Pipe layout drawing + schedule showing pipe sizes and insulation is included in documentation folder
8.2 | Verifier review of pipe + pump installation:
| A | Pipe installation reasonably matches design layout
| B | Pipe insulation matches design specs
| C | Pump/s Manufacturer + Model #
| D | Is pump single speed or variable?
| E | Design hydronic loop flow rate (GPM)
| F | Measured hydronic loop flow rate (GPM)
| G | Measure pump power input
Note on AD26: TOTAL SYSTEM AIRFLOW: +/- 15% of design value BRANCHES: +/- 20% or 25cfm of the design value, whichever is greater
Note on AF26: For rooms with doors and supply airflow
Note on AH26: Must be no more than 3Pa pressure difference
Note on D27: insert additional rows as needed

## Hot Water
Domestic Hot Water (DHW) PHIUS+ On-site Quality Control- For Dwelling Units in Mixed Use Buildings Only
# | Item |  | Rater Verified
1 | Domestic Hot Water (DHW)
1.1 | Project team has provided DHW drawings with lengths, diameter and insulation specs
1.2 | Hot water pipe install generally matches the design (length, diameter and insulation)? Describe any differences below
Rater Notes:
1.3 | All hot water systems and associated pumps are verified to be accurate per project specifications
1.4 | DHW is "central system" or "individual apartment" systems?
1.4 | Recirculation system installed? If so, please describe
Hot water distribution temperature rise test: Highest volumetric plumbing run tested for temperature rise. No more than 0.6 Gal shall be emitted from the highest volumetric plumbing run with a temperature rise of 10 deg F. or, alternative path, with DWH meeting DOE EF/UEF requirements and Water Sense labeled faucets and shower heads installed, no more than 1.4 Gal shall be emitted from the highest volumetric plumbing run with a hot water temperature rise of 10 deg F. This test may be completed using sampling protocols as described earlier in this manual.
!
!
!
!
!
!
!
!

## Lighting & Electric Loads
Appliances, Lighting & Service Electric Loads PHIUS+ On-site Quality Control
# | Item |  |  | Rater Verified
1 | Appliances
1.1 | Type #1 Manufacturer + Model #
1.2 | Type #1 kWh/yr
1.3 | Type #1 - % of total installed appliance
1.4 | Type #2 Manufacturer + Model #
1.5 | Type #2 kWh/yr
1.6 | Type #2 - % of total installed appliance
1.7 | Type 1 & 2 - weighted average kWh/yr |  | 0
1.8 | PHIUS energy model input (kWh/day) |  | 0
2
2.1 | Type #1 Manufacturer + Model #
2.2 | Type #1 kWh/yr
2.3 | Type #1 - % of total installed appliance
2.4 | Type #2 Manufacturer + Model #
2.5 | Type #2 kWh/yr
2.6 | Type #2 - % of total installed appliance
2.7 | Type 1 & 2 - weighted average kWh/yr |  | 0
2.8 | PHIUS energy model input (kWh/day) |  | #DIV/0!
3
3.1 | Type #1 Manufacturer + Model #
3.2 | Type #1 kWh/yr
3.3 | Type #1 - % of total installed appliance
3.4 | Type #2 Manufacturer + Model #
3.5 | Type #2 kWh/yr
3.6 | Type #2 - % of total installed appliance
3.7 | Type 1 & 2 - weighted average kWh/yr
3.8 | PHIUS energy model input (kWh/day)
3.9
3.10
3.11 |  |  | 0
3.12 |  |  | 0
3.13 |  |  | 0
3.14 |  |  | 0
4
4.1 | Type #1 Manufacturer + Model #
4.2 | Type #1 kWh/yr
4.3 | Type #1 - % of total installed appliance
4.4 | Type #2 Manufacturer + Model #
4.5 | Type #2 kWh/yr
4.6 | Type #2 - % of total installed appliance
4.7 | Type 1 & 2 - weighted average kWh/yr
4.8 | PHIUS energy model input (kWh/day)
4.9
4.10
4.11 |  |  | TBD
4.12 |  |  | TBD
5 | Lighting
5.1 | PHIUS+ Verifier has reviewed lighting plan and lamp/fixture schedule
5.2 | Installed lighting matches lighting plan and lamp/fixture schedule - describe variations, if applicable
5.3 | Project meets requirements forcommon space lighting requirements of ENERGY STAR MFHR
6 | Major Service / Electric Loads
6.1 | Project team has provided PHIUS+ Verifier with detailed service mechanical / electrical equipment plan/schedule?
6.2 | Installed air handlers, pumps, motors, etc match the project plans/schedule?
6.3 | Describe variations
6.4 | PHIUS+ Verifier provided electrical commissioning reports from third-party balancing/commissioning agent with electrical measurements?
7 | Renewable Energy Systems
7.1 | Project team has installed a renewable energy system (take photos of system and any inverters)
7.2 | If no renewable energy system installed, project has completed provisions of DOE Zero Energy Ready Homes PV Ready Checklist

## IAQ
https://www.epa.gov/sites/production/files/2018-03/documents/indoor_airplus_fillable_verification_checklist.pdf
https://www.epa.gov/sites/production/files/2018-03/documents/indoor_airplus_construction_specifications.pdf
For Mixed Use Buildings- all items on the checklist apply to dwelling units.
For Commercial, non-residential spaces all items apply except Combustion Pollutants items 5.2, 5.3 and 5.4- follow PHIUS Guidebook for these items
X
| 2022-04-06 | 2022-04-06

## NOTES For MFNC Doc's
NOTES RELATED TO USE OF MFNC DOCUMENTS
For Mixed Use Buildings- Energy Star MFNC Program Requirements must be met for all Dwelling & Sleeping units. Dwelling & Sleeping Units are to be certified under the MFNC
For non-residential buildings and non-residential spaces within mixed use buildings, all items in the Energy Star MFNC shall apply, but certification under the Energy Star MFNC Program is not required
Please check the EPA Energy Star website for current version of the program documents before proceeding:
PROGRAM REQUIREMENTS:
https://www.energystar.gov/partner_resources/residential_new/homes_prog_reqs/multifamily_national_page
SUPPORTING DOCUMENTS:
Multifamily Workbook- The Energy Star MF Workbook is presented on the following worksheets for your use. Please check to see if EPA has issued any updates
Photo Documentation Guidance- for refernce. PHIUS encourages use of this guidance where appropriate
https://www.energystar.gov/sites/default/files/asset/document/ENERGY_STAR_MFNC_Photo_Documentation_Guidance.pdf
| 2022-04-06 | 2022-04-06

## ES Project Information
Introduction: | Insert general project information in this tab. This information will autopopulate tabs throughout the workbook. MROs can copy the summary table at the bottom of this page to into their reporting spreadsheet to submit projects to EPA.
Project Details
Project Name: |  |  | Permit Date:
Project Address: |  | City: |  | State:
Pathway: |  | Version: (Prescriptive and ERI Only)
Heating & Cooling Equipment Pathway:
Stories: |  | Climate Zone:
Project Square Feet: |  | Number of Units:
Market Sector: |  | Number of IAP Units:
Builder / Developer Details
Builder / Developer 1 Company Name: |  | Builder / Developer 1 Employee:
Builder / Developer 2 Company Name: |  | Builder / Developer 2 Employee:
Rater Details
Rater Company Name:
Rater Employee:
Other Professional Details
ASHRAE Modeler Company Name:
ASHRAE Modeler Employee:
Functional Testing Agent Company Name:
Functional Testing (FT) Agent Employee:
Licensed Professional Company Name: (Optional) .
Licensed Professional Employee: (Optional) .

## ES Must Correct Report
Instructions
ENERGY STAR Multifamily Workbook
Must Correct Report
Checklist Items to Correct |  | Checklist Comments
1a. Rater Design Checklist - Must Correct
Rater Design Checklist | Must Correct | Comments
1. Partnership Status | 0 | 0
1.1 Rater has verified and documented that builder or developer has an ENERGY STAR partnership agreement using www.energystar.gov/partnerlocator. Builder Name: __________________________ Developer Name: _______________________ | 0 | 0
1.2 ASHRAE Only: Rater has verified that modeler is listed in the online directory using www.energystar.gov/ASHRAEdirectory. Modeler name: ________________________________ (Not required for projects in California) | 0 | 0
2. High-Performance Fenestration | 0 | 0
2.1 Dwelling units: | 0 | 0
2.1.1 Prescriptive: Specified fenestration meets or exceeds ENERGY STAR MF Reference Design requirements. 5 | 0 | 0
2.1.2 ERI and ASHRAE Only: Specified fenestration meets or exceeds 2009 IECC residential requirements. 5 | 0 | 0
2.2 Common space: 2 | 0 | 0
2.2.1 ERI and Prescriptive: Specified fenestration meets or exceeds ENERGY STAR MF Reference Design requirements. 5 | 0 | 0
2.2.2 ASHRAE Only: Specified fenestration meets or exceeds 2009 IECC commercial requirements. 5 | 0 | 0
3. High-Performance Insulation | 0 | 0
3.1 Dwelling unit: | 0 | 0
3.1.1: Prescriptive: Specified ceiling 6, wall 7, and slab-on-grade insulation levels meet or exceed ENERGY STAR MF Reference Design requirements. 8, 9, 10 | 0 | 0
3.1.2: ERI and ASHRAE Only: Specified ceiling 6, wall 7, floor, and slab-on-grade insulation levels meet or exceed values from the “Group R” column in the 2009 IECC Commercial chapter. 8, 9, 10 | 0 | 0
3.2 Common space: 2 | 0 | 0
3.2.1 ERI and Prescriptive: Specified ceiling 6, wall 7, and slab-on-grade insulation levels meet or exceed ENERGY STAR MF Reference Design requirements. 8, 9, 10 | 0 | 0
3.2.2 ASHRAE Only: Specified ceiling 6, wall 7, floor, and slab-on-grade insulation levels meet or exceed the values from the "All Other" column in the 2009 IECC Commercial chapter. 8, 9, 10 | 0 | 0
4. Review of HVAC Design Report | 0 | 0
4a. Review of ANSI / RESNET / ACCA Std. 310 HVAC Design Report with ENERGY STAR MFNC Supplement 3 | 0 | 0
4a.1 HVAC design report compliant with ANSI / RESNET / ACCA Std. 310, with the ENERGY STAR MFNC supplement, collected for records, with no Items left blank. | 0 | 0
4a.2 ANSI / RESNET / ACCA Std. 310 Rater Design Review Checklist completed for applicable housing type, with all items marked, “Rater Verified”. | 0 | 0
4a.3 Prescriptive Path: Dwelling Unit Mechanical Ventilation is <150% of ASHRAE 62.2-2013 requirements. 11 | 0 | 0
4a.4 Total occupant gains do not exceed 645 Btuh per occupant. 12 | 0 | 0
4a.5 Non-occupant internal gains are less than 3,600 Btuh. | 0 | 0
4a.6 Cooling sizing % is within the cooling sizing limit selected by the HVAC designer. | 0 | 0
4b. Review of ENERGY STAR MFNC National HVAC Design Report (National HVAC Design Report Item # indicatd in parenthesis) | 0 | 0
4b.1 National HVAC Design Report collected for records, with no Items left blank. | 0 | 0
4b.2 National HVAC Design Report reviewed by Rater for the following parameters (National HVAC Design Report Item # indicated in parenthesis): | 0 | 0
4b.2.1 Prescriptive Path: Dwelling Unit Mechanical Ventilation (2.7) is <150% of ASHRAE 62.2-2013 requirements. 11 | 0 | 0
4b.2.2 Cooling season and heating season outdoor design temperatures used in loads (3.4) are within the limits defined for the State and County where the building will be built, or the designer has provided an allowance from EPA to use alternative values. All limits are published at www.energystar.gov/hvacdesigntemps. Note that revised (i.e., 2019 Edition) limits are required to be used for all HVAC Design Reports generated after 07/01/2020. 14 | 0 | 0
4b.2.3 Number of occupants used in loads (3.6) is within ± 2 of the dwelling unit to be certified and occupant gains (3.7) do not exceed 645 Btuh per occupant. 12 | 0 | 0
4b.2.4 Conditioned floor area used in loads (3.8) is between 100 sq. ft. smaller and 300 sq. ft. larger than the dwelling unit to be certified. 15 | 0 | 0
4b.2.5 Window area used in loads (3.9) is between 15 sq. ft. smaller and 60 sq. ft. larger than the dwelling unit to be certified, or for dwelling units to be certified with > 500 sq. ft. of window area, between 3% smaller and 12% larger. 16 | 0 | 0
4b.2.6 Predominant window SHGC used in loads (3.10) is within 0.1 of predominant value in the dwelling unit to be certified. 17 | 0 | 0
4b.2.7 Mechanical ventilation used in loads (3.12) is the same as the ventilation design (2.7) for the given unit plan. | 0 | 0
4b.2.8 Non-occupant internal gains (3.13) are less than 3,600 Btuh. | 0 | 0
4b.2.9 Sensible & total heat gain are documented (3.14, 3.16) for the orientation of the dwelling unit to be certified. 18 | 0 | 0
4b.2.10 Cooling sizing % (4.18) is within the cooling sizing limit (4.19) selected by the HVAC designer. | 0 | 0
5. Additional Construction Document Review | 0 | 0
5.1 Air Sealing: Review construction documents to verify that air-sealing details at assemblies adjacent to exterior and unconditioned spaces are represented which, at a minimum, demonstrate compliance with checklist items in Section 4 of the National Rater Field Checklist (noted with an asterisk below). Items 5.1.9 and 5.1.10 are not verified by the Rater in the field, but are recommended. | N/A | 0
5.1.1 Ducts, flues, shafts, plumbing, piping, wiring, exhaust fans, & other penetrations to unconditioned space sealed, with blocking / flashing as needed*. | N/A | 0
5.1.2 Recessed lighting fixtures adjacent to unconditioned space ICAT labeled and gasketed. Also, if in insulated ceiling without attic above, exterior surface of fixture insulated to ≥ R-10 in CZ 4-8*. | N/A | 0
5.1.3 Continuous top plate or blocking is at top of walls adjoining unconditioned space including at balloon-framed parapets, and sealed*. | N/A | 0
5.1.4 Drywall sealed to top plate at all unconditioned attic / wall interfaces using caulk, foam, drywall adhesive (but not other construction adhesives), or equivalent material. Either apply sealant directly between drywall and top plate or to the seam between the two from the attic above*. | N/A | 0
5.1.5 Rough opening around windows & exterior doors sealed*. 19 | N/A | 0
5.1.6 Assemblies that separate attached garages from occupiable space sealed and, also, an air barrier installed, sealed, and aligned with these assemblies*. 20 | N/A | 0
5.1.7 Attic access panels, roof hatches and drop-down stairs are gasketed (i.e., not caulked) or equipped with durable covers that are gasketed*. 21 | N/A | 0
5.1.8 Doors adjacent to unconditioned space (e.g., attics, garages, basements), ambient conditions, or a unit entrance to a corridor / stairwell, made substantially air-tight with doorsweep and weatherstripping or equivalent gasket*. | N/A | 0
5.1.9 Above-grade sill plates adjacent to conditioned space sealed to foundation or sub-floor. Gasket also placed beneath above-grade sill plate if resting atop concrete / masonry & adjacent to conditioned space. 22, 23 | N/A | 0
5.1.10 The gap between the common wall (e.g., the drywall shaft wall) and the structural framing between units sealed at all exterior boundaries. | N/A | 0
5.2 Dwelling Unit Compartmentalization | N/A | 0
5.2.1 Review construction documents to verify that air-sealing details 24 are represented such that air exchange between the dwelling unit and outside as well as the dwelling unit and other adjacent spaces is minimized and designed to achieve compartmentalization less than or equal to 0.30 CFM50 per square feet of dwelling unit enclosure area, following procedures in ANSI / RESNET / ICC Std. 380. | N/A | 0
5.2.2 Seal all spaces 5.1.1-5.1.10 on adiabatic unit enclosure assemblies. | N/A | 0
5.3 Prescriptive Path: Verify that Window-to-wall ratio ≤ 30%. 25 | N/A | 0
5.4 Verify that fully-aligned air barrier details are in compliance with checklist items in Section 2 of the National Rater Field Checklist. | N/A | 0
5.5 Verify that thermal bridging details are in compliance with checklist items in Section 3 of the National Rater Field Checklist. | N/A | 0
5.6 Verify that HVAC details are in compliance with checklist items in Sections 5 - 10 of the National Rater Field Checklist. | N/A | 0
5.6.1 Verify that HVAC design includes access and means to measure the dwelling-unit mechanical ventilation airflow rate. | N/A | 0
5.6.2 Verify that bedrooms with design airflow ≥ 150 CFM are specified with a combination of transfer grilles, jump ducts dedicated return ducts, and/or undercut doors to achieve a Rater-measured pressure differential ≥ -5 Pa and ≤ +5 Pa with respect to the main body of the dwelling unit when all air handlers are operating. | N/A | 0
5.6.3 Verify that Functional Testing Agent(s) hold credential required to complete the applicable sections of the National HVAC Functional Testing Checklist for all HVAC equipment in the building. For Path A, a Functional Testing Agent is not needed to complete Sections 2 and 3 for unitary HVAC systems serving dwelling units that will be verified and graded by the Rater. 26 | N/A | 0
5.7 Verify that Domestic Hot Water, Lighting, Appliances, Plumbing Fixtures, and Whole Building Utility Data Acquisition Strategy details are in compliance with checklist items in Sections 11 – 14 of the National Rater Field Checklist. | N/A | 0
1b. Rater Field Checklist - Must Correct
Rater Design Checklist | Must Correct | Notes/Comments
Thermal Enclosure System | 0 | 0
1. High-Performance Fenestration & Insulation | 0 | 0
1.1 Fenestration meets or exceeds specification in Items 2.1 and 2.2 of the National Rater Design Review Checklist. | 0 | 0
1.2 Insulation meets or exceeds levels specified in Items 3.1 and 3.2 of the National Rater Design Review Checklist. | 0 | 0
1.3 All insulation achieves Grade I install per ANSI / RESNET / ICC Std. 301. Alternatives in footnote 6. 6,7 | 0 | 0
1.4 Prescriptive Path: Window-to-wall ratio ≤ 30%. 8 | 0 | 0
1.5 Heated plenums in unconditioned space or ambient conditions must meet the following requirements: 9 | 0 | 0
1.5.1 Sides of plenum are an air barrier and insulated to ≥ R-3ci in CZ 1-4; ≥ R-5ci in CZ 5-6; ≥ R-7.5ci in CZ 7; ≥ R-9.5ci in CZ 8, AND; | 0 | 0
1.5.2 Insulation at top of plenum meets or exceeds the R-value for mass floors from the “All Other” column of Table 502.2(1) of 2009 IECC, AND; | 0 | 0
1.5.3 Bottom of plenum must have at least R-13 insulation. 10 | 0 | 0
1.6 Garages with space heating must meet the following requirements: 9 | 0 | 0
1.6.1 Insulation on above grade walls and walls on the first story below grade ≥ R-5ci in CZ 5-6; ≥ R-7.5ci in CZ 7; ≥ R-9.5ci in CZ 8, AND; | 0 | 0
1.6.2 Garage ceiling insulation meets or exceeds the R-value for mass floors from the “All Other” column of Table 502.2(1) of 2009 IECC. | 0 | 0
2. Fully-Aligned Air Barriers 11 At each insulated location below, a complete air barrier is provided that is fully aligned as follows: | 0 | 0
Ceilings: At interior or exterior horizontal surface of ceiling insulation in Climate Zones 1-3; at interior horizontal surface of ceiling insulation in Climate Zones 4-8. Also, at exterior vertical surface of ceiling insulation in all climate zones (e.g., using a wind baffle that extends to the full height of the insulation in every bay or a tabbed baffle in each bay with a soffit vent that prevents wind washing in adjacent bays). 12 | 0 | 0
2.1 Dropped ceilings / soffits below unconditioned attics, chase / dead space, and all other ceilings. | 0 | 0
Walls: At exterior vertical surface of wall insulation in all climate zones; also at interior vertical surface of wall insulation in Climate Zones 4-8. 13 | 0 | 0
2.2 Walls behind showers, tubs, staircases, and fireplaces. | 0 | 0
2.3 Architectural bump-outs, dead space, and all other exterior walls. | 0 | 0
Floors: At exterior vertical surface of floor insulation in all climate zones and, if over unconditioned space, also at interior horizontal surface including supports to ensure alignment. Alternatives in Footnotes 15 & 16. 14, 15, 16 | 0 | 0
2.4 Floors above garages, floors above unconditioned spaces, and cantilevered floors. | 0 | 0
2.5 All other floors adjoining unconditioned space (e.g., rim / band joists at exterior wall or at porch roof). | 0 | 0
3. Reduced Thermal Bridging | 0 | 0
3.1 For insulated ceilings with attic space above (i.e., non-cathedralized), Grade I insulation extends to the inside face of the exterior wall below and is ≥ R-21 in CZ 1-5; ≥ R-30 in CZ 6-8. 17 | 0 | 0
3.2 For insulated ceilings with attic space above, attic access panels and drop-down stairs insulated ≥ R-10 or equipped with durable ≥ R-10 cover. 18 | 0 | 0
3.3 Insulation beneath attic platforms (e.g., HVAC platforms, walkways) ≥ R-21 in CZ 1-5; ≥ R-30 in CZ 6-8. | 0 | 0
3.4 For slabs on grade in CZ 4-8, 100% of slab edge insulated to ≥ R-5 at the depth specified by Table 502.2(1) of the 2009 IECC and aligned with the thermal boundary of the walls. 19, 20 | 0 | 0
3.5 For elevated concrete slabs in CZ 4-8 (i.e., podiums and projected balconies, but not intermediate slab floor edges) 100% of the slab edge insulated to ≥ R-5. For podiums, insulation must be installed for the full height of the podium wall. Alternatives in Footnote 21. 21 | 0 | 0
3.6 For elevated concrete slabs in CZ 4-8 (i.e., podiums, but not intermediate floor slabs), floor insulation meets the U-factor specified in Table 502.1.2 of the 2009 IECC for Group R when dwelling units are above the slab, and for ‘All Other’ when common space is above the slab. 22 | 0 | 0
3.7 At above-grade walls and rim / band joists separating conditioned from unconditioned space, one of the following options used: 23, 26 | 0 | 0
3.7.1 Continuous rigid insulation, insulated siding, or combination of the two is ≥ R-3 in CZ 1-4; ≥ R-5 in CZ 5-8 24, 25, 26, 27; OR; | 0 | 0
3.7.2 Structural Insulated Panels OR; Insulated Concrete Forms OR; Double-wall framing OR; 24, 26, 28 | 0 | 0
3.7.3 Option only for wood-framed walls either in CZ 1-3 OR ≤ 3 stories: ‘advanced framing’ details including all of the Items below: 26, 29 | 0 | 0
3.7.3a Corners insulated ≥ R-6 to edge, 30 AND; | 0 | 0
3.7.3b Headers above windows & doors insulated ≥ R-3 for 2x4 framing or equivalent cavity width, and ≥ R-5 for all other assemblies (e.g., with 2x6 framing), 31 AND; | 0 | 0
3.7.3c Interior / exterior wall intersections insulated to same R-value as rest of exterior wall. 32 | 0 | 0
4. Air Sealing (Unless otherwise noted below, “sealed” indicates the use of caulk, foam, or equivalent material.) | 0 | 0
4.1 Ducts, flues, shafts, plumbing, piping, wiring, exhaust fans, & other penetrations to unconditioned space sealed, with blocking / flashing as needed. | 0 | 0
4.2 Recessed lighting fixtures adjacent to unconditioned space ICAT labeled and gasketed. Also, if in insulated ceiling without attic above, exterior surface of fixture insulated to ≥ R-10 in CZ 4-8. | 0 | 0
4.3 Continuous top plate or blocking is at top of walls adjoining unconditioned space including at balloon-framed parapets, and sealed. | 0 | 0
4.4 Drywall sealed to top plate at all unconditioned attic / wall interfaces using caulk, foam, drywall adhesive (but not other construction adhesives), or equivalent material. Either apply sealant directly between drywall and top plate or to the seam between the two from the attic above. | 0 | 0
4.5 Rough opening around windows & exterior doors sealed. 33 | 0 | 0
4.6 Assemblies that separate attached garages from occupiable space sealed and, also, an air barrier installed, sealed, and aligned with these assemblies. 34 | 0 | 0
4.7 Doors adjacent to unconditioned space (e.g., attics, garages, basements) or ambient conditions made substantially air-tight with doorsweep and weatherstripping or equivalent gasket. | 0 | 0
4.8 Attic access panels, roof hatches and drop-down stairs are gasketed (i.e., not caulked) or equipped with durable covers that are gasketed. 18 | 0 | 0
The following items must be additionally verified in dwelling units, to reduce air leakage between conditioned spaces. | 0 | 0
4.9 Doors serving as a unit entrance from a corridor / stairwell made substantially air-tight with doorsweep and weatherstripping or equivalent gasket. | 0 | 0
4.10 Rater-measured compartmentalization is no greater than 0.30 CFM50 per square feet of dwelling unit enclosure area, following procedures in ANSI / RESNET / ICC Std. 380. 35 | 0 | 0
4.10.1 For dwelling units with forced air distribution systems without ducted returns and located in a closet adjacent to unconditioned space, the Rater-measured pressure difference between the space containing the air handler and the conditioned space during the compartmentalization test is no greater than 5 Pa. 36 | 0 | 0
HVAC System 37 (HVAC Design Report Item # indicated in parenthesis) | 0 | 0
5. Heating & Cooling Equipment – Complete Path A -Dwelling Unit HVAC Grading OR Path B – Dwelling Unit HVAC Commissioning 38 | 0 | 0
Path A 39 | 0 | 0
5a.1 Blower fan volumetric airflow is Grade I or II per ANSI / RESNET / ACCA Std. 310 | 0 | 0
5a.2 Blower fan watt draw is Grade I or II per ANSI / RESNET / ACCA Std. 310 | 0 | 0
5a.3 Refrigerant charge is Grade I per ANSI / RESNET / ACCA Std. 310. See Footnote 40 for exemptions. 40 | 0 | 0
Path B | 0 | 0
5b.1 HVAC manufacturer & model number on installed equipment matches either of the following (check box): 41  National HVAC Design Report (4.6-4.9 & 4.25-4.26)  Written approval received from designer | 0 | 0
5b.2 External static pressure measured by Rater at contractor-provided test locations and documented below: 42 Return-Side External Static Pressure: ________IWC Supply-Side External Static Pressure: __________IWC | 0 | 0
5.4 Prescriptive Path: Heating and cooling equipment serving dwelling units and common spaces meet the efficiency levels specified in the Exhibit X. Electric resistance heating is not installed in dwelling units. | 0 | 0
5.5 ERI Path: Heating and cooling equipment serving common spaces, but not serving dwelling units, meet the efficiency levels specified in the Exhibit X. See Exhibit X for restrictions on electric resistance heating. | 0 | 0
5.6 National HVAC Functional Testing Checklist(s) collected prior to certification, with all HVAC systems in the building / project fully documented. Exception: Where credentialed HVAC Contractor(s) are completing the National HVAC Functional Testing Checklist, the checklist is not required to be collected for the systems they verify. 43 | 0 | 0
5.7 Rater has verified that Functional Testing Agent(s) (“FT Agent(s)”) completing the National HVAC Functional Testing Checklist(s), hold(s) one of the required credentials and are listed on the appropriate online directory. 43 Credential: ______________________ “FT Agent” Company Name(s): _______________________ | 0 | 0
Equipment Controls | 0 | 0
5.8 All heating and cooling systems serving a dwelling unit have thermostatic controls within the dwelling unit which are not located on exterior walls. | 0 | 0
5.8.1 Prescriptive Path: Dwelling unit thermostats are programmable. | 0 | 0
5.9 Stair and elevator shaft vents equipped with motorized dampers that are capable of being automatically closed during normal building operation and are interlocked to open as required by fire and smoke detection systems. Dampers are verified to be closed at the time of inspection. | 0 | 0
5.10 Freeze protection systems, such as heat tracing of piping and heat exchangers, including self-regulating heat tracing, and garage / plenum heaters include automatic controls that are verified to shut off the systems when pipe wall or garage / plenum temperatures are above 40°F. | 0 | 0
5.10.1 Where heat tracing is installed for freeze-protection, controls must be based on pipe wall temperature and a minimum of R-3 pipe insulation is also required. | 0 | 0
5.11 Snow- and ice-melting systems include automatic controls that are verified to shut off the systems when the pavement temperature is above 50°F and no precipitation is falling, and an automatic or manual control is installed that is verified to shut off system when the outdoor temperature is above 40°F, so that the potential for snow or ice accumulation is negligible. | 0 | 0
Hydronic Distribution | 0 | 0
5.12 For hydronic distribution systems, all terminal heating and cooling distribution equipment are separated from the riser or distribution loop by a control valve or terminal distribution pump, so that heated or cooled fluid is not delivered to the dwelling unit distribution equipment when there is no call from the thermostat. | 0 | 0
5.13 Terminal units in hydronic distribution systems are equipped with pressure independent balancing valves or pressure independent control valves. | 0 | 0
5.14 Piping of a heating or cooling system is insulated in accordance with Item 4.40 on the National HVAC Design Report, including where passing through planks or any other penetrations. | 0 | 0
5.15 For circulating pumps serving hydronic heating or cooling systems with three-phase motors, 1 horsepower or larger, motors meet or exceed efficiency standards for NEMA Premium™ motors. If 5 horsepower or larger, also installed with variable frequency drives. | 0 | 0
6. Duct Quality Installation - Applies to Heating, Cooling, Ventilation, Exhaust, & Pressure Balancing Ducts, Unless Noted in Footnote. | 0 | 0
6.1 Ductwork installed without kinks, sharp bends, compressions, or excessive coiled flexible ductwork. 45 | 0 | 0
6.2 Bedrooms with a design supply airflow ≥ 150 CFM (per Item 5.2 on the National HVAC Design Report) pressure-balanced (e.g., using transfer grilles, jump ducts, dedicated return ducts, undercut doors) to achieve a Rater-measured pressure differential ≥ -5 Pa and ≤ +5 Pa with respect to the main body of the dwelling unit when all air handlers are operating. See Footnote 46 for test configuration. 46 | 0 | 0
6.3 All supply and return ducts in unconditioned space, including connections to trunk ducts, are insulated to ≥ R-6. 47 | 0 | 0
6.3.1 Prescriptive Path: Dwelling unit ductwork meets the location and insulation requirements specified in the ENERGY STAR Multifamily Reference Design. | 0 | 0
6.4 Rater-measured total duct leakage in dwelling units meets one of the following two options: 48, 49 | 0 | 0
6.4.1 Rough-in: Tested per allowances below, with air handler & all ducts, building cavities used as ducts, & duct boots installed. In addition, all duct boots sealed to finished surface, Rater-verified at final. 50 No ducted returns 36: The greater of ≤ 3 CFM25 per 100 sq. ft. of CFA or ≤ 30 CFM. Additionally, the Rater-measured pressure difference between the space containing the air handler and the conditioned space, with the air handler running at high speed, is ≤ 5 Pa. For systems > 1 ton, increase by 1 Pa per half ton. One or two ducted returns 36: The greater of ≤ 4 CFM25 per 100 sq. ft. of CFA or ≤ 40 CFM. Three or more ducted returns 36 : The greater of ≤ 6 CFM25 per 100 sq. ft. of CFA or ≤ 60 CFM. | 0 | 0
6.4.2 Final: Tested per allowances below, with the air handler & all ducts, building cavities used as ducts, duct boots, & register grilles atop the finished surface (e.g., drywall, floor) installed. 51 No ducted returns 36: The greater of ≤ 6 CFM25 per 100 sq. ft. of CFA or ≤ 60 CFM. Additionally, the Rater-measured pressure difference between the space containing the air handler and the conditioned space, with the air handler running at high speed, is ≤ 5 Pa. For systems > 1 ton, increase by 1 Pa per half ton. One or two ducted returns 36: The greater of ≤ 8 CFM25 per 100 sq. ft. of CFA or ≤ 80 CFM. Three or more ducted returns 36 : The greater of ≤ 12 CFM25 per 100 sq. ft. of CFA or ≤ 120 CFM. | 0 | 0
6.5 Townhouses only: Rater-measured duct leakage to the outside the greater of ≤ 4 CFM25 per 100 sq. ft. of CFA or ≤ 40 CFM25. 48, 52 | 0 | 0
6.6 Common Space: Supply, return, and exhaust ductwork and all plenums are sealed at all transverse joints, longitudinal seams, and duct wall penetrations with mastic or mastic tape | 0 | 0
6.7 Duct leakage of central exhaust systems that serve four or more dwelling units, meets one of the following two options: | 0 | 0
6.7.1 Rough-in: Tested including horizontal run outs, trunks, branches, and take-offs up to, but not including, the grilles, the leakage does not exceed 25% of exhaust fan flow. 53 | 0 | 0
6.7.2 Final: Tested inclusive of all ductwork between the fan and the grilles, the leakage does not exceed 30% of exhaust fan flow. 53 | 0 | 0
7. Dwelling-Unit & Common Space Mechanical Ventilation System | 0 | 0
7.1 Ventilation manufacturer & model number on installed equipment matches either of the following (check box): 41  National HVAC Design Report  Written approval received from designer | 0 | 0
7.2 Rater-measured ventilation rate is within either ± 15 CFM or ± 15% of dwelling unit design values (2.7), and meets or exceeds rates required by ASHRAE 62.2-2010. 54 | 0 | 0
7.3 Measured ventilation rate is within either ± 15 CFM or ± 15 % of common space design values (2.9), and meets or exceeds rates required by ASHRAE 62.1-2010 (2.8). 55 | 0 | 0
7.4 Townhouses only: A readily-accessible ventilation override control installed and also labeled if its function is not obvious (e.g., a label is required for a standalone wall switch, but not for a switch that’s on the ventilation equipment). | 0 | 0
7.5 No outdoor air intakes connected to return side of the dwelling unit HVAC system, unless controls are installed to operate intermittently & automatically based on a timer and to restrict intake when not in use (e.g., motorized damper). | 0 | 0
7.6 If located in the dwelling unit, system fan rated ≤ 3 sones if intermittent and ≤ 2 sone if continuous, or exempted. 56 | 0 | 0
7.7 If system utilizes the dwelling unit HVAC fan, then the intalled fan type is ECM / ICM (4.12), or the controls will reduce the standalone ventilation run-time by accounting for hours when the HVAC system is heating or cooling. | 0 | 0
7.8 In-unit bathroom fans or in-line fans are ENERGY STAR certified if used as part of the dwelling-unit mechanical ventilation system. 57 | 0 | 0
7.9 If central exhaust fans, ≤ 1 HP, are installed as part of the dwelling-unit mechanical ventilation system, then they are direct-drive, ECM, with variable speed controllers. If > 1 HP, they are installed with NEMATM Premium Motors. | 0 | 0
7.10 Air inlet locations (Complete if ventilation air inlet locations were installed (2.22, 2.23); otherwise check “N/A”): 58, 59 | 0 | 0
7.10.1 Inlet(s) pull ventilation air directly from outdoors and not from attic, crawlspace, garage, or adjacent dwelling unit. | 0 | 0
7.10.2 Inlet(s) are ≥ 2 ft. above grade or roof deck; ≥ 10 ft. of stretched-string distance from known contamination sources not exiting the roof, and ≥ 3 ft. distance from dryer exhausts and sources exiting the roof. 60 | 0 | 0
8. Local Mechanical Exhaust | 0 | 0
Dwelling Unit Mechanical exhaust - In each dwelling unit kitchen and bathroom, a system is installed that exhausts directly to the outdoors and meets one of the following Rater-measured airflow and manufacturer-rated sound level standards: 54, 61 | 0 | 0
Location | 0 | 0
8.1 Kitchen Airflow Continuous Rate: ≥ 5 ACH, based on kitchen volume 63, 64 Intermittent Rate 62: ≥ 100 CFM and, if not integrated with range, also ≥ 5 ACH based on kitchen volume 63, 64, 65 Sound Continuous Rate: Recommended: ≤ 1 sone Intermittent Rate 62: Recommended: ≤ 3 sones | 0 | 0
8.2 Bathroom Airflow Continuous Rate: ≥ 20 CFM Intermittent Rate 62: ≥ 50 CFM Sound Continuous Rate: Required: ≤ 2 sones Intermittent Rate 62: Recommended: ≤ 3 sones | 0 | 0
Common Space 2 and Garage Mechanical Exhaust | 0 | 0
8.3 Measured exhaust rates are ≥ ASHRAE 62.1 rates (2c). 55 | 0 | 0
8.4 Where a garage exhaust ventilation system is installed, it is equipped with controls that sense CO and NO2. | 0 | 0
9. Filtration | 0 | 0
9.1 MERV 6+ filter(s) installed in each dwelling unit ducted mech. System, serving an individual dwelling unit located to facilitate access & regular service by the occupant or building owner. 66 | 0 | 0
9.1.1 Filter access panel includes gasket and fits snugly against the exposed edge of filter when closed to prevent bypass. 67 | 0 | 0
9.1.2 All return air and mechanically supplied outdoor air passes through filter prior to conditioning. | 0 | 0
10. Combustion Appliances | 0 | 0
10.1 Furnaces, boilers, and water heaters located within the building’s pressure boundary are mechanically drafted or direct-vented. If mechanically drafted, the minimum volume of combustion air required for safe operation by the manufacturer and/or code shall be met or exceeded and make-up air sources must be mechanically closed when the combustion appliance is not in operation. Alternatives in Footnote 70. 68, 69, 70 | 0 | 0
10.2 Fireplaces located within the building’s pressure boundary are direct-vented. 68, 69 | 0 | 0
10.3 No unvented combustion appliances other than cooking ranges or ovens are located inside the building’s pressure boundary. For cooking ranges and ovens, local mechanical exhaust per Checklist Item 8.1 requirements must be met. 68 | 0 | 0
Other | 0 | 0
11. Domestic Hot Water | 0 | 0
11.1 Prescriptive Path: Hot water equipment rated in EF or UEF meet the efficiency levels specified in the ENERGY STAR Multifamily Reference Design. Boilers providing hot water are ≥85% Et. 71 | 0 | 0
11.2 ERI: For hot water equipment serving common spaces but not dwelling units nor shared laundry: where rated EF or UEF, meet the efficiency levels specified in the ENERGY STAR Multifamily Reference Design. Where rated in thermal efficiency, meet or exceed 85% Et. 71 | 0 | 0
11.3 For in-unit storage water heaters, AHRI Certificate confirms the presence of a heat trap. | 0 | 0
11.4 DHW piping located in the dwelling unit is insulated with a minimum of R-3. 72 | 0 | 0
11.5 Rater-measured delivery temperatures at faucets and showerheads do not exceed 125°F. 73 | 0 | 0
12. Lighting | 0 | 0
12.1 Common Space 2 Lighting Controls: | 0 | 0
12.1.1 ERI and Prescriptive Path: All common spaces 2 (including shared garages), except the building lobby and where automatic shutoff would endanger the safety of occupants, have occupancy sensors or automatic bi-level lighting controls installed and operation has been verified. | 0 | 0
12.1.2 ASHRAE path only: All common spaces 2 (including shared garages), except the building lobby, corridors, and stairwells and where automatic shutoff would endanger the safety of occupants, have occupancy sensors or automatic bi-level lighting controls installed and operation has been verified. | 0 | 0
12.2 Common Space 2 Lighting Power Density Maximum (except garages): 74 | 0 | 0
12.2.1 ERI and Prescriptive Path: Total installed lighting power for the combined common spaces 2 must not exceed ASHRAE 90.1-2007 allowances for those combined spaces, using the Space-by-Space or Building Area Method. See Footnote 75 for allowances. 75 | 0 | 0
12.2.2 ASHRAE path only: Total installed lighting power for the combined common spaces 2 must not exceed ASHRAE 90.1-2007 allowances for those combined spaces, using the Space-by-Space or Building Area Method, by more than 20%. See Footnote 75 for allowances. 75 | 0 | 0
12.3 Shared garages: Lighting power density does not exceed 0.24 W/ft2. | 0 | 0
12.4 Exterior lighting controls: Fixtures, including parking lot fixtures, must include automatic switching on timers or photocell controls except fixtures intended for 24-hour operation, required for security, or located on dwelling unit balconies. | 0 | 0
12.5 ERI Path: All exterior and common space lighting fixtures meet the efficiency requirements in the ENERGY STAR Multifamily Reference Design, except fixtures located on dwelling unit balconies. 76, 77 | 0 | 0
12.6 Prescriptive Path: All lighting fixtures (i.e., dwelling units, common spaces, and exterior) meet the efficiency requirements in the ENERGY STAR Multifamily Reference Design. 76, 77 | 0 | 0
12.7 Prescriptive Path: Dwelling unit overall in-unit lighting power density ≤ 0.75 W/ft2. When calculating overall lighting power density, use 1.1 W/ft2 where lighting is not installed. 74 | 0 | 0
13. Appliances, Ceiling Fans, and Plumbing Fixtures | 0 | 0
13.1 Prescriptive Path: Installed appliances and plumbing fixtures in dwelling units and common spaces meet the criteria in the ENERGY STAR Multifamily Reference Design. 78 | 0 | 0
13.2 ERI Path: Installed appliances and plumbing fixtures in common spaces, and not included in the ERI model, meet the criteria in the ENERGY STAR Multifamily Reference Design. 78 | 0 | 0
13.3 Prescriptive Path: Shower compartments with multiple fixtures cannot be operated simultaneously OR the total flow rate per shower compartment must not exceed 1.75 gallons per minute, as rated at 80 psi. | 0 | 0
14. Whole Building Energy Consumption Data Acquisition | 0 | 0
14.1 For buildings 50,000 ft2 and larger, a strategy that enables the collection of monthly or annual building-level energy consumption data (electricity, natural gas, chilled water, steam, fuel oil, propane, etc.) has been confirmed. 79 | 0 | 0
To refresh report:
1a. Rater Design Checklist
Right-click in cell A7 >Filter > Reapply
1b. Rater Field Checklist
Right-click in cell A72 >Filter > Reapply

## ES 1a. Rater Design Checklist
ALL PATHWAYS
Project Name: |  | Number of Units: |  | Permit Date:
Project Address: |  | City: |  | State:
Rater Design Review Checklist 1
|  | Must Correct | Rater 4 Verified | Comments | Column1 | Pathway Tag | Required Fields | Field Type | Additional Columns
| 1. Partnership Status |  |  |  |  | All | Required | Section Header
| Footnote 1. This Checklist applies to all dwelling units, sleeping units, common spaces 2, and garages (open or enclosed) in the building being certified, and where speciified, parking lots. These requirements do not apply to parking garages or lots where the cost of the energy use of the parking garage or lot is not the responsibility of the Builder/Developer, Building Owner, or Property Manager. This Checklist does not apply to commercial or retail spaces. This Checklist does not apply to common spaces that are located in buildings on the property without any dwelling or sleeping units. The term ‘sleeping unit’ refers to a room or space in which people sleep, which can also include permanent provisions for living, eating, and either sanitation or kitchen facilities but not both. Where the term ‘dwelling unit’ is used in this Checklist, the requirement is also required of ‘sleeping’ units. The term ‘building’ refers to a structure utilized or intended for supporting or sheltering occupancy for a residential purpose; a structure with no dwelling or sleeping units connected to a structure with dwelling or sleeping units by less than 10% of its exterior wall area is not to be included in the ‘building’. |  |  |  |  | All | Required | Footnote 1 - Checklist
| Footnote 4. The term ‘Rater’ refers to the person(s) completing the third-party verification required for certification. The person(s) shall: a) be a Certified Rater, Approved Inspector, or an equivalent designation as determined by a Verification Oversight Organization or Multifamily Review Organization and, b) have attended and successfully completed an EPA-recognized training class. See www.energystar.gov/mftraining. |  |  |  |  | All | Required | Footnote 4 - Checklist
| 1.1 Rater has verified and documented that builder or developer has an ENERGY STAR partnership agreement using www.energystar.gov/partnerlocator. Builder Name: __________________________ Developer Name: _______________________ |  |  |  |  | All | Required | Checklist
| 1.2 ASHRAE Only: Rater has verified that modeler is listed in the online directory using www.energystar.gov/ASHRAEdirectory. Modeler name: ________________________________ (Not required for projects in California) |  |  |  |  | ASHRAE | Required | Checklist
| 2. High-Performance Fenestration |  |  |  |  | All | Required | Section Header
| 2.1 Dwelling units: |  |  |  |  | All | Required | Checklist
| 2.1.1 Prescriptive: Specified fenestration meets or exceeds ENERGY STAR MF Reference Design requirements. 5 |  |  |  |  | Prescriptive | Required | Checklist
| Footnote 5. All windows, doors and skylights must meet or exceed the U-factor and SHGC requirements specified in the table below. If no NFRC rating is noted on the window or in product literature (e.g., for site-built fenestration), select the U-factor and SHGC value from Tables 4 and 10, respectively, in 2013 ASHRAE Handbook of Fundamentals, Chapter 15. Select the highest U-factor and SHGC value among the values listed for the known window characteristics (e.g., frame type, number of panes, glass color, and presence of low-e coating). Note that the U-factor requirement applies to all fenestration while the SHGC only applies to the glazed portion. SEE TABLE IN Tab 6. Fenestration The following exemptions apply: i. An area-weighted average of fenestration products shall be permitted to satisfy the U-factor requirements; ii. An area-weighted average of fenestration products ≥ 50% glazed shall be permitted to satisfy the SHGC requirements; and iii. 5% of all combined fenestration area (glazed and opaque) shall be exempt from the U-factor and SHGC requirements, and shall be excluded from area-weighted averages calculated using i) and ii), above. In PHIUS+ or PHI certified buildings, where triple-glazed window assemblies with thermal breaks / spacers between the panes are used, such windows meet the intent of Items 2.1 and 2.2 and shall be excluded when assessing compliance of i) through iii), above. |  |  |  |  | Prescriptive | Required | Footnote 5 - 2.1.1
| 2.1.2 ERI and ASHRAE Only: Specified fenestration meets or exceeds 2009 IECC residential requirements. 5 |  |  |  |  | ERI, ASHRAE | Required | Checklist
| Footnote 5. All windows, doors and skylights must meet or exceed the U-factor and SHGC requirements specified in the table below. If no NFRC rating is noted on the window or in product literature (e.g., for site-built fenestration), select the U-factor and SHGC value from Tables 4 and 10, respectively, in 2013 ASHRAE Handbook of Fundamentals, Chapter 15. Select the highest U-factor and SHGC value among the values listed for the known window characteristics (e.g., frame type, number of panes, glass color, and presence of low-e coating). Note that the U-factor requirement applies to all fenestration while the SHGC only applies to the glazed portion. SEE TABLE IN Tab 6. Fenestration The following exemptions apply: i. An area-weighted average of fenestration products shall be permitted to satisfy the U-factor requirements; ii. An area-weighted average of fenestration products ≥ 50% glazed shall be permitted to satisfy the SHGC requirements; and iii. 5% of all combined fenestration area (glazed and opaque) shall be exempt from the U-factor and SHGC requirements, and shall be excluded from area-weighted averages calculated using i) and ii), above. In PHIUS+ or PHI certified buildings, where triple-glazed window assemblies with thermal breaks / spacers between the panes are used, such windows meet the intent of Items 2.1 and 2.2 and shall be excluded when assessing compliance of i) through iii), above. |  |  |  |  | ERI, ASHRAE | Required | Footnote 5 - 2.1.2
| 2.2 Common space: 2 |  |  |  |  | All | Required | Checklist
| Footnote 2. The term ‘common space’ refers to any spaces in the building being certified that serve a function in support of the residential part of the building that is not part of a dwelling or sleeping unit. This includes spaces used by residents, such as corridors, stairs, lobbies, laundry rooms, exercise rooms, residential recreation rooms, and dining halls, as well as offices and other spaces used by building management, administration or maintenance in support of support the residents. |  |  |  |  | All | Required | Footnote 2 - 2.2
| 2.2.1 ERI and Prescriptive: Specified fenestration meets or exceeds ENERGY STAR MF Reference Design requirements. 5 |  |  |  |  | ERI, Prescriptive | Required | Checklist
| Footnote 5. All windows, doors and skylights must meet or exceed the U-factor and SHGC requirements specified in the table below. If no NFRC rating is noted on the window or in product literature (e.g., for site-built fenestration), select the U-factor and SHGC value from Tables 4 and 10, respectively, in 2013 ASHRAE Handbook of Fundamentals, Chapter 15. Select the highest U-factor and SHGC value among the values listed for the known window characteristics (e.g., frame type, number of panes, glass color, and presence of low-e coating). Note that the U-factor requirement applies to all fenestration while the SHGC only applies to the glazed portion. SEE TABLE IN Tab 6. Fenestration The following exemptions apply: i. An area-weighted average of fenestration products shall be permitted to satisfy the U-factor requirements; ii. An area-weighted average of fenestration products ≥ 50% glazed shall be permitted to satisfy the SHGC requirements; and iii. 5% of all combined fenestration area (glazed and opaque) shall be exempt from the U-factor and SHGC requirements, and shall be excluded from area-weighted averages calculated using i) and ii), above. In PHIUS+ or PHI certified buildings, where triple-glazed window assemblies with thermal breaks / spacers between the panes are used, such windows meet the intent of Items 2.1 and 2.2 and shall be excluded when assessing compliance of i) through iii), above. |  |  |  |  | ERI, Prescriptive | Required | Footnote 5 - 2.2.1
| 2.2.2 ASHRAE Only: Specified fenestration meets or exceeds 2009 IECC commercial requirements. 5 |  |  |  |  | ASHRAE | Required | Checklist
| Footnote 5. All windows, doors and skylights must meet or exceed the U-factor and SHGC requirements specified in the table below. If no NFRC rating is noted on the window or in product literature (e.g., for site-built fenestration), select the U-factor and SHGC value from Tables 4 and 10, respectively, in 2013 ASHRAE Handbook of Fundamentals, Chapter 15. Select the highest U-factor and SHGC value among the values listed for the known window characteristics (e.g., frame type, number of panes, glass color, and presence of low-e coating). Note that the U-factor requirement applies to all fenestration while the SHGC only applies to the glazed portion. SEE TABLE IN Tab 6. Fenestration The following exemptions apply: i. An area-weighted average of fenestration products shall be permitted to satisfy the U-factor requirements; ii. An area-weighted average of fenestration products ≥ 50% glazed shall be permitted to satisfy the SHGC requirements; and iii. 5% of all combined fenestration area (glazed and opaque) shall be exempt from the U-factor and SHGC requirements, and shall be excluded from area-weighted averages calculated using i) and ii), above. In PHIUS+ or PHI certified buildings, where triple-glazed window assemblies with thermal breaks / spacers between the panes are used, such windows meet the intent of Items 2.1 and 2.2 and shall be excluded when assessing compliance of i) through iii), above. |  |  |  |  | ASHRAE | Required | Footnote 5 - 2.2.2
| 3. High-Performance Insulation |  |  |  |  | All | Required | Section Header
| 3.1 Dwelling unit: |  |  |  |  | All | Required | Checklist
| 3.1.1: Prescriptive: Specified ceiling 6, wall 7, and slab-on-grade insulation levels meet or exceed ENERGY STAR MF Reference Design requirements. 8, 9, 10 |  |  |  |  | Prescriptive | Required | Checklist
| Footnote 6. Where the term ‘ceiling’ is used, the component insulation levels for “roofs” shall be used and does not apply to adiabatic ceilings, such as the insulated or uninsulated ceiling between two dwelling units in a multistory building. |  |  |  |  | Prescriptive | Required | Footnote 6 - 3.1.1
| Footnote 7. Items 3.1 and 3.2 are also applicable to walls that are adjacent to other buildings or adjacent to unconditioned spaces within the building. Where the wall assembly includes continuous insulation that is interrupted by fasteners or service openings, an assembly U-factor must be calculated. For the interrupted portions, the continuous insulation cannot contribute to the assembly U-factor and an overall U-factor shall be calculated based on an area weighted ratio. Thermally broken shelf-angles are exempt from de-rating. |  |  |  |  | Prescriptive | Required | Footnote 7 - 3.1.1
| Footnote 8. Specified levels shall meet or exceed the component insulation levels in 2009 IECC Table 502.2(1) or the table specified in the ENERGY STAR Multifamily Reference Design. The following exceptions apply: a. For ceilings with attic spaces, R-30 shall satisfy the requirement for R-38 and R-38 shall satisfy the requirement for R-49 wherever the full height of uncompressed insulation at the lower R-value extends over the wall top plate at the eaves. This exemption shall not apply if the alternative calculations in d) are used; b. For ceilings without attic spaces, that are not roofs with insulation above deck, R-30 shall satisfy the requirement for any required value above R-30 if the design of the roof / ceiling assembly does not provide sufficient space for the required insulation value. This exemption shall be limited to 20% of the total insulated ceiling area. This exemption shall not apply if the alternative calculations in d) are used; c. Common spaces following the ENERGY STAR Multifamily Reference Design should use the “All Other” column and also use the row of the table that best corresponds to the common space features. Unlike Prescriptive Path dwelling units, the common spaces do not need to follow the row corresponding to a wood-framed building. d. An alternative equivalent U-factor or total UA calculation may also be used to demonstrate compliance, as follows: An assembly with a U-factor equal or less than specified in 2009 IECC Table 502.1.2 complies. A total building thermal envelope UA that is less than or equal to the total UA resulting from the U-factors in Table 502.1.2 also complies. The performance of all components (i.e., roofs, walls, floors, slabs-on-grade, and fenestration) can be traded off using the UA approach. Note that Items 1.5, 1.6, and 3.1 through 3.7 of the National Rater Field Checklist shall be met regardless of the UA tradeoffs calculated. The UA calculation shall be done using a method consistent with the ASHRAE Handbook of Fundamentals and shall include the thermal bridging effects of framing materials. The calculation for a steel-frame envelope assembly shall use the ASHRAE zone method or a method providing equivalent results, and not a series-parallel path calculation method. |  |  |  |  | Prescriptive | Required | Footnote 8 - 3.1.1
| Footnote 9. Consistent with the 2009 IECC, slab edge insulation is only required for slab-on-grade floors with a floor surface less than 24 inches below grade. Slab-on-grade perimeter insulation shall extend to the top of the slab to provide a complete thermal break. If the top edge of the insulation is installed between the exterior wall and the edge of the interior slab, it shall be permitted to be cut at a 45-degree angle away from the exterior wall. Alternatively, the thermal break is permitted to be created using ≥ R-3 rigid insulation on top of an existing slab (e.g., in a building undergoing a gut rehabilitation). In such cases, up to 10% of the slab surface is permitted to not be insulated (e.g., for sleepers, for sill plates). Insulation installed on top of slab shall be covered by a durable floor surface (e.g., hardwood, tile, carpet). |  |  |  |  | Prescriptive | Required | Footnote 9 - 3.1.1
| Footnote 10. Where an insulated wall separates a garage, patio, porch, or other unconditioned space from the conditioned space of the building, slab perimeter insulation shall also be installed at this interface to provide a thermal break between the conditioned and unconditioned slab, if the slab is in contact with the ground at that interface. Where specific details cannot meet this requirement, partners shall provide the detail to EPA to request an exemption prior to the building’s certification. EPA will compile exempted details and work with industry to develop feasible details for use in future revisions to the program. A list of currently exempted details is available at: www.energystar.gov/slabedge. |  |  |  |  | Prescriptive | Required | Footnote 10 - 3.1.1
| 3.1.2: ERI and ASHRAE Only: Specified ceiling 6, wall 7, floor, and slab-on-grade insulation levels meet or exceed values from the “Group R” column in the 2009 IECC Commercial chapter. 8, 9, 10 |  |  |  |  | ERI, ASHRAE | Required | Checklist
| Footnote 6. Where the term ‘ceiling’ is used, the component insulation levels for “roofs” shall be used and does not apply to adiabatic ceilings, such as the insulated or uninsulated ceiling between two dwelling units in a multistory building. |  |  |  |  | ERI, ASHRAE | Required | Footnote 6 - 3.1.2
| Footnote 7. Items 3.1 and 3.2 are also applicable to walls that are adjacent to other buildings or adjacent to unconditioned spaces within the building. Where the wall assembly includes continuous insulation that is interrupted by fasteners or service openings, an assembly U-factor must be calculated. For the interrupted portions, the continuous insulation cannot contribute to the assembly U-factor and an overall U-factor shall be calculated based on an area weighted ratio. Thermally broken shelf-angles are exempt from de-rating. |  |  |  |  | ERI, ASHRAE | Required | Footnote 7 - 3.1.2
| Footnote 8. Specified levels shall meet or exceed the component insulation levels in 2009 IECC Table 502.2(1) or the table specified in the ENERGY STAR Multifamily Reference Design. The following exceptions apply: a. For ceilings with attic spaces, R-30 shall satisfy the requirement for R-38 and R-38 shall satisfy the requirement for R-49 wherever the full height of uncompressed insulation at the lower R-value extends over the wall top plate at the eaves. This exemption shall not apply if the alternative calculations in d) are used; b. For ceilings without attic spaces, that are not roofs with insulation above deck, R-30 shall satisfy the requirement for any required value above R-30 if the design of the roof / ceiling assembly does not provide sufficient space for the required insulation value. This exemption shall be limited to 20% of the total insulated ceiling area. This exemption shall not apply if the alternative calculations in d) are used; c. Common spaces following the ENERGY STAR Multifamily Reference Design should use the “All Other” column and also use the row of the table that best corresponds to the common space features. Unlike Prescriptive Path dwelling units, the common spaces do not need to follow the row corresponding to a wood-framed building. d. An alternative equivalent U-factor or total UA calculation may also be used to demonstrate compliance, as follows: An assembly with a U-factor equal or less than specified in 2009 IECC Table 502.1.2 complies. A total building thermal envelope UA that is less than or equal to the total UA resulting from the U-factors in Table 502.1.2 also complies. The performance of all components (i.e., roofs, walls, floors, slabs-on-grade, and fenestration) can be traded off using the UA approach. Note that Items 1.5, 1.6, and 3.1 through 3.7 of the National Rater Field Checklist shall be met regardless of the UA tradeoffs calculated. The UA calculation shall be done using a method consistent with the ASHRAE Handbook of Fundamentals and shall include the thermal bridging effects of framing materials. The calculation for a steel-frame envelope assembly shall use the ASHRAE zone method or a method providing equivalent results, and not a series-parallel path calculation method. |  |  |  |  | ERI, ASHRAE | Required | Footnote 8 - 3.1.2
| Footnote 9. Consistent with the 2009 IECC, slab edge insulation is only required for slab-on-grade floors with a floor surface less than 24 inches below grade. Slab-on-grade perimeter insulation shall extend to the top of the slab to provide a complete thermal break. If the top edge of the insulation is installed between the exterior wall and the edge of the interior slab, it shall be permitted to be cut at a 45-degree angle away from the exterior wall. Alternatively, the thermal break is permitted to be created using ≥ R-3 rigid insulation on top of an existing slab (e.g., in a building undergoing a gut rehabilitation). In such cases, up to 10% of the slab surface is permitted to not be insulated (e.g., for sleepers, for sill plates). Insulation installed on top of slab shall be covered by a durable floor surface (e.g., hardwood, tile, carpet). |  |  |  |  | ERI, ASHRAE | Required | Footnote 9 - 3.1.2
| Footnote 10. Where an insulated wall separates a garage, patio, porch, or other unconditioned space from the conditioned space of the building, slab perimeter insulation shall also be installed at this interface to provide a thermal break between the conditioned and unconditioned slab, if the slab is in contact with the ground at that interface. Where specific details cannot meet this requirement, partners shall provide the detail to EPA to request an exemption prior to the building’s certification. EPA will compile exempted details and work with industry to develop feasible details for use in future revisions to the program. A list of currently exempted details is available at: www.energystar.gov/slabedge. |  |  |  |  | ERI, ASHRAE | Required | Footnote 10 - 3.1.2
| 3.2 Common space: 2 |  |  |  |  | All | Required | Checklist
| Footnote 2. The term ‘common space’ refers to any spaces in the building being certified that serve a function in support of the residential part of the building that is not part of a dwelling or sleeping unit. This includes spaces used by residents, such as corridors, stairs, lobbies, laundry rooms, exercise rooms, residential recreation rooms, and dining halls, as well as offices and other spaces used by building management, administration or maintenance in support of the residents. |  |  |  |  | All | Required | Footnote 2 - 3.2
| 3.2.1 ERI and Prescriptive: Specified ceiling 6, wall 7, and slab-on-grade insulation levels meet or exceed ENERGY STAR MF Reference Design requirements. 8, 9, 10 |  |  |  |  | ERI, Prescriptive | Required | Checklist
| Footnote 6. Where the term ‘ceiling’ is used, the component insulation levels for “roofs” shall be used and does not apply to adiabatic ceilings, such as the insulated or uninsulated ceiling between two dwelling units in a multistory building. |  |  |  |  | ERI, Prescriptive | Required | Footnote 6 - 3.2.1
| Footnote 7. Items 3.1 and 3.2 are also applicable to walls that are adjacent to other buildings or adjacent to unconditioned spaces within the building. Where the wall assembly includes continuous insulation that is interrupted by fasteners or service openings, an assembly U-factor must be calculated. For the interrupted portions, the continuous insulation cannot contribute to the assembly U-factor and an overall U-factor shall be calculated based on an area weighted ratio. Thermally broken shelf-angles are exempt from de-rating. |  |  |  |  | ERI, Prescriptive | Required | Footnote 7 - 3.2.1
| Footnote 8. Specified levels shall meet or exceed the component insulation levels in 2009 IECC Table 502.2(1) or the table specified in the ENERGY STAR Multifamily Reference Design. The following exceptions apply: a. For ceilings with attic spaces, R-30 shall satisfy the requirement for R-38 and R-38 shall satisfy the requirement for R-49 wherever the full height of uncompressed insulation at the lower R-value extends over the wall top plate at the eaves. This exemption shall not apply if the alternative calculations in d) are used; b. For ceilings without attic spaces, that are not roofs with insulation above deck, R-30 shall satisfy the requirement for any required value above R-30 if the design of the roof / ceiling assembly does not provide sufficient space for the required insulation value. This exemption shall be limited to 20% of the total insulated ceiling area. This exemption shall not apply if the alternative calculations in d) are used; c. Common spaces following the ENERGY STAR Multifamily Reference Design should use the “All Other” column and also use the row of the table that best corresponds to the common space features. Unlike Prescriptive Path dwelling units, the common spaces do not need to follow the row corresponding to a wood-framed building. d. An alternative equivalent U-factor or total UA calculation may also be used to demonstrate compliance, as follows: An assembly with a U-factor equal or less than specified in 2009 IECC Table 502.1.2 complies. A total building thermal envelope UA that is less than or equal to the total UA resulting from the U-factors in Table 502.1.2 also complies. The performance of all components (i.e., roofs, walls, floors, slabs-on-grade, and fenestration) can be traded off using the UA approach. Note that Items 1.5, 1.6, and 3.1 through 3.7 of the National Rater Field Checklist shall be met regardless of the UA tradeoffs calculated. The UA calculation shall be done using a method consistent with the ASHRAE Handbook of Fundamentals and shall include the thermal bridging effects of framing materials. The calculation for a steel-frame envelope assembly shall use the ASHRAE zone method or a method providing equivalent results, and not a series-parallel path calculation method. |  |  |  |  | ERI, Prescriptive | Required | Footnote 8 - 3.2.1
| Footnote 9. Consistent with the 2009 IECC, slab edge insulation is only required for slab-on-grade floors with a floor surface less than 24 inches below grade. Slab-on-grade perimeter insulation shall extend to the top of the slab to provide a complete thermal break. If the top edge of the insulation is installed between the exterior wall and the edge of the interior slab, it shall be permitted to be cut at a 45-degree angle away from the exterior wall. Alternatively, the thermal break is permitted to be created using ≥ R-3 rigid insulation on top of an existing slab (e.g., in a building undergoing a gut rehabilitation). In such cases, up to 10% of the slab surface is permitted to not be insulated (e.g., for sleepers, for sill plates). Insulation installed on top of slab shall be covered by a durable floor surface (e.g., hardwood, tile, carpet). |  |  |  |  | ERI, Prescriptive | Required | Footnote 9 - 3.2.1
| Footnote 10. Where an insulated wall separates a garage, patio, porch, or other unconditioned space from the conditioned space of the building, slab perimeter insulation shall also be installed at this interface to provide a thermal break between the conditioned and unconditioned slab, if the slab is in contact with the ground at that interface. Where specific details cannot meet this requirement, partners shall provide the detail to EPA to request an exemption prior to the building’s certification. EPA will compile exempted details and work with industry to develop feasible details for use in future revisions to the program. A list of currently exempted details is available at: www.energystar.gov/slabedge. |  |  |  |  | ERI, Prescriptive | Required | Footnote 10 - 3.2.1
| 3.2.2 ASHRAE Only: Specified ceiling 6, wall 7, floor, and slab-on-grade insulation levels meet or exceed the values from the "All Other" column in the 2009 IECC Commercial chapter. 8, 9, 10 |  |  |  |  | ASHRAE | Required | Checklist
| Footnote 6. Where the term ‘ceiling’ is used, the component insulation levels for “roofs” shall be used and does not apply to adiabatic ceilings, such as the insulated or uninsulated ceiling between two dwelling units in a multistory building. |  |  |  |  | ASHRAE | Required | Footnote 6 - 3.2.2
| Footnote 7. Items 3.1 and 3.2 are also applicable to walls that are adjacent to other buildings or adjacent to unconditioned spaces within the building. Where the wall assembly includes continuous insulation that is interrupted by fasteners or service openings, an assembly U-factor must be calculated. For the interrupted portions, the continuous insulation cannot contribute to the assembly U-factor and an overall U-factor shall be calculated based on an area weighted ratio. Thermally broken shelf-angles are exempt from de-rating. |  |  |  |  | ASHRAE | Required | Footnote 7 - 3.2.2
| Footnote 8. Specified levels shall meet or exceed the component insulation levels in 2009 IECC Table 502.2(1) or the table specified in the ENERGY STAR Multifamily Reference Design. The following exceptions apply: a. For ceilings with attic spaces, R-30 shall satisfy the requirement for R-38 and R-38 shall satisfy the requirement for R-49 wherever the full height of uncompressed insulation at the lower R-value extends over the wall top plate at the eaves. This exemption shall not apply if the alternative calculations in d) are used; b. For ceilings without attic spaces, that are not roofs with insulation above deck, R-30 shall satisfy the requirement for any required value above R-30 if the design of the roof / ceiling assembly does not provide sufficient space for the required insulation value. This exemption shall be limited to 20% of the total insulated ceiling area. This exemption shall not apply if the alternative calculations in d) are used; c. Common spaces following the ENERGY STAR Multifamily Reference Design should use the “All Other” column and also use the row of the table that best corresponds to the common space features. Unlike Prescriptive Path dwelling units, the common spaces do not need to follow the row corresponding to a wood-framed building. d. An alternative equivalent U-factor or total UA calculation may also be used to demonstrate compliance, as follows: An assembly with a U-factor equal or less than specified in 2009 IECC Table 502.1.2 complies. A total building thermal envelope UA that is less than or equal to the total UA resulting from the U-factors in Table 502.1.2 also complies. The performance of all components (i.e., roofs, walls, floors, slabs-on-grade, and fenestration) can be traded off using the UA approach. Note that Items 1.5, 1.6, and 3.1 through 3.7 of the National Rater Field Checklist shall be met regardless of the UA tradeoffs calculated. The UA calculation shall be done using a method consistent with the ASHRAE Handbook of Fundamentals and shall include the thermal bridging effects of framing materials. The calculation for a steel-frame envelope assembly shall use the ASHRAE zone method or a method providing equivalent results, and not a series-parallel path calculation method. |  |  |  |  | ASHRAE | Required | Footnote 8 - 3.2.2
| Footnote 9. Consistent with the 2009 IECC, slab edge insulation is only required for slab-on-grade floors with a floor surface less than 24 inches below grade. Slab-on-grade perimeter insulation shall extend to the top of the slab to provide a complete thermal break. If the top edge of the insulation is installed between the exterior wall and the edge of the interior slab, it shall be permitted to be cut at a 45-degree angle away from the exterior wall. Alternatively, the thermal break is permitted to be created using ≥ R-3 rigid insulation on top of an existing slab (e.g., in a building undergoing a gut rehabilitation). In such cases, up to 10% of the slab surface is permitted to not be insulated (e.g., for sleepers, for sill plates). Insulation installed on top of slab shall be covered by a durable floor surface (e.g., hardwood, tile, carpet). |  |  |  |  | ASHRAE | Required | Footnote 9 - 3.2.2
| Footnote 10. Where an insulated wall separates a garage, patio, porch, or other unconditioned space from the conditioned space of the building, slab perimeter insulation shall also be installed at this interface to provide a thermal break between the conditioned and unconditioned slab, if the slab is in contact with the ground at that interface. Where specific details cannot meet this requirement, partners shall provide the detail to EPA to request an exemption prior to the building’s certification. EPA will compile exempted details and work with industry to develop feasible details for use in future revisions to the program. A list of currently exempted details is available at: www.energystar.gov/slabedge. |  |  |  |  | ASHRAE | Required | Footnote 10 - 3.2.2
| 4. Review of HVAC Design Report |  |  |  |  | All | Required | Section Header
| 4a. Review of ANSI / RESNET / ACCA Std. 310 HVAC Design Report with ENERGY STAR MFNC Supplement 3 |  |  |  |  | All | Required | Section Header | 4a
| Footnote 3. Path A – Dwelling Unit HVAC Grading shall not be used until an Effective Date has been defined by RESNET for ANSI / RESNET / ACCA Std. 310. Path A – Dwelling Unit HVAC Grading shall then use ANSI / RESNET / ACCA Std. 310 including all Addenda and Normative Appendices, with new versions and Addenda implemented according to the Effective Date and Transition Period End Date defined by RESNET. RESNET interpretations of Standard 310 shall also be followed. |  |  |  |  | All | Required | Footnote 3 - 4a | 4a
| 4a.1 HVAC design report compliant with ANSI / RESNET / ACCA Std. 310, with the ENERGY STAR MFNC supplement, collected for records, with no Items left blank. |  |  |  |  | All | Required | Checklist | 4a
| 4a.2 ANSI / RESNET / ACCA Std. 310 Rater Design Review Checklist completed for applicable housing type, with all items marked, “Rater Verified”. |  |  |  |  | All | Required | Checklist | 4a
| 4a.3 Prescriptive Path: Dwelling Unit Mechanical Ventilation is <150% of ASHRAE 62.2-2013 requirements. 11 |  |  |  |  | Prescriptive | Required | Checklist | 4a
| Footnote 11. Raters may use this table to determine the maximum ventilation rate allowed. REFER TO TABLE IN REFERENCE TABLES TAB |  |  |  |  | All | Required | Footnote 11 - 4a.3 | 4a
| 4a.4 Total occupant gains do not exceed 645 Btuh per occupant. 12 |  |  |  |  | All | Required | Checklist | 4a
| Footnote 12. To determine the number of occupants among all HVAC systems in the dwelling unit, calculate the number of bedrooms, as defined below, and add one. The number of occupants used in loads must be within ± 2 of the dwelling unit to be certified. A bedroom is defined by ANSI / RESNET / ICC Standard 301-2014 as a room or space 70 sq. ft. or greater size, with egress window and closet, used or intended to be used for sleeping. A “den”, “library”, or “home office” with a closet, egress window, and 70 sq. ft. or greater size or other similar rooms shall count as a bedroom, but living rooms and foyers shall not. An egress window, as defined in 2009 IRC Section R310, shall refer to any operable window that provides for a means of escape and access for rescue in the event of an emergency. The egress window definition has been summarized for convenience. The egress window shall: •have a sill height of not more than 44 inches above the floor; AND •have a minimum net clear opening of 5.7 sq. ft.; AND •have a minimum net clear opening height of 24 in.; AND •have a minimum net clear opening width of 20 in.; AND •be operational from the inside of the room without the use of keys, tools or special knowledge. |  |  |  |  | All | Required | Footnote 12 - 4a.4 | 4a
| 4a.5 Non-occupant internal gains are less than 3,600 Btuh. |  |  |  |  | All | Required | Checklist | 4a
| 4a.6 Cooling sizing % is within the cooling sizing limit selected by the HVAC designer. |  |  |  |  | All | Required | Checklist | 4a
| 4b. Review of ENERGY STAR MFNC National HVAC Design Report (National HVAC Design Report Item # indicatd in parenthesis) |  |  |  |  | All | Required | Section Header | 4b
| 4b.1 National HVAC Design Report collected for records, with no Items left blank. |  |  |  |  | All | Required | Checklist | 4b
| 4b.2 National HVAC Design Report reviewed by Rater for the following parameters (National HVAC Design Report Item # indicated in parenthesis): |  |  |  |  | All | Required | Checklist | 4b
| 4b.2.1 Prescriptive Path: Dwelling Unit Mechanical Ventilation (2.7) is <150% of ASHRAE 62.2-2013 requirements. 11 |  |  |  |  | Prescriptive | Required | Checklist | 4b
| Footnote 11. Raters may use this table to determine the maximum ventilation rate allowed. SEE TABLE IN REFERENCE TABLES TAB |  |  |  |  | Prescriptive | Required | Footnote 11 - 4b.2.1 | 4b
| 4b.2.2 Cooling season and heating season outdoor design temperatures used in loads (3.4) are within the limits defined for the State and County where the building will be built, or the designer has provided an allowance from EPA to use alternative values. All limits are published at www.energystar.gov/hvacdesigntemps. Note that revised (i.e., 2019 Edition) limits are required to be used for all HVAC Design Reports generated after 07/01/2020. 14 |  |  |  |  | All | Required | Checklist | 4b
| Footnote 14. Visit www.energystar.gov/hvacdesigntemps for the maximum cooling season design temperature and minimum heating season design temperature permitted and the process for a designer to obtain an allowance from EPA. The same design report is permitted to be used in other counties, as long as the design temperature limits in those other counties meet or exceed the cooling and heating season temperature limits for the county selected. For example, if Fauquier County, VA, is used for the load calculations, with a 1% cooling temperature limit of 93 °F, then the same report could be used in Fairfax County (which has a higher limit of 94 °F) but not in Arlington County (which has a lower limit of 92 °F). |  |  |  |  | All | Required | Footnote 14 - 4b.2.2 | 4b
| 4b.2.3 Number of occupants used in loads (3.6) is within ± 2 of the dwelling unit to be certified and occupant gains (3.7) do not exceed 645 Btuh per occupant. 12 |  |  |  |  | All | Required | Checklist | 4b
| Footnote 12. To determine the number of occupants among all HVAC systems in the dwelling unit, calculate the number of bedrooms, as defined below, and add one. The number of occupants used in loads must be within ± 2 of the dwelling unit to be certified. A bedroom is defined by ANSI / RESNET / ICC Standard 301-2014 as a room or space 70 sq. ft. or greater size, with egress window and closet, used or intended to be used for sleeping. A “den”, “library”, or “home office” with a closet, egress window, and 70 sq. ft. or greater size or other similar rooms shall count as a bedroom, but living rooms and foyers shall not. An egress window, as defined in 2009 IRC Section R310, shall refer to any operable window that provides for a means of escape and access for rescue in the event of an emergency. The egress window definition has been summarized for convenience. The egress window shall: •have a sill height of not more than 44 inches above the floor; AND •have a minimum net clear opening of 5.7 sq. ft.; AND •have a minimum net clear opening height of 24 in.; AND •have a minimum net clear opening width of 20 in.; AND •be operational from the inside of the room without the use of keys, tools or special knowledge. |  |  |  |  | All | Required | Footnote 12 - 4b.2.3 | 4b
| 4b.2.4 Conditioned floor area used in loads (3.8) is between 100 sq. ft. smaller and 300 sq. ft. larger than the dwelling unit to be certified. 15 |  |  |  |  | All | Required | Checklist | 4b
| Footnote 15. Conditioned Floor Area for the dwelling unit to be certified shall be calculated in accordance with the definition in ANSI / RESNET / ICC Standard 301-2019. |  |  |  |  | All | Required | Footnote 15 - 4b.2.4 | 4b
| 4b.2.5 Window area used in loads (3.9) is between 15 sq. ft. smaller and 60 sq. ft. larger than the dwelling unit to be certified, or for dwelling units to be certified with > 500 sq. ft. of window area, between 3% smaller and 12% larger. 16 |  |  |  |  | All | Required | Checklist | 4b
| Footnote 16. Window area for the dwelling unit to be certified shall be calculated in accordance with the on-site inspection protocol provided in Normative Appendix B of ANSI / RESNET / ICC Standard 301-2019. |  |  |  |  | All | Required | Footnote 16 - 4b.2.5 | 4b
| 4b.2.6 Predominant window SHGC used in loads (3.10) is within 0.1 of predominant value in the dwelling unit to be certified. 17 |  |  |  |  | All | Required | Checklist | 4b
| Footnote 17. “Predominant” is defined as the SHGC value used in the greatest amount of window area in the dwelling unit. |  |  |  |  | All | Required | Footnote 17 - 4b.2.6 | 4b
| 4b.2.7 Mechanical ventilation used in loads (3.12) is the same as the ventilation design (2.7) for the given unit plan. |  |  |  |  | All | Required | Checklist | 4b
| 4b.2.8 Non-occupant internal gains (3.13) are less than 3,600 Btuh. |  |  |  |  | All | Required | Checklist | 4b
| 4b.2.9 Sensible & total heat gain are documented (3.14, 3.16) for the orientation of the dwelling unit to be certified. 18 |  |  |  |  | All | Required | Checklist | 4b
| Footnote 18. Orientation represents the direction that the front door of the dwelling unit is facing. The designer is only required to document the loads for the orientation(s) that the dwelling unit might be built in. For example, if a unit plan will only be built in a specific orientation (e.g., facing South), then the designer only needs to document the loads for this one orientation. |  |  |  |  | All | Required | Footnote 18 - 4b.2.9 | 4b
| 4b.2.10 Cooling sizing % (4.18) is within the cooling sizing limit (4.19) selected by the HVAC designer. |  |  |  |  | All | Required | Checklist | 4b
| 5. Additional Construction Document Review |  |  |  |  | All | Optional | Section Header
| 5.1 Air Sealing: Review construction documents to verify that air-sealing details at assemblies adjacent to exterior and unconditioned spaces are represented which, at a minimum, demonstrate compliance with checklist items in Section 4 of the National Rater Field Checklist (noted with an asterisk below). Items 5.1.9 and 5.1.10 are not verified by the Rater in the field, but are recommended. | N/A |  |  |  | All | Optional | Checklist
| 5.1.1 Ducts, flues, shafts, plumbing, piping, wiring, exhaust fans, & other penetrations to unconditioned space sealed, with blocking / flashing as needed*. | N/A |  |  |  | All | Optional | Checklist
| 5.1.2 Recessed lighting fixtures adjacent to unconditioned space ICAT labeled and gasketed. Also, if in insulated ceiling without attic above, exterior surface of fixture insulated to ≥ R-10 in CZ 4-8*. | N/A |  |  |  | All | Optional | Checklist
| 5.1.3 Continuous top plate or blocking is at top of walls adjoining unconditioned space including at balloon-framed parapets, and sealed*. | N/A |  |  |  | All | Optional | Checklist
| 5.1.4 Drywall sealed to top plate at all unconditioned attic / wall interfaces using caulk, foam, drywall adhesive (but not other construction adhesives), or equivalent material. Either apply sealant directly between drywall and top plate or to the seam between the two from the attic above*. | N/A |  |  |  | All | Optional | Checklist
| 5.1.5 Rough opening around windows & exterior doors sealed*. 19 | N/A |  |  |  | All | Optional | Checklist
| Footnote 19. In Climate Zones 1 through 3, a continuous stucco cladding system sealed to windows and doors is permitted to be used in lieu of sealing rough openings with caulk or foam. |  |  |  |  | All | Optional | Footnote 19 - 5.1.5
| 5.1.6 Assemblies that separate attached garages from occupiable space sealed and, also, an air barrier installed, sealed, and aligned with these assemblies*. 20 | N/A |  |  |  | All | Optional | Checklist
| Footnote 20. For dwelling or sleeping units adjacent to garages, EPA recommends, but does not require, carbon monoxide (CO) alarms installed in a central location in the immediate vicinity of each separate sleeping zone and according to NFPA 720. |  |  |  |  | All | Optional | Footnote 20 - 5.1.6
| 5.1.7 Attic access panels, roof hatches and drop-down stairs are gasketed (i.e., not caulked) or equipped with durable covers that are gasketed*. 21 | N/A |  |  |  | All | Optional | Checklist
| Footnote 21. Examples of durable covers include, but are not limited to, pre-fabricated covers with integral insulation, rigid foam adhered to cover with adhesive, or batt insulation mechanically fastened to the cover (e.g., using bolts, metal wire, or metal strapping). |  |  |  |  | All | Optional | Footnote 21 - 5.1.7
| 5.1.8 Doors adjacent to unconditioned space (e.g., attics, garages, basements), ambient conditions, or a unit entrance to a corridor / stairwell, made substantially air-tight with doorsweep and weatherstripping or equivalent gasket*. | N/A |  |  |  | All | Optional | Checklist
| 5.1.9 Above-grade sill plates adjacent to conditioned space sealed to foundation or sub-floor. Gasket also placed beneath above-grade sill plate if resting atop concrete / masonry & adjacent to conditioned space. 22, 23 | N/A |  |  |  | All | Optional | Checklist
| Footnote 22. Existing sill plates (e.g., in a building undergoing a gut rehabilitation) on the interior side of structural masonry or monolithic walls may not be able to complete this Item. In addition, other existing sill plates resting atop concrete or masonry and adjacent to conditioned space can in lieu of using a gasket, be sealed with caulk, foam, or equivalent material at both the interior seam between the sill plate and the subfloor and the seam between the top of the sill plate and the sheathing. |  |  |  |  | All | Optional | Footnote 22 - 5.1.9
| Footnote 23. In Climate Zones 1 through 3, a continuous stucco cladding system adjacent to sill and bottom plates is an alternate option of sealing plates to foundation or sub-floor with caulk, foam, or equivalent material. |  |  |  |  | All | Optional | Footnote 23 - 5.1.9
| 5.1.10 The gap between the common wall (e.g., the drywall shaft wall) and the structural framing between units sealed at all exterior boundaries. | N/A |  |  |  | All | Optional | Checklist
| 5.2 Dwelling Unit Compartmentalization | N/A |  |  |  | All | Optional | Checklist
| 5.2.1 Review construction documents to verify that air-sealing details 24 are represented such that air exchange between the dwelling unit and outside as well as the dwelling unit and other adjacent spaces is minimized and designed to achieve compartmentalization less than or equal to 0.30 CFM50 per square feet of dwelling unit enclosure area, following procedures in ANSI / RESNET / ICC Std. 380. | N/A |  |  |  | All | Optional | Checklist
| Footnote 24. Recommended air leakage paths to be sealed include, but are not limited to the following: a. Plumbing penetrations, including those from water piping, drain waste and vent piping, HVAC piping, and gas line piping. b. Electrical penetrations, including those for receptacle outlets, lighting outlets / fixtures, communications wiring, thermostats, and smoke alarms. c. HVAC penetrations, including those for fans and for exhaust, supply, transfer, and return air ducts. d. Envelope penetrations, including at the intersection of baseboard trim and floor, at the intersection of walls and ceilings, around window trim and dwelling unit doors, including the door latch hole. |  |  |  |  | All | Optional | Footnote 24 - 5.2.1
| 5.2.2 Seal all spaces 5.1.1-5.1.10 on adiabatic unit enclosure assemblies. | N/A |  |  |  | All | Optional | Checklist
| 5.3 Prescriptive Path: Verify that Window-to-wall ratio ≤ 30%. 25 | N/A |  |  |  | Prescriptive | Optional | Checklist
| Footnote 25. Window-to-Wall ratio is taken as the sum of all window area divided by the total exterior above-grade wall area. All decorative glass and skylight window area contribute to the total window area to above-grade wall ratio (WWR). Spandrel sections of curtain wall systems contribute to the above-grade wall area. |  |  |  |  | Prescriptive | Optional | Footnote 25 - 5.3
| 5.4 Verify that fully-aligned air barrier details are in compliance with checklist items in Section 2 of the National Rater Field Checklist. | N/A |  |  |  | All | Optional | Checklist
| 5.5 Verify that thermal bridging details are in compliance with checklist items in Section 3 of the National Rater Field Checklist. | N/A |  |  |  | All | Optional | Checklist
| 5.6 Verify that HVAC details are in compliance with checklist items in Sections 5 - 10 of the National Rater Field Checklist. | N/A |  |  |  | All | Optional | Checklist
| 5.6.1 Verify that HVAC design includes access and means to measure the dwelling-unit mechanical ventilation airflow rate. | N/A |  |  |  | All | Optional | Checklist
| 5.6.2 Verify that bedrooms with design airflow ≥ 150 CFM are specified with a combination of transfer grilles, jump ducts dedicated return ducts, and/or undercut doors to achieve a Rater-measured pressure differential ≥ -5 Pa and ≤ +5 Pa with respect to the main body of the dwelling unit when all air handlers are operating. | N/A |  |  |  | All | Optional | Checklist
| 5.6.3 Verify that Functional Testing Agent(s) hold credential required to complete the applicable sections of the National HVAC Functional Testing Checklist for all HVAC equipment in the building. For Path A, a Functional Testing Agent is not needed to complete Sections 2 and 3 for unitary HVAC systems serving dwelling units that will be verified and graded by the Rater. 26 | N/A |  |  |  | All | Optional | Checklist
| Footnote 26. Functional Testing Agents must hold an approved credential, as listed at www.energystar.gov/ftas, or must be a representative of the Original Equipment Manufacturer (OEM), or a contractor credentialed by an HVAC Quality Installation Training and Oversight Organization (H-QUITO), if not completing Sections 6 and higher. Functional Testing Agents may not be the installing contractor unless they are a credentialed contractor. An explanation of the credentialing process and links to H-QUITOs, which maintain lists of credentialed contractors, can be found at www.energystar.gov/findhvac. A directory of other FT Agents can be found at www.energystar.gov/ftas. |  |  |  |  | All | Optional | Footnote 26 - 5.6.3
| 5.7 Verify that Domestic Hot Water, Lighting, Appliances, Plumbing Fixtures, and Whole Building Utility Data Acquisition Strategy details are in compliance with checklist items in Sections 11 – 14 of the National Rater Field Checklist. | N/A |  |  |  | All | Optional | Checklist
Rater Name: |  | Date of Review:
Rater Signature: |  | Rater Company Name:
SELECT PATHWAY
(Reset to All Paths)
(Reset to All Available)
Rater Design Checklist
(Reset All)
ERI
ASHRAE
Prescriptive
Required Only
Optional Only
Show all Footnotes
Hide all Footnotes
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Title 24: Dwelling Unit Models
Title 24: Whole Building Models
Hide Footnote(s)
Show Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)

## ES 1b. Rater Field Checklist
ALL PATHWAYS
Project Name: |  | Number of Units: |  | Permit Date:
Project Address: |  | City: |  | State:
Rater Field Review Checklist 1
Construction Verification
|  | Must Correct | Builder Verified 3 | LP Verified 39 | Rater Verified 4 | N/A 5 | Pathway Tag | Required Fields | Field Type | Additional Columns | Notes/Comments
| Footnote 1. This Checklist applies to all dwelling units, sleeping units, common spaces 2, and garages (open or enclosed) in the building being certified, and where specified, parking lots. These requirements do not apply to parking garages or lots where the cost of the energy use of the parking garage or lot is not the responsibility of the Builder/Developer, Building Owner or Property Manager. This Checklist does not apply to commercial or retail spaces. This Checklist does not apply to common spaces 2 that are located in buildings on the property without any dwelling or sleeping units. The term ‘sleeping unit’ refers to a room or space in which people sleep, which can also include permanent provisions for living, eating, and either sanitation or kitchen facilities but not both. Where the term ‘dwelling unit’ is used in this Checklist, the requirement is also required of ‘sleeping’ units. The term ‘building’ refers to a structure utilized or intended for supporting or sheltering occupancy for a residential purpose; a structure with no dwelling or sleeping units connected to a structure with dwelling or sleeping units by less than 10% of its exterior wall area is not to be included in the ‘building’. | [5 empty] | All | Required | Footnote 1 - Checklist
| Footnote 2. The term ‘common space’ refers to any spaces in the building being certified that serve a function in support of the residential part of the building that is not part of a dwelling or sleeping unit. This includes spaces used by residents, such as corridors, stairs, lobbies, laundry rooms, exercise rooms, residential recreation rooms, and dining halls, as well as offices and other spaces used by building management, administration or maintenance in support of the residents. | [5 empty] | All | Required | Footnote 2 - Checklist
| Footnote 3. At the discretion of the Rater, the builder or developer may verify up to eight items in Sections 1-4 of this Checklist. For the purpose of this Checklist, “Builder” represents either the builder or the developer. When exercised, the builder’s responsibility will be formally acknowledged by the builder, or their designated agent, signing off on the checklist for the item(s) that they verified. However, if a quality assurance review indicates that Items have not been successfully completed, the Rater will be responsible for facilitating corrective action. | [5 empty] | All | Required | Footnote 3 - Checklist
| Footnote 4. The term ‘Rater’ refers to the person(s) completing the third-party verification required for certification. The person(s) shall: a) be a Certified Rater, Approved Inspector, or an equivalent designation as determined by a Verification Oversight Organization or Multifamily Review Organization and, b) have attended and successfully completed an EPA-recognized training class. See www.energystar.gov/mftraining. | [5 empty] | All | Required | Footnote 4 - Checklist
| Footnote 5. The column titled “N/A,” which denotes items that are “not applicable,” should be used when the checklist Item is not present in the project or conflicts with local requirements. | [5 empty] | All | Required | Footnote 5 - Checklist
| Footnote 44. At the discretion of the Rater, a Licensed Professional (LP), (i.e., a Registered Architect or Professional Engineer in good standing and with a current license), may verify any of the items in Sections 5, 11, and 12 of this Checklist, where a checkbox is provided for “LP Verified”. When exercised, the LP’s responsibility will be formally acknowledged by the LP signing off on the checklist for the item(s) that they verified. However, if a quality assurance review indicates that Items have not been successfully completed, the Rater will be responsible for facilitating corrective action. | [5 empty] | All | Required | Footnote 44 - Checklist
| Thermal Enclosure System | [5 empty] | All | Required | Section Header
| 1. High-Performance Fenestration & Insulation | [5 empty] | All | Required | Section Header
| 1.1 Fenestration meets or exceeds specification in Items 2.1 and 2.2 of the National Rater Design Review Checklist. |  |  | - |  | - | All | Required | Checklist
| 1.2 Insulation meets or exceeds levels specified in Items 3.1 and 3.2 of the National Rater Design Review Checklist. |  |  | - |  | - | All | Required | Checklist
| 1.3 All insulation achieves Grade I install per ANSI / RESNET / ICC Std. 301. Alternatives in footnote 6. 6,7 |  |  | - |  | - | All | Required | Checklist
| Footnote 6. Two alternatives are provided: a) Grade II cavity insulation is permitted to be used for assemblies that contain a layer of continuous, air impermeable insulation ≥ R-3 in Climate Zones 1 to 4, ≥ R-5 in Climate Zones 5 to 8; b) Grade II batts are permitted to be used in floors if they fill the full width and depth of the floor cavity, even when compression occurs due to excess insulation, as long as the R-value of the batts has been appropriately assessed based on manufacturer guidance and the only defect preventing the insulation from achieving Grade I is the compression caused by the excess insulation. | [5 empty] | All | Required | Footnote 6 - 1.3
| Footnote 7. Ensure compliance with this requirement using ANSI / RESNET / ICC Std. 301 including all Addenda and Normative Appendices, with new versions and Addenda implemented according to the Effective Date and Transition Period End Date defined by RESNET. RESNET interpretations of Standard 301 shall also be followed. | [5 empty] | All | Required | Footnote 7 - 1.3
| 1.4 Prescriptive Path: Window-to-wall ratio ≤ 30%. 8 |  |  | - |  |  | Prescriptive | Required | Checklist
| Footnote 8. Window-to-Wall ratio is taken as the sum of all window area divided by the total exterior above-grade wall area. All decorative glass and skylight window area contribute to the total window area to above-grade wall ratio (WWR). Spandrel sections of curtain wall systems contribute to the above-grade wall area. | [5 empty] | Prescriptive | Required | Footnote 8 - 1.4
| 1.5 Heated plenums in unconditioned space or ambient conditions must meet the following requirements: 9 | [5 empty] | All | Required | Checklist
| Footnote 9. Compliance with Items 1.5 and 1.6 is not required for ASHRAE projects, but the energy used by the heating systems must be modeled following the requirements in the Simulation Guidelines, available at www.energystar.gov/mfguidance. | [5 empty] | All | Required | Footnote 9 - 1.5
| 1.5.1 Sides of plenum are an air barrier and insulated to ≥ R-3ci in CZ 1-4; ≥ R-5ci in CZ 5-6; ≥ R-7.5ci in CZ 7; ≥ R-9.5ci in CZ 8, AND; |  |  | - |  |  | All | Required | Checklist
| 1.5.2 Insulation at top of plenum meets or exceeds the R-value for mass floors from the “All Other” column of Table 502.2(1) of 2009 IECC, AND; |  |  | - |  |  | All | Required | Checklist
| 1.5.3 Bottom of plenum must have at least R-13 insulation. 10 |  |  | - |  |  | All | Required | Checklist
| Footnote 10. The bottom of the plenum is permitted to be suspended ceiling tiles or other non-air barrier material. If fiberglass insulation is installed, it must be paper-faced. | [5 empty] | All | Required | Footnote 10 - 1.5.3
| 1.6 Garages with space heating must meet the following requirements: 9 | [5 empty] | All | Required | Checklist
| Footnote 9. Compliance with Items 1.5 and 1.6 is not required for ASHRAE projects, but the energy used by the heating systems must be modeled following the requirements in the Simulation Guidelines, available at www.energystar.gov/mfguidance. | [5 empty] | All | Required | Footnote 9 - 1.6
| 1.6.1 Insulation on above grade walls and walls on the first story below grade ≥ R-5ci in CZ 5-6; ≥ R-7.5ci in CZ 7; ≥ R-9.5ci in CZ 8, AND; |  |  | - |  |  | All | Required | Checklist
| 1.6.2 Garage ceiling insulation meets or exceeds the R-value for mass floors from the “All Other” column of Table 502.2(1) of 2009 IECC. |  |  | - |  |  | All | Required | Checklist
| 2. Fully-Aligned Air Barriers 11 At each insulated location below, a complete air barrier is provided that is fully aligned as follows: | [5 empty] | All | Required | Section Header
| Footnote 11. For purposes of this Checklist, an air barrier is defined as any durable solid material that blocks air flow between conditioned space and unconditioned space, including necessary sealing to block excessive air flow at edges and seams and adequate support to resist positive and negative pressures without displacement or damage. EPA recommends, but does not require, rigid air barriers. Open-cell or closed-cell foam shall have a finished thickness ≥ 5.5 in. or 1.5 in., respectively, to qualify as an air barrier unless the manufacturer indicates otherwise. If flexible air barriers such as house wrap are used, they shall be fully sealed at all seams and edges and supported using fasteners with caps or heads ≥ 1 in. diameter unless otherwise indicated by the manufacturer. Flexible air barriers shall not be made of kraft paper, paper-based products, or other materials that are easily torn. If polyethylene is used, its thickness shall be ≥ 6 mil. | [5 empty] | All | Required | Footnote 11 - 2
| Ceilings: At interior or exterior horizontal surface of ceiling insulation in Climate Zones 1-3; at interior horizontal surface of ceiling insulation in Climate Zones 4-8. Also, at exterior vertical surface of ceiling insulation in all climate zones (e.g., using a wind baffle that extends to the full height of the insulation in every bay or a tabbed baffle in each bay with a soffit vent that prevents wind washing in adjacent bays). 12 | [5 empty] | All | Required | Section Details
| Footnote 12. All insulated ceiling surfaces, regardless of slope (e.g., cathedral ceilings, tray ceilings, conditioned attic roof decks, flat ceilings, sloped ceilings), must meet the requirements for ceilings, unless the ceiling is adiabatic. | [5 empty] | All | Required | Footnote 12 - 2 Ceilings
| 2.1 Dropped ceilings / soffits below unconditioned attics, chase / dead space, and all other ceilings. |  |  | - |  |  | All | Required | Checklist
| Walls: At exterior vertical surface of wall insulation in all climate zones; also at interior vertical surface of wall insulation in Climate Zones 4-8. 13 | [5 empty] | All | Required | Section Details
| Footnote 13. All insulated vertical surfaces are considered walls (e.g., above and below grade exterior walls, knee walls) and must meet the air barrier requirements for walls. The following exceptions apply: air barriers recommended, but not required, in adiabatic walls; and, in Climate Zones 4 through 8, an air barrier at the interior vertical surface of insulation is recommended but not required in basement walls or crawlspace walls. For the purpose of these exceptions, a basement or crawlspace is a space for which ≥ 40% of the total gross wall area is below-grade. | [5 empty] | All | Required | Footnote 13 - 2 Walls
| 2.2 Walls behind showers, tubs, staircases, and fireplaces. |  |  | - |  |  | All | Required | Checklist
| 2.3 Architectural bump-outs, dead space, and all other exterior walls. |  |  | - |  | - | All | Required | Checklist
| Floors: At exterior vertical surface of floor insulation in all climate zones and, if over unconditioned space, also at interior horizontal surface including supports to ensure alignment. Alternatives in Footnotes 15 & 16. 14, 15, 16 | [5 empty] | All | Required | Section Details
| Footnote 14. EPA highly recommends, but does not require, an air barrier at the interior vertical surface of floor insulation in Climate Zones 4-8. | [5 empty] | All | Required | Footnote 14 - 2 Floors
| Footnote 15. Examples of supports necessary for permanent contact include staves for batt insulation or netting for blown-in insulation. Alternatively, supports are not required if batts fill the full depth of the floor cavity, even when compression occurs due to excess insulation, as long as the R-value of the batts has been appropriately assessed based on manufacturer guidance and the only defect preventing the insulation from achieving the required installation grade is the compression caused by the excess insulation. | [5 empty] | All | Required | Footnote 15 - 2 Floors
| Footnote 16. Alternatively, an air barrier is permitted to be installed at the exterior horizontal surface of the floor insulation if the insulation is installed in contact with this air barrier, the exterior vertical surfaces of the floor cavity are also insulated, and air barriers are included at the exterior vertical surfaces of this insulation. | [5 empty] | All | Required | Footnote 16 - 2 Floors
| 2.4 Floors above garages, floors above unconditioned spaces, and cantilevered floors. |  |  | - |  |  | All | Required | Checklist
| 2.5 All other floors adjoining unconditioned space (e.g., rim / band joists at exterior wall or at porch roof). |  |  | - |  |  | All | Required | Checklist
| 3. Reduced Thermal Bridging | [5 empty] | All | Required | Section Header
| 3.1 For insulated ceilings with attic space above (i.e., non-cathedralized), Grade I insulation extends to the inside face of the exterior wall below and is ≥ R-21 in CZ 1-5; ≥ R-30 in CZ 6-8. 17 |  |  | - |  |  | All | Required | Checklist
| Footnote 17. The minimum designated R-values must be achieved regardless of the trade-offs determined using an equivalent U-factor or UA alternative calculation. Note that if the minimum designated values are used, then higher insulation values may be needed elsewhere to meet Item 1.2. Also, note that these requirements can be met by using any available strategy, such as a raised-heel truss, alternate framing that provides adequate space, and / or high-density insulation. | [5 empty] | All | Required | Footnote 17 - 3.1
| 3.2 For insulated ceilings with attic space above, attic access panels and drop-down stairs insulated ≥ R-10 or equipped with durable ≥ R-10 cover. 18 |  |  | - |  |  | All | Required | Checklist
| Footnote 18. Examples of durable covers include, but are not limited to, pre-fabricated covers with integral insulation, rigid foam adhered to cover with adhesive, or batt insulation mechanically fastened to the cover (e.g., using bolts, metal wire, or metal strapping. Low-slope roof hatch covers to be insulated to R-5 minimum. | [5 empty] | All | Required | Footnote 18 - 3.2
| 3.3 Insulation beneath attic platforms (e.g., HVAC platforms, walkways) ≥ R-21 in CZ 1-5; ≥ R-30 in CZ 6-8. |  |  | - |  |  | All | Required | Checklist
| 3.4 For slabs on grade in CZ 4-8, 100% of slab edge insulated to ≥ R-5 at the depth specified by Table 502.2(1) of the 2009 IECC and aligned with the thermal boundary of the walls. 19, 20 |  |  | - |  |  | All | Required | Checklist
| Footnote 19. Consistent with the 2009 IECC, slab edge insulation is only required for slab-on-grade floors with a floor surface less than 24 inches below grade. Slab-on-grade perimeter insulation shall extend to the top of the slab to provide a complete thermal break. If the top edge of the insulation is installed between the exterior wall and the edge of the interior slab, it shall be permitted to be cut at a 45-degree angle away from the exterior wall. Alternatively, the thermal break is permitted to be created using ≥ R-3 rigid insulation on top of an existing slab (e.g., in a building undergoing a gut rehabilitation). In such cases, up to 10% of the slab surface is permitted to not be insulated (e.g., for sleepers, for sill plates). Insulation installed on top of slab shall be covered by a durable floor surface (e.g., hardwood, tile, carpet). | [5 empty] | All | Required | Footnote 19 - 3.4
| Footnote 20. Where an insulated wall separates a garage, patio, porch, or other unconditioned space from the conditioned space of the building, slab perimeter insulation shall also be installed at this interface to provide a thermal break between the conditioned and unconditioned slab, if the slab is in contact with the ground at that interface. Where specific details cannot meet this requirement, partners shall provide the detail to EPA to request an exemption prior to the building’s certification. EPA will compile exempted details and work with industry to develop feasible details for use in future revisions to the program. A list of currently exempted details is available at: www.energystar.gov/slabedge. | [5 empty] | All | Required | Footnote 20 - 3.4
| 3.5 For elevated concrete slabs in CZ 4-8 (i.e., podiums and projected balconies, but not intermediate slab floor edges) 100% of the slab edge insulated to ≥ R-5. For podiums, insulation must be installed for the full height of the podium wall. Alternatives in Footnote 21. 21 |  |  | - |  |  | All | Required | Checklist
| Footnote 21. For projected balconies, install a minimum of R-5 slab edge insulation to provide a thermal break between conditioned space and the unconditioned projected balcony slab. Alternatively, a UA calculation for the wall assembly that accounts for this uninsulated projected slab must be performed to demonstrate compliance with Item 1.2. For the purpose of this UA calculation, the area of the wall that is uninsulated due to the projected balcony is required to be calculated as 400% of that actual area. For example, for a projected balcony that is 20 feet wide, and has a thickness of 1 foot, the area to be used in the UA calculation is 80 ft2 instead of 20 ft2. The distance the balcony projects from the building is not used in this calculation. | [5 empty] | All | Required | Footnote 21 - 3.5
| 3.6 For elevated concrete slabs in CZ 4-8 (i.e., podiums, but not intermediate floor slabs), floor insulation meets the U-factor specified in Table 502.1.2 of the 2009 IECC for Group R when dwelling units are above the slab, and for ‘All Other’ when common space is above the slab. 22 |  |  | - |  |  | All | Required | Checklist
| Footnote 22. Whether insulating from above or below the slab, thermal breaks must be accounted for when determining compliance with floor U-factors. Where structural columns cause a discontinuity in the installed floor insulation, the UA calculation for the floor assembly must account for this uninsulated area of the floor. For the purpose of this UA calculation, the area of the floor that is uninsulated due to the structural columns is required to be calculated as 400% of that actual area. For example, for a 4’x4’ column, the area to be used in the UA calculation is 64 ft2 instead of 16 ft2. The height of the column is not used in this calculation. Alternatively, if the structural column is insulated for a minimum of 4 vertical feet, the modification to the UA calculation is not required, and the U-value of the column insulation shall be associated with the uninsulated area of the floor due to the column. | [5 empty] | All | Required | Footnote 22 - 3.6
| 3.7 At above-grade walls and rim / band joists separating conditioned from unconditioned space, one of the following options used: 23, 26 | [5 empty] | All | Required | Checklist
| Footnote 23. Item 3.7 is applicable to walls that are adjacent to other buildings or adjacent to unconditioned spaces within the building. Mass walls utilized as the thermal mass component of a passive solar design (e.g., a Trombe wall) are exempt from this Item. To be eligible for this exemption, the passive solar design shall be comprised of the following five components: an aperture or collector, an absorber, thermal mass, a distribution system, and a control system. For more information, see: www.energy.gov/sites/prod/files/guide_to_passive_solar_home_design.pdf. Mass walls that are not part of a passive solar design (e.g., CMU block or log home enclosure) shall either utilize the strategies outlined in Item 3.7 or the pathway in the assembly with the least thermal resistance, as determined using a method consistent with the 2013 ASHRAE Handbook of Fundamentals, shall provide ≥ 50% of the applicable assembly resistance, defined as the reciprocal of the mass wall equivalent U-factor in the 2009 IECC Table 502.1.2. Documentation identifying the pathway with the least thermal resistance and its resistance value shall be collected by the Rater and any Builder Verified or Rater Verified box under Item 3.7 shall be checked. | [5 empty] | All | Required | Footnote 23 - 3.7
| Footnote 26. Walls and rim / band joists using steel or other metal framing shall meet the reduced thermal bridging requirements by complying with Item 3.7.1 of the Checklist and may not demonstrate compliance using Item 3.7.2 or 3.7.3. | [5 empty] | All | Required | Footnote 26 - 3.7
| 3.7.1 Continuous rigid insulation, insulated siding, or combination of the two is ≥ R-3 in CZ 1-4; ≥ R-5 in CZ 5-8 24, 25, 26, 27; OR; |  |  | - |  |  | All | Required | Checklist
| Footnote 24. Up to 10% of the total exterior wall surface area is exempted from the reduced thermal bridging requirements to accommodate intentional designed details (e.g., architectural details such as thermal fins, wing walls, brick returns, stone window sills, metal panels, or masonry fireplaces; structural details, such as fasteners (e.g., shelf angles, metal clips, z-girts, brick ties), projected balconies, and service openings (e.g., PTACs or PTHPs), but not steel columns or wall area occupied by intermediate floors). It shall be apparent to the Rater that the exempted areas are intentional designed details or the exempted area shall be documented in a plan provided by the builder, architect, or engineer. The entire area of the wall area that is bypassed by the fastener must be used in the calculation. The Rater need not evaluate the necessity of the designed detail to certify the project. | [5 empty] | All | Required | Footnote 24 - 3.7.1
| Footnote 25. If used, insulated siding shall be attached directly over a water-resistive barrier and sheathing. In addition, it shall provide the required R-value as demonstrated through either testing in accordance with ASTM C 1363 or by attaining the required R-value at its minimum thickness. Insulated sheathing rated for water protection can be used as a water resistant barrier if all seams are taped and sealed. If non-insulated structural sheathing is used at corners, the advanced framing details listed in Item 3.7.3 shall be met for those wall sections. | [5 empty] | All | Required | Footnote 25 - 3.7.1
| Footnote 26. Walls and rim / band joists using steel or other metal framing shall meet the reduced thermal bridging requirements by complying with Item 3.7.1 of the Checklist and may not demonstrate compliance using Item 3.7.2 or 3.7.3. | [5 empty] | All | Required | Footnote 26 - 3.7.1
| Footnote 27. In a building undergoing a gut rehabilitation, continuous interior insulation may be used in lieu of continuous exterior rigid insulation or insulated siding. | [5 empty] | All | Required | Footnote 27 - 3.7.1
| 3.7.2 Structural Insulated Panels OR; Insulated Concrete Forms OR; Double-wall framing OR; 24, 26, 28 |  |  | - |  |  | All | Required | Checklist
| Footnote 24. Up to 10% of the total exterior wall surface area is exempted from the reduced thermal bridging requirements to accommodate intentional designed details (e.g., architectural details such as thermal fins, wing walls, brick returns, stone window sills, metal panels, or masonry fireplaces; structural details, such as fasteners (e.g., shelf angles, metal clips, z-girts, brick ties), projected balconies, and service openings (e.g., PTACs or PTHPs), but not steel columns or wall area occupied by intermediate floors). It shall be apparent to the Rater that the exempted areas are intentional designed details or the exempted area shall be documented in a plan provided by the builder, architect, or engineer. The entire area of the wall area that is bypassed by the fastener must be used in the calculation. The Rater need not evaluate the necessity of the designed detail to certify the project. | [5 empty] | All | Required | Footnote 24 - 3.7.2
| Footnote 26. Walls and rim / band joists using steel or other metal framing shall meet the reduced thermal bridging requirements by complying with Item 3.7.1 of the Checklist and may not demonstrate compliance using Item 3.7.2 or 3.7.3. | [5 empty] | All | Required | Footnote 26 - 3.7.2
| Footnote 28. Double-wall framing is defined as any framing method that ensures a continuous layer of insulation covering the studs to at least the R-value required in Item 3.7.1 of the Checklist, such as offset double-stud walls, aligned double-stud walls with continuous insulation between the adjacent stud faces, or single-stud walls with 2x2 or 2x3 cross-framing. In all cases, insulation shall fill the entire wall cavity from the interior to exterior sheathing except at windows, doors and other penetrations. | [5 empty] | All | Required | Footnote 28 - 3.7.2
| 3.7.3 Option only for wood-framed walls either in CZ 1-3 OR ≤ 3 stories: ‘advanced framing’ details including all of the Items below: 26, 29 | [5 empty] | All | Required | Checklist
| Footnote 26. Walls and rim / band joists using steel or other metal framing shall meet the reduced thermal bridging requirements by complying with Item 3.7.1 of the Checklist and may not demonstrate compliance using Item 3.7.2 or 3.7.3. | [5 empty] | All | Required | Footnote 26 - 3.7.3
| Footnote 29. Rim / band joists are exempt from this requirement. For the purpose of this requirement, “≤ 3 stories” refers to any portion of the building elevation where the wood-framed walls do not exceed 3 stories in height. Partial floors that meet the definition of a mezzanine or loft, as defined by the 2012 IRC, do not count as a story. All ‘advanced framing’ details shall be met except where the builder, architect, or engineer provides a framing plan that encompasses the details in question, indicating that structural members are required at these locations and including the rationale for these members (e.g., full-depth solid framing is required at wall corners or interior / exterior wall intersections for shear strength, a full-depth solid header is required above a window to transfer load to jacks studs, additional jack studs are required to support transferred loads, additional cripple studs are required to maintain on-center spacing, or stud spacing must be reduced to support multiple stories in a multifamily building). The Rater shall retain a copy of the detail and rationale for their records, but need not evaluate the rationale to certify the building. | [5 empty] | All | Required | Footnote 29 - 3.7.3
| 3.7.3a Corners insulated ≥ R-6 to edge, 30 AND; |  |  | - |  |  | All | Required | Checklist
| Footnote 30. All exterior corners shall be constructed to allow access for the installation of ≥ R-6 insulation that extends to the exterior wall sheathing. Examples of compliance options include standard-density insulation with alternative framing techniques, such as using three studs per corner, or high-density insulation (e.g., spray foam) with standard framing techniques. | [5 empty] | All | Required | Footnote 30 - 3.7.3a
| 3.7.3b Headers above windows & doors insulated ≥ R-3 for 2x4 framing or equivalent cavity width, and ≥ R-5 for all other assemblies (e.g., with 2x6 framing), 31 AND; |  |  | - |  |  | All | Required | Checklist
| Footnote 31. Compliance options include continuous rigid insulation sheathing, SIP headers, other prefabricated insulated headers, single-member or two-member headers with insulation either in between or on one side, or an equivalent assembly. R-value requirement refers to manufacturer’s nominal insulation value. | [5 empty] | All | Required | Footnote 31 - 3.7.3b
| 3.7.3c Interior / exterior wall intersections insulated to same R-value as rest of exterior wall. 32 |  |  | - |  |  | All | Required | Checklist
| Footnote 32. Insulation shall run behind interior / exterior wall intersections using ladder blocking, full length 2x6 or 1x6 furring behind the first partition stud, drywall clips, or other equivalent alternative. | [5 empty] | All | Required | Footnote 32 - 3.7.3c
| 4. Air Sealing (Unless otherwise noted below, “sealed” indicates the use of caulk, foam, or equivalent material.) | [5 empty] | All | Required | Section Header
| 4.1 Ducts, flues, shafts, plumbing, piping, wiring, exhaust fans, & other penetrations to unconditioned space sealed, with blocking / flashing as needed. |  |  | - |  | - | All | Required | Checklist
| 4.2 Recessed lighting fixtures adjacent to unconditioned space ICAT labeled and gasketed. Also, if in insulated ceiling without attic above, exterior surface of fixture insulated to ≥ R-10 in CZ 4-8. |  |  | - |  |  | All | Required | Checklist
| 4.3 Continuous top plate or blocking is at top of walls adjoining unconditioned space including at balloon-framed parapets, and sealed. |  |  | - |  |  | All | Required | Checklist
| 4.4 Drywall sealed to top plate at all unconditioned attic / wall interfaces using caulk, foam, drywall adhesive (but not other construction adhesives), or equivalent material. Either apply sealant directly between drywall and top plate or to the seam between the two from the attic above. |  |  | - |  |  | All | Required | Checklist
| 4.5 Rough opening around windows & exterior doors sealed. 33 |  |  | - |  | - | All | Required | Checklist
| Footnote 33. In Climate Zones 1 through 3, a continuous stucco cladding system sealed to windows and doors is permitted to be used in lieu of sealing rough openings with caulk or foam. | [5 empty] | All | Required | Footnote 33 - 4.5
| 4.6 Assemblies that separate attached garages from occupiable space sealed and, also, an air barrier installed, sealed, and aligned with these assemblies. 34 |  |  | - |  |  | All | Required | Checklist
| Footnote 34. For dwelling or sleeping units adjacent to garages, EPA recommends, but does not require, carbon monoxide (CO) alarms installed in a central location in the immediate vicinity of each separate sleeping zone and according to NFPA 720. | [5 empty] | All | Required | Footnote 34 - 4.6
| 4.7 Doors adjacent to unconditioned space (e.g., attics, garages, basements) or ambient conditions made substantially air-tight with doorsweep and weatherstripping or equivalent gasket. |  |  | - |  |  | All | Required | Checklist
| 4.8 Attic access panels, roof hatches and drop-down stairs are gasketed (i.e., not caulked) or equipped with durable covers that are gasketed. 18 |  |  | - |  |  | All | Required | Checklist
| Footnote 18. Examples of durable covers include, but are not limited to, pre-fabricated covers with integral insulation, rigid foam adhered to cover with adhesive, or batt insulation mechanically fastened to the cover (e.g., using bolts, metal wire, or metal strapping. Low-slope roof hatch covers to be insulated to R-5 minimum. | [5 empty] | All | Required | Footnote 18 - 4.8
| The following items must be additionally verified in dwelling units, to reduce air leakage between conditioned spaces. |  |  | - |  |  | All | Required | Section Details
| 4.9 Doors serving as a unit entrance from a corridor / stairwell made substantially air-tight with doorsweep and weatherstripping or equivalent gasket. |  |  | - |  |  | All | Required | Checklist
| 4.10 Rater-measured compartmentalization is no greater than 0.30 CFM50 per square feet of dwelling unit enclosure area, following procedures in ANSI / RESNET / ICC Std. 380. 35 |  | - | - |  |  | All | Required | Checklist
| Footnote 35. Where a sampling protocol is permitted in accordance with the National or California Program Requirements, at least 20% of the dwelling or sleeping units adjacant to a garage shall be selected for testing. | [5 empty] | All | Required | Footnote 35 - 4.10
| 4.10.1 For dwelling units with forced air distribution systems without ducted returns and located in a closet adjacent to unconditioned space, the Rater-measured pressure difference between the space containing the air handler and the conditioned space during the compartmentalization test is no greater than 5 Pa. 36 |  | - | - |  |  | All | Required | Checklist
| Footnote 36. A ‘ducted return’ is defined as a continuous duct made of sheet metal, duct board, or flexible duct that connects one or more return grilles to the return-side inlet of the air handler. Any other approach to convey air from return or transfer grille(s) to the air handler, such as the use of building cavities, does not constitute a ‘ducted return’. | [5 empty] | All | Required | Footnote 36 - 4.10.1
| HVAC System 37 (HVAC Design Report Item # indicated in parenthesis) | [5 empty] | All | Required | Section Header
| Footnote 37. This section of the Checklist is designed to meet the requirements of ASHRAE 62.1-2010 / 2013, ASHRAE 62.2-2010 / 2013, and ANSI / ACCA’s 5 QI-2015 protocol, thereby improving the performance of HVAC equipment in new multifamily buildings when compared to multifamily buildings built to minimum code. However, these features alone cannot prevent all ventilation, indoor air quality, and HVAC problems, (e.g., those caused by a lack of maintenance or by occupant behavior). Therefore, this Checklist is not a guarantee of proper ventilation, indoor air quality, or HVAC performance. | [5 empty] | All | Required | Footnote 37 - HVAC System
| 5. Heating & Cooling Equipment – Complete Path A -Dwelling Unit HVAC Grading OR Path B – Dwelling Unit HVAC Commissioning 38 | [5 empty] | All | Required | Section Header
| Footnote 38. Two paths are provided for satisfying the mandatory requirements for all certified buildings, Exhibit 2. Path A – Dwelling Unit HVAC Grading allows a Rater to utilize ANSI / RESNET / ACCA Std. 310 39, a standard for grading the installation of residential HVAC systems serving individual Dwelling Units and a Functional Testing Agent to verify common spaces and central systems. Path B – Functional Testing Agent utilizes a Functional Testing Agent for all systems. Either path may be selected, but all requirements within that path must be satisfied for the building to be certified. | [5 empty] | All | Required | Footnote 38 - 5
| Path A 39 | [5 empty] | All | Required | Section Details
| Footnote 39. Path A – Dwelling Unit HVAC Grading shall not be used until an Effective Date has been defined by RESNET for ANSI / RESNET / ACCA Std. 310. Path A – Dwelling Unit HVAC Grading shall then use ANSI / RESNET / ACCA Std. 310 including all Addenda and Normative Appendices, with new versions and Addenda implemented according to the Effective Date and Transition Period End Date defined by RESNET. RESNET interpretations of Standard 310 shall also be followed. For units following path A, all unitary HVAC Systems including air conditioners and heat pumps up to 65 kBtuh and furnaces up to 125 kBtuh serving individual dwelling or sleeping units shall comply with 5a.1 through 5a.3 for the building to be certified. | [5 empty] | All | Required | Footnote 39 - Path A
| 5a.1 Blower fan volumetric airflow is Grade I or II per ANSI / RESNET / ACCA Std. 310 |  | - |  |  |  | All | Required | Checklist
| 5a.2 Blower fan watt draw is Grade I or II per ANSI / RESNET / ACCA Std. 310 |  | - |  |  |  | All | Required | Checklist
| 5a.3 Refrigerant charge is Grade I per ANSI / RESNET / ACCA Std. 310. See Footnote 40 for exemptions. 40 |  | - |  |  |  | All | Required | Checklist
| Footnote 40. If the non-invasive procedure in ANSI / RESNET / ACCA Std. 310 is not permitted to be used during the final inspection of a unit (i.e., due to the equipment type or to outdoor air temperatures that do not meet the requirements of the non-invasive method), then the unit is permitted to be certified with a default refrigerant charge designation of Grade III. Note that in these circumstances, the weigh-in method procedure in ANSI / RESNET / ACCA Std. 310 may still be used to pursue a Grade I designation. | [5 empty] | All | Required | Footnote 40 - 5a.3
Path B
| 5b.1 HVAC manufacturer & model number on installed equipment matches either of the following (check box): 41  National HVAC Design Report (4.6-4.9 & 4.25-4.26)  Written approval received from designer |  | - | - |  |  | All | Required | Checklist
| Footnote 41. If installed equipment does not match the National HVAC Design Report, then prior to certification the Rater shall obtain written approval from the designer (e.g., email, updated National HVAC Design Report) confirming that the installed equipment meets the requirements of the National HVAC Design Report. In cases where the condenser unit is installed after the time of inspection by the Rater, the HVAC manufacturer and model numbers on installed equipment can be documented through the use of photographs provided by the Functional Testing Agent after installation is complete. | [5 empty] | All | Required | Footnote 41 - 5b.1
| 5b.2 External static pressure measured by Rater at contractor-provided test locations and documented below: 42 Return-Side External Static Pressure: ________IWC Supply-Side External Static Pressure: __________IWC | [5 empty] | All | Required | Checklist
| Footnote 42. The Rater shall measure and record the external static pressure in the return-side and supply-side of the system using the contractor-provided test locations. However, at this time, the Rater need not assess whether these values are within a specific range to certify the dwelling unit. | [5 empty] | All | Required | Footnote 42 - 5b.2
| 5.4 Prescriptive Path: Heating and cooling equipment serving dwelling units and common spaces meet the efficiency levels specified in the Exhibit X. Electric resistance heating is not installed in dwelling units. |  | - | - |  |  | Prescriptive | Required | Checklist
| 5.5 ERI Path: Heating and cooling equipment serving common spaces, but not serving dwelling units, meet the efficiency levels specified in the Exhibit X. See Exhibit X for restrictions on electric resistance heating. |  | - | - |  |  | ERI | Required | Checklist
| 5.6 National HVAC Functional Testing Checklist(s) collected prior to certification, with all HVAC systems in the building / project fully documented. Exception: Where credentialed HVAC Contractor(s) are completing the National HVAC Functional Testing Checklist, the checklist is not required to be collected for the systems they verify. 43 |  | - | - |  |  | All | Required | Checklist
| Footnote 43. Functional Testing Agents must hold an approved credential, as listed at www.energystar.gov/ftas, or must be a representative of the Original Equipment Manufacturer (OEM), or a contractor credentialed by an HVAC Quality Installation Training and Oversight Organization (H-QUITO), if not completing Sections 6 and higher. Functional Testing Agents may not be the installing contractor unless they are a credentialed contractor. An explanation of the credentialing process and links to H-QUITOs, which maintain lists of credentialed contractors, can be found at www.energystar.gov/findhvac. A directory of other FT Agents can be found at www.energystar.gov/ftas. For Path A, a Functional Testing Agent is not needed to complete Sections 2 and 3 for unitary HVAC systems serving dwelling units that will be verified and graded by the Rater. | [5 empty] | All | Required | Footnote 43 - 5.6
| 5.7 Rater has verified that Functional Testing Agent(s) (“FT Agent(s)”) completing the National HVAC Functional Testing Checklist(s), hold(s) one of the required credentials and are listed on the appropriate online directory. 43 Credential: ______________________ “FT Agent” Company Name(s): _______________________ |  | - | - |  |  | All | Required | Checklist
| Footnote 43. Functional Testing Agents must hold an approved credential, as listed at www.energystar.gov/ftas, or must be a representative of the Original Equipment Manufacturer (OEM), or a contractor credentialed by an HVAC Quality Installation Training and Oversight Organization (H-QUITO), if not completing Sections 6 and higher. Functional Testing Agents may not be the installing contractor unless they are a credentialed contractor. An explanation of the credentialing process and links to H-QUITOs, which maintain lists of credentialed contractors, can be found at www.energystar.gov/findhvac. A directory of other FT Agents can be found at www.energystar.gov/ftas. For Path A, a Functional Testing Agent is not needed to complete Sections 2 and 3 for unitary HVAC systems serving dwelling units that will be verified and graded by the Rater. | [5 empty] | All | Required | Footnote 43 - 5.7
| Equipment Controls | [5 empty] | All | Required | Section Details
| 5.8 All heating and cooling systems serving a dwelling unit have thermostatic controls within the dwelling unit which are not located on exterior walls. |  | - | - |  |  | All | Required | Checklist
| 5.8.1 Prescriptive Path: Dwelling unit thermostats are programmable. |  | - | - |  |  | Prescriptive | Required | Checklist
| 5.9 Stair and elevator shaft vents equipped with motorized dampers that are capable of being automatically closed during normal building operation and are interlocked to open as required by fire and smoke detection systems. Dampers are verified to be closed at the time of inspection. |  | - |  |  |  | All | Required | Checklist
| 5.10 Freeze protection systems, such as heat tracing of piping and heat exchangers, including self-regulating heat tracing, and garage / plenum heaters include automatic controls that are verified to shut off the systems when pipe wall or garage / plenum temperatures are above 40°F. |  | - |  |  |  | All | Required | Checklist
| 5.10.1 Where heat tracing is installed for freeze-protection, controls must be based on pipe wall temperature and a minimum of R-3 pipe insulation is also required. |  | - |  |  |  | All | Required | Checklist
| 5.11 Snow- and ice-melting systems include automatic controls that are verified to shut off the systems when the pavement temperature is above 50°F and no precipitation is falling, and an automatic or manual control is installed that is verified to shut off system when the outdoor temperature is above 40°F, so that the potential for snow or ice accumulation is negligible. |  | - |  |  |  | All | Required | Checklist
| Hydronic Distribution | [5 empty] | All | Required | Section Header
| 5.12 For hydronic distribution systems, all terminal heating and cooling distribution equipment are separated from the riser or distribution loop by a control valve or terminal distribution pump, so that heated or cooled fluid is not delivered to the dwelling unit distribution equipment when there is no call from the thermostat. |  | - |  |  |  | All | Required | Checklist
| 5.13 Terminal units in hydronic distribution systems are equipped with pressure independent balancing valves or pressure independent control valves. |  | - |  |  |  | All | Required | Checklist
| 5.14 Piping of a heating or cooling system is insulated in accordance with Item 4.40 on the National HVAC Design Report, including where passing through planks or any other penetrations. |  | - |  |  |  | All | Required | Checklist
| 5.15 For circulating pumps serving hydronic heating or cooling systems with three-phase motors, 1 horsepower or larger, motors meet or exceed efficiency standards for NEMA Premium™ motors. If 5 horsepower or larger, also installed with variable frequency drives. |  | - |  |  |  | All | Required | Checklist
| 6. Duct Quality Installation - Applies to Heating, Cooling, Ventilation, Exhaust, & Pressure Balancing Ducts, Unless Noted in Footnote. | [5 empty] | All | Required | Section Header
| 6.1 Ductwork installed without kinks, sharp bends, compressions, or excessive coiled flexible ductwork. 45 |  | - | - |  |  | All | Required | Checklist
| Footnote 45. Kinks are to be avoided and are caused when ducts are bent across sharp corners such as framing members. Sharp bends are to be avoided and occur when the radius of the turn in the duct is less than one duct diameter. Compression is to be avoided and occurs when flexible ducts in unconditioned space are installed in cavities smaller than the outer duct diameter and ducts in conditioned space are installed in cavities smaller than inner duct diameter. Ducts shall not include coils or loops except to the extent needed for acoustical control. | [5 empty] | All | Required | Footnote 45 - 6.1
| 6.2 Bedrooms with a design supply airflow ≥ 150 CFM (per Item 5.2 on the National HVAC Design Report) pressure-balanced (e.g., using transfer grilles, jump ducts, dedicated return ducts, undercut doors) to achieve a Rater-measured pressure differential ≥ -5 Pa and ≤ +5 Pa with respect to the main body of the dwelling unit when all air handlers are operating. See Footnote 46 for test configuration. 46 |  | - | - |  |  | All | Required | Checklist
| Footnote 46. Item 6.2 does not apply to ventilation ducts, exhaust ducts, or non-ducted systems. For an HVAC system with a multi-speed fan, the highest design fan speed shall be used when verifying this requirement. When verifying this requirement, doors separating bedrooms from the main body of the dwelling unit (e.g., a door between a bedroom and a hallway) shall be closed and doors to rooms that can only be entered from the bedroom (e.g., a closet, a bathroom) shall be open. The Rater-measured pressure shall be rounded to the nearest whole number to assess compliance. | [5 empty] | All | Required | Footnote 46 - 6.2
| 6.3 All supply and return ducts in unconditioned space, including connections to trunk ducts, are insulated to ≥ R-6. 47 |  | - | - |  |  | All | Required | Checklist
| Footnote 47. Item 6.3 does not apply to ducts that are a part of local mechanical exhaust or exhaust-only dwelling-unit mechanical ventilation systems. EPA recommends, but does not require, that all metal ductwork not encompassed by Section 6 (e.g., exhaust ducts, duct boots, ducts in conditioned space) also be insulated and that insulation be sealed to duct boots to prevent condensation. | [5 empty] | All | Required | Footnote 47 - 6.3
| 6.3.1 Prescriptive Path: Dwelling unit ductwork meets the location and insulation requirements specified in the ENERGY STAR Multifamily Reference Design. |  | - | - |  |  | Prescriptive | Required | Checklist
| 6.4 Rater-measured total duct leakage in dwelling units meets one of the following two options: 48, 49 | [5 empty] | All | Required | Checklist
| Footnote 48. Item 6.4 and 6.5 only apply to heating, cooling, and balanced ventilation ducts that only serve one dwelling unit. Duct leakage testing is not required if the ducts and air handler are in conditioned space and the total supply duct length of the system, including all supply trunks and branches, is ≤ 10 ft. Duct leakage shall be determined and documented by a Rater using ANSI / RESNET / ICC Std. 380 including all Addenda and Normative Appendices, with new versions and Addenda implemented according to the Effective Date and Transition Period End Date defined by RESNET. RESNET interpretations of Standard 380 shall also be followed. Leakage limits shall be assessed on a per-system, rather than per-dwelling unit, basis. For balanced ventilation ducts that are not connected to space heating or cooling systems, a Rater is permitted to visually verify, in lieu of duct leakage testing, that all seams and connections are sealed with mastic or metal tape and all duct boots are sealed to floor, wall, or ceiling using caulk, foam, or mastic tape. | [5 empty] | All | Required | Footnote 48 - 6.4
| Footnote 49: Note that compliance with Item 6.4.1 or 6.4.2 in conjunction with Section 4a of the National Rater Design Review Checklist automatically achieves Grade I total duct leakage per ANSI / RESNET / ACCA Std. 310. | [5 empty] | All | Required | Footnote 49 - 6.4
| 6.4.1 Rough-in: Tested per allowances below, with air handler & all ducts, building cavities used as ducts, & duct boots installed. In addition, all duct boots sealed to finished surface, Rater-verified at final. 50 No ducted returns 36: The greater of ≤ 3 CFM25 per 100 sq. ft. of CFA or ≤ 30 CFM. Additionally, the Rater-measured pressure difference between the space containing the air handler and the conditioned space, with the air handler running at high speed, is ≤ 5 Pa. For systems > 1 ton, increase by 1 Pa per half ton. One or two ducted returns 36: The greater of ≤ 4 CFM25 per 100 sq. ft. of CFA or ≤ 40 CFM. Three or more ducted returns 36 : The greater of ≤ 6 CFM25 per 100 sq. ft. of CFA or ≤ 60 CFM. |  | - | - |  |  | All | Required | Checklist
| Footnote 36. A ‘ducted return’ is defined as a continuous duct made of sheet metal, duct board, or flexible duct that connects one or more return grilles to the return-side inlet of the air handler. Any other approach to convey air from return or transfer grille(s) to the air handler, such as the use of building cavities, does not constitute a ‘ducted return’. | [5 empty] | All | Required | Footnote 36 - 6.4.1
| Footnote 50. Cabinets (e.g., kitchen, bath, multimedia) or ducts that connect duct boots to toe-kick registers are not required to be in place during the ‘rough-in’ test. | [5 empty] | All | Required | Footnote 50 - 6.4.1
| 6.4.2 Final: Tested per allowances below, with the air handler & all ducts, building cavities used as ducts, duct boots, & register grilles atop the finished surface (e.g., drywall, floor) installed. 51 No ducted returns 36: The greater of ≤ 6 CFM25 per 100 sq. ft. of CFA or ≤ 60 CFM. Additionally, the Rater-measured pressure difference between the space containing the air handler and the conditioned space, with the air handler running at high speed, is ≤ 5 Pa. For systems > 1 ton, increase by 1 Pa per half ton. One or two ducted returns 36: The greater of ≤ 8 CFM25 per 100 sq. ft. of CFA or ≤ 80 CFM. Three or more ducted returns 36 : The greater of ≤ 12 CFM25 per 100 sq. ft. of CFA or ≤ 120 CFM. |  | - | - |  |  | All | Required | Checklist
| Footnote 36. A ‘ducted return’ is defined as a continuous duct made of sheet metal, duct board, or flexible duct that connects one or more return grilles to the return-side inlet of the air handler. Any other approach to convey air from return or transfer grille(s) to the air handler, such as the use of building cavities, does not constitute a ‘ducted return’. | [5 empty] | All | Required | Footnote 36 - 6.4.2
| Footnote 51. Registers atop carpets are permitted to be removed and the face of the duct boot temporarily sealed during testing. In such cases, the Rater shall visually verify that the boot has been durably sealed to the subfloor (e.g., using duct mastic or caulk) to prevent leakage during normal operation. | [5 empty] | All | Required | Footnote 51 - 6.4.2
| 6.5 Townhouses only: Rater-measured duct leakage to the outside the greater of ≤ 4 CFM25 per 100 sq. ft. of CFA or ≤ 40 CFM25. 48, 52 |  | - | - |  |  | All | Required | Checklist
| Footnote 48. Item 6.4 and 6.5 only apply to heating, cooling, and balanced ventilation ducts that only serve one dwelling unit. Duct leakage testing is not required if the ducts and air handler are in conditioned space and the total supply duct length of the system, including all supply trunks and branches, is ≤ 10 ft. Duct leakage shall be determined and documented by a Rater using ANSI / RESNET / ICC Std. 380 including all Addenda and Normative Appendices, with new versions and Addenda implemented according to the Effective Date and Transition Period End Date defined by RESNET. RESNET interpretations of Standard 380 shall also be followed. Leakage limits shall be assessed on a per-system, rather than per-dwelling unit, basis. For balanced ventilation ducts that are not connected to space heating or cooling systems, a Rater is permitted to visually verify, in lieu of duct leakage testing, that all seams and connections are sealed with mastic or metal tape and all duct boots are sealed to floor, wall, or ceiling using caulk, foam, or mastic tape. | [5 empty] | All | Required | Footnote 48 - 6.5
| Footnote 52. Testing of duct leakage to the outdoors can be waived in accordance with the 2nd or 3rd alternative of ANSI / RESNET / ICC Std. 301, Table 4.2.2 (1), footnote (w). Alternatively, testing of duct leakage to outdoors can be waived in accordance with Section 5.5.2 of ANSI / RESNET / ICC Std. 380 if total duct leakage, at rough-in or final, is ≤ 4 CFM25 per 100 sq. ft. of conditioned floor area or 40 CFM25, whichever is larger. Guidance to assist partners with these alternatives, including modeling inputs, is available at www.energystar.gov/newhomesguidance. | [5 empty] | All | Required | Footnote 52 - 6.5
| 6.6 Common Space: Supply, return, and exhaust ductwork and all plenums are sealed at all transverse joints, longitudinal seams, and duct wall penetrations with mastic or mastic tape |  | - | - |  |  | All | Required | Checklist
| 6.7 Duct leakage of central exhaust systems that serve four or more dwelling units, meets one of the following two options: |  | - | - |  |  | All | Required | Checklist
| 6.7.1 Rough-in: Tested including horizontal run outs, trunks, branches, and take-offs up to, but not including, the grilles, the leakage does not exceed 25% of exhaust fan flow. 53 |  | - | - |  |  | All | Required | Checklist
| Footnote 53. For the purpose of computing leakage allowance, exhaust fan flow shall be the lesser of the rated fan flow and at rough-in, 133% of the sum of the design exhaust airflow of the dwelling units that are exhausted by that central fan or at final, 143% of the sum of the design exhaust airflow of the dwelling units that are exhausted by that central fan. Duct leakage shall be tested at the design or average operating pressure and shall use the procedures in the RESNET Guidelines for Multifamily Energy Ratings, available at www.resnet.us/blog/resnet-adoptsguidelines-for-multifamily-energy-ratings/. Where testing at the design or average operating pressure is not feasible, testing at 50 Pa is permitted, however the following flow equation must be used to determine the leakage allowance at 50 Pa. CFM50 = CFMdesign / [Pdesign(0.65) / 50(0.65)] No less than 50% of the ductwork, based on total linear feet, shall be tested and must include ductwork other than the main trunks. Where portions of ductwork are tested, rather than entire risers, the percentage of leakage allowed is based upon the design airflow of the dwelling units that are exhausted in that portion. Where failures occur, the percentage of total linear feet required to be tested increases by 10%. Where aerosol-based sealant is used on some but not all risers, the ductwork selected for testing must be representative of all sealing strategies used. This test is not required of central exhaust systems serving clothes dryers. | [5 empty] | All | Required | Footnote 52 - 6.7.1
| 6.7.2 Final: Tested inclusive of all ductwork between the fan and the grilles, the leakage does not exceed 30% of exhaust fan flow. 53 |  | - | - |  |  | All | Required | Checklist
| Footnote 53. For the purpose of computing leakage allowance, exhaust fan flow shall be the lesser of the rated fan flow and at rough-in, 133% of the sum of the design exhaust airflow of the dwelling units that are exhausted by that central fan or at final, 143% of the sum of the design exhaust airflow of the dwelling units that are exhausted by that central fan. Duct leakage shall be tested at the design or average operating pressure and shall use the procedures in the RESNET Guidelines for Multifamily Energy Ratings, available at www.resnet.us/blog/resnet-adoptsguidelines-for-multifamily-energy-ratings/. Where testing at the design or average operating pressure is not feasible, testing at 50 Pa is permitted, however the following flow equation must be used to determine the leakage allowance at 50 Pa. CFM50 = CFMdesign / [Pdesign(0.65) / 50(0.65)] No less than 50% of the ductwork, based on total linear feet, shall be tested and must include ductwork other than the main trunks. Where portions of ductwork are tested, rather than entire risers, the percentage of leakage allowed is based upon the design airflow of the dwelling units that are exhausted in that portion. Where failures occur, the percentage of total linear feet required to be tested increases by 10%. Where aerosol-based sealant is used on some but not all risers, the ductwork selected for testing must be representative of all sealing strategies used. This test is not required of central exhaust systems serving clothes dryers. | [5 empty] | All | Required | Footnote 52 - 6.7.2
| 7. Dwelling-Unit & Common Space Mechanical Ventilation System | [5 empty] | All | Required | Section Header
| 7.1 Ventilation manufacturer & model number on installed equipment matches either of the following (check box): 41  National HVAC Design Report  Written approval received from designer |  | - | - |  | - | All | Required | Checklist
| Footnote 41. If installed equipment does not match the National HVAC Design Report, then prior to certification the Rater shall obtain written approval from the designer (e.g., email, updated National HVAC Design Report) confirming that the installed equipment meets the requirements of the National HVAC Design Report. In cases where the condenser unit is installed after the time of inspection by the Rater, the HVAC manufacturer and model numbers on installed equipment can be documented through the use of photographs provided by the Functional Testing Agent after installation is complete. | [5 empty] | All | Required | Footnote 41 - 7.1
| 7.2 Rater-measured ventilation rate is within either ± 15 CFM or ± 15% of dwelling unit design values (2.7), and meets or exceeds rates required by ASHRAE 62.2-2010. 54 |  | - | - |  | - | All | Required | Checklist
| 54. The dwelling-unit ventilation air flow and local exhaust air flows shall be determined and documented by a Rater using ANSI / RESNET / ICC Std. 380 including all Addenda and Normative Appendices, with new versions and Addenda implemented according to the Effective Date and Transition Period End Date defined by RESNET. RESNET interpretations of Standard 380 shall also be followed. In Item 7.2, the dwelling-unit ventilation rates required by ASHRAE 62.2-2010 can be calculated using the Multifamily Workbook or the following equation: 0.01 x Conditioned Floor Area + 7.5 x (number of bedrooms + 1). Where local codes do not permit dwelling-unit ventilation to exceed ASHRAE 62.2-2010 rates, Rater-measured ventilation rate is permitted to be 0-15 CFM less than rates required by ASHRAE 62.2-2010. | [5 empty] | All | Required | Footnote 54 - 7.2
| 7.3 Measured ventilation rate is within either ± 15 CFM or ± 15 % of common space design values (2.9), and meets or exceeds rates required by ASHRAE 62.1-2010 (2.8). 55 |  | - | - |  | - | All | Required | Checklist
| Footnote 55. While common spaces are not under the scope of ANSI / RESNET / ICC Std. 380, the ventilation air flow and exhaust air flows in common spaces shall be measured in accordance with the procedures in ANSI / RESNET / ICC Std. 380. The air flows may be measured by a Rater or a certified air-balancing contractor under the observation of a Rater. Where a system provides supply air that is a mix of return and outdoor air, and not 100% outdoor air, the outdoor air intake airflow shall be measured and compared to the total supply airflow to determine percentage of outdoor air supplied. This percentage shall be applied to airflow measured at supply registers to determine outdoor air provided for comparison to design airflow rates. | [5 empty] | All | Required | Footnote 55 - 7.3
| 7.4 Townhouses only: A readily-accessible ventilation override control installed and also labeled if its function is not obvious (e.g., a label is required for a standalone wall switch, but not for a switch that’s on the ventilation equipment). |  | - | - |  | - | All | Required | Checklist
| 7.5 No outdoor air intakes connected to return side of the dwelling unit HVAC system, unless controls are installed to operate intermittently & automatically based on a timer and to restrict intake when not in use (e.g., motorized damper). |  | - | - |  | - | All | Required | Checklist
| 7.6 If located in the dwelling unit, system fan rated ≤ 3 sones if intermittent and ≤ 2 sone if continuous, or exempted. 56 |  | - | - |  | - | All | Required | Checklist
| Footnote 56. Dwelling-unit mechanical ventilation fans shall be rated for sound at no less than the airflow rate in Item 2.7 of the National HVAC Design Report. Fans exempted from this requirement include HVAC air handler fans, remote-mounted fans, and intermittent fans rated ≥ 400 CFM. To be considered for this exemption, a remote-mounted fan must be mounted outside the habitable spaces, bathrooms, toilets, and hallways and there shall be ≥ 4 ft. ductwork between the fan and intake grill. Per ASHRAE 62.2-2010, habitable spaces are intended for continual human occupancy; such space generally includes areas used for living, sleeping, dining, and cooking but does not generally include bathrooms, toilets, hallways, storage areas, closets, or utility rooms. | [5 empty] | All | Required | Footnote 56 - 7.6
| 7.7 If system utilizes the dwelling unit HVAC fan, then the intalled fan type is ECM / ICM (4.12), or the controls will reduce the standalone ventilation run-time by accounting for hours when the HVAC system is heating or cooling. |  | - | - |  |  | All | Required | Checklist
| 7.8 In-unit bathroom fans or in-line fans are ENERGY STAR certified if used as part of the dwelling-unit mechanical ventilation system. 57 |  | - | - |  |  | All | Required | Checklist
| Footnote 57. Bathroom fans with a rated flow rate ≥ 500 CFM are exempted from the requirement to be ENERGY STAR certified. | [5 empty] | All | Required | Footnote 57 - 7.8
| 7.9 If central exhaust fans, ≤ 1 HP, are installed as part of the dwelling-unit mechanical ventilation system, then they are direct-drive, ECM, with variable speed controllers. If > 1 HP, they are installed with NEMATM Premium Motors. |  | - | - |  |  | All | Required | Checklist
| 7.10 Air inlet locations (Complete if ventilation air inlet locations were installed (2.22, 2.23); otherwise check “N/A”): 58, 59 | [5 empty] | All | Required | Checklist
| Footnote 58. Ventilation air inlets that are only visible via rooftop access are exempted from Item 7.9 and the Rater shall mark “N/A”. The outlet and inlet of balanced ventilation systems shall meet these spacing requirements unless manufacturer instructions indicate that a smaller distance may be used. However, if this occurs the manufacturer’s instructions shall be collected for documentation purposes. | [5 empty] | All | Required | Footnote 58 - 7.10
| Footnote 59. Without proper maintenance, ventilation air inlet screens often become filled with debris. Therefore, EPA recommends, but does not require, that these ventilation air inlets be located so as to facilitate access and regular service by the building owner. | [5 empty] | All | Required | Footnote 59 - 7.10
| 7.10.1 Inlet(s) pull ventilation air directly from outdoors and not from attic, crawlspace, garage, or adjacent dwelling unit. |  | - | - |  | - | All | Required | Checklist
| 7.10.2 Inlet(s) are ≥ 2 ft. above grade or roof deck; ≥ 10 ft. of stretched-string distance from known contamination sources not exiting the roof, and ≥ 3 ft. distance from dryer exhausts and sources exiting the roof. 60 |  | - | - |  | - | All | Required | Checklist
| Footnote 60. Known contamination sources include, but are not limited to, stacks, vents, exhausts, and vehicles. | [5 empty] | All | Required | Footnote 60 - 7.10.2
| 8. Local Mechanical Exhaust | [5 empty] | All | Required | Section Header
| Dwelling Unit Mechanical exhaust - In each dwelling unit kitchen and bathroom, a system is installed that exhausts directly to the outdoors and meets one of the following Rater-measured airflow and manufacturer-rated sound level standards: 54, 61 | [5 empty] | All | Required | Section Details
| 54. The dwelling-unit ventilation air flow and local exhaust air flows shall be determined and documented by a Rater using ANSI / RESNET / ICC Std. 380 including all Addenda and Normative Appendices, with new versions and Addenda implemented according to the Effective Date and Transition Period End Date defined by RESNET. RESNET interpretations of Standard 380 shall also be followed. In Item 7.2, the dwelling-unit ventilation rates required by ASHRAE 62.2-2010 can be calculated using the Multifamily Workbook or the following equation: 0.01 x Conditioned Floor Area + 7.5 x (number of bedrooms + 1). Where local codes do not permit dwelling-unit ventilation to exceed ASHRAE 62.2-2010 rates, Rater-measured ventilation rate is permitted to be 0-15 CFM less than rates required by ASHRAE 62.2-2010. | [5 empty] | All | Required | Footnote 54 - 8 DUME
| Footnote 61. Continuous bathroom local mechanical exhaust fans shall be rated for sound at no less than the airflow rate in Item 8.2. Intermittent bathroom and both intermittent and continuous kitchen local mechanical exhaust fans are recommended, but not required, to be rated for sound at no less than the airflow rate in Items 8.1 and 8.2. Per ASHRAE 62.2-2010, an exhaust system is one or more fans that remove air from the building, causing outdoor air to enter by ventilation inlets or normal leakage paths through the building envelope (e.g., bath exhaust fans, range hoods, clothes dryers). Per ASHRAE 62.2-2010, a bathroom is any room containing a bathtub, shower, spa, or similar source of moisture. | [5 empty] | All | Required | Footnote 61 - 8 DUME
| Location | [5 empty] | All | Required | Section Header
| 8.1 Kitchen Airflow Continuous Rate: ≥ 5 ACH, based on kitchen volume 63, 64 Intermittent Rate 62: ≥ 100 CFM and, if not integrated with range, also ≥ 5 ACH based on kitchen volume 63, 64, 65 Sound Continuous Rate: Recommended: ≤ 1 sone Intermittent Rate 62: Recommended: ≤ 3 sones |  | - | - |  | - | All | Required | Checklist
| Footnote 62. An intermittent mechanical exhaust system, where provided, shall be designed to operate as needed by the occupant. Control devices shall not impede occupant control in intermittent systems. | [5 empty] | All | Required | Footnote 62 - 8.1
| Footnote 63. Kitchen volume shall be determined by drawing the smallest possible rectangle on the floor plan that encompasses all cabinets, pantries, islands, peninsulas, ranges / ovens, and the kitchen exhaust fan, and multiplying by the average ceiling height for this area. In addition, the continuous kitchen exhaust rate shall be ≥ 25 CFM, per 2009 IRC Table M1507.3, regardless of the rate calculated using the kitchen volume. Cabinet volume shall be included in the kitchen volume. | [5 empty] | All | Required | Footnote 63 - 8.1
| Footnote 64. Alternatively, the prescriptive duct sizing requirements in Table 5.3 of ASHRAE 62.2-2010 are permitted to be used for kitchen exhaust fans based upon the rated airflow of the fan at 0.25 IWC. If the rated airflow is unknown, ≥ 6 in. smooth duct shall be used, with a rectangular to round duct transition as needed. Guidance to assist partners with these alternatives is available at www.energystar.gov/newhomesguidance. As an alternative to Item 8.1, dwelling units are permitted to use a continuous kitchen exhaust rate of 25 CFM per 2009 IRC Table M1507.3, if they are either a) PHIUS+ or PHI certified, or b) provide both dwelling-unit ventilation and local mechanical kitchen exhaust using a balanced system, and have a Rater-verified whole-building infiltration rate ≤ 0.05 CFM50 per sq. ft. of Enclosure Area, and a Rater-verified dwelling unit compartmentalization rate ≤ 0.30 CFM50 per sq. ft. of Enclosure Area if multiple dwelling units are present in the building. ‘Enclosure Area’ is defined as the area of the surfaces that bound the volume being pressurized / depressurized during the test. | [5 empty] | All | Required | Footnote 64 - 8.1
| Footnote 65. All intermittent kitchen exhaust fans must be capable of exhausting at least 100 CFM. In addition, if the fan is not part of a vented range hood or appliance-range hood combination (i.e., if the fan is not integrated with the range), then it must also be capable of exhausting ≥ 5 ACH, based on the kitchen volume. | [5 empty] | All | Required | Footnote 65 - 8.1
| 8.2 Bathroom Airflow Continuous Rate: ≥ 20 CFM Intermittent Rate 62: ≥ 50 CFM Sound Continuous Rate: Required: ≤ 2 sones Intermittent Rate 62: Recommended: ≤ 3 sones |  | - | - |  | - | All | Required | Checklist
| Footnote 62. An intermittent mechanical exhaust system, where provided, shall be designed to operate as needed by the occupant. Control devices shall not impede occupant control in intermittent systems. | [5 empty] | All | Required | Footnote 62 - 8.2
| Common Space 2 and Garage Mechanical Exhaust | [5 empty] | All | Required | Section Header
| Footnote 2. The term ‘common space’ refers to any spaces in the building being certified that serve a function in support of the residential part of the building that is not part of a dwelling or sleeping unit. This includes spaces used by residents, such as corridors, stairs, lobbies, laundry rooms, exercise rooms, residential recreation rooms, and dining halls, as well as offices and other spaces used by building management, administration or maintenance in support of the residents. | [5 empty] | All | Required | Footnote 2 - 8 CSME
| 8.3 Measured exhaust rates are ≥ ASHRAE 62.1 rates (2c). 55 |  | - | - |  |  | All | Required | Checklist
| Footnote 55. While common spaces are not under the scope of ANSI / RESNET / ICC Std. 380, the ventilation air flow and exhaust air flows in common spaces shall be measured in accordance with the procedures in ANSI / RESNET / ICC Std. 380. The air flows may be measured by a Rater or a certified air-balancing contractor under the observation of a Rater. Where a system provides supply air that is a mix of return and outdoor air, and not 100% outdoor air, the outdoor air intake airflow shall be measured and compared to the total supply airflow to determine percentage of outdoor air supplied. This percentage shall be applied to airflow measured at supply registers to determine outdoor air provided for comparison to design airflow rates. | [5 empty] | All | Required | Footnote 54 - 8.3
| 8.4 Where a garage exhaust ventilation system is installed, it is equipped with controls that sense CO and NO2. |  | - | - |  |  | All | Required | Checklist
| 9. Filtration | [5 empty] | All | Required | Section Header
| 9.1 MERV 6+ filter(s) installed in each dwelling unit ducted mech. System, serving an individual dwelling unit located to facilitate access & regular service by the occupant or building owner. 66 |  | - | - |  |  | All | Required | Checklist
| Footnote 66. Based upon, ASHRAE 62.2-2010, ducted mechanical systems are those that supply air to an occupiable space with a total amount of supply ductwork exceeding 10 ft. in length and through a thermal conditioning component, except for evaporative coolers. Systems that do not meet this definition are exempt from this requirement. While filters are recommended for mini-split systems, HRV’s, and ERV’s, these systems, ducted or not, typically do not have MERV-rated filters available for use and are, therefore, also exempted under this version of the requirements. HVAC filters located in the attic shall be considered accessible to the occupant or building owner if either 1) drop-down stairs provide access to attic and a permanently installed walkway has been provided between the attic access location and the filter or 2) the filter location enables arm-length access from a portable ladder without the need to step into the attic and the ceiling height where access is provided is ≤ 12 ft. | [5 empty] | All | Required | Footnote 66 - 9.1
| 9.1.1 Filter access panel includes gasket and fits snugly against the exposed edge of filter when closed to prevent bypass. 67 |  | - | - |  |  | All | Required | Checklist
| Footnote 67. The filter media box (i.e., the component in the HVAC system that houses the filter) may be either site-fabricated by the installer or pre-fabricated by the manufacturer to meet this requirement. These requirements only apply when the filter is installed in a filter media box located in the HVAC system, not when the filter is installed flush with the return grill. | [5 empty] | All | Required | Footnote 67 - 9.1.1
| 9.1.2 All return air and mechanically supplied outdoor air passes through filter prior to conditioning. |  | - | - |  |  | All | Required | Checklist
| 10. Combustion Appliances | [5 empty] | All | Required | Section Header
| 10.1 Furnaces, boilers, and water heaters located within the building’s pressure boundary are mechanically drafted or direct-vented. If mechanically drafted, the minimum volume of combustion air required for safe operation by the manufacturer and/or code shall be met or exceeded and make-up air sources must be mechanically closed when the combustion appliance is not in operation. Alternatives in Footnote 70. 68, 69, 70 |  | - | - |  |  | All | Required | Checklist
| Footnote 68.The pressure boundary is the primary enclosure boundary separating indoor and outdoor air. For example, a volume that has more leakage to outside than to conditioned space would be outside the pressure boundary. | [5 empty] | All | Required | Footnote 68 - 10.1
| Footnote 69. Per the 2009 International Mechanical Code, a direct-vent appliance is one that is constructed and installed so that all air for combustion is derived from the outdoor atmosphere and all flue gases are discharged to the outside atmosphere; a mechanical draft system is a venting system designed to remove flue or vent gases by mechanical means consisting of an induced draft portion under non-positive static pressure or a forced draft portion under positive static pressure; and a natural draft system is a venting system designed to remove flue or vent gases under nonpositive static vent pressure entirely by natural draft. | [5 empty] | All | Required | Footnote 69 - 10.1
| Footnote 70. Naturally drafted equipment is only allowed if located in a space outside the pressure boundary, where the envelope assemblies separating it from conditioned space are insulated and air-sealed. | [5 empty] | All | Required | Footnote 70 - 10.1
| 10.2 Fireplaces located within the building’s pressure boundary are direct-vented. 68, 69 |  | - | - |  |  | All | Required | Checklist
| Footnote 68. The pressure boundary is the primary enclosure boundary separating indoor and outdoor air. For example, a volume that has more leakage to outside than to conditioned space would be outside the pressure boundary. | [5 empty] | All | Required | Footnote 68 - 10.2
| Footnote 69. Per the 2009 International Mechanical Code, a direct-vent appliance is one that is constructed and installed so that all air for combustion is derived from the outdoor atmosphere and all flue gases are discharged to the outside atmosphere; a mechanical draft system is a venting system designed to remove flue or vent gases by mechanical means consisting of an induced draft portion under non-positive static pressure or a forced draft portion under positive static pressure; and a natural draft system is a venting system designed to remove flue or vent gases under nonpositive static vent pressure entirely by natural draft. | [5 empty] | All | Required | Footnote 69 - 10.2
| 10.3 No unvented combustion appliances other than cooking ranges or ovens are located inside the building’s pressure boundary. For cooking ranges and ovens, local mechanical exhaust per Checklist Item 8.1 requirements must be met. 68 |  | - | - |  |  | All | Required | Checklist
| Footnote 68. The pressure boundary is the primary enclosure boundary separating indoor and outdoor air. For example, a volume that has more leakage to outside than to conditioned space would be outside the pressure boundary. | [5 empty] | All | Required | Footnote 68 - 10.3
| Other | [5 empty] | All | Required | Section Header
| 11. Domestic Hot Water | [5 empty] | All | Required | Section Header
| 11.1 Prescriptive Path: Hot water equipment rated in EF or UEF meet the efficiency levels specified in the ENERGY STAR Multifamily Reference Design. Boilers providing hot water are ≥85% Et. 71 |  | - | - |  |  | Prescriptive | Required | Checklist
| Footnote 71. Where water heater efficiency is rated in Uniform Energy Factor (UEF) rather than Energy Factor (EF), the EF may be calculated from the Uniform Energy Factor (UEF) using the RESNET EF Calculator 2017. The calculated EF must meet the efficiency levels specified in the ENERGY STAR Multifamily Reference Design. | [5 empty] | Prescriptive | Required | Footnote 71 - 11.1
| 11.2 ERI: For hot water equipment serving common spaces but not dwelling units nor shared laundry: where rated EF or UEF, meet the efficiency levels specified in the ENERGY STAR Multifamily Reference Design. Where rated in thermal efficiency, meet or exceed 85% Et. 71 |  | - | - |  |  | ERI | Required | Checklist
| Footnote 71. Where water heater efficiency is rated in Uniform Energy Factor (UEF) rather than Energy Factor (EF), the EF may be calculated from the Uniform Energy Factor (UEF) using the RESNET EF Calculator 2017. The calculated EF must meet the efficiency levels specified in the ENERGY STAR Multifamily Reference Design. | [5 empty] | ERI | Required | Footnote 71 - 11.2
| 11.3 For in-unit storage water heaters, AHRI Certificate confirms the presence of a heat trap. |  | - | - |  |  | All | Required | Checklist
| 11.4 DHW piping located in the dwelling unit is insulated with a minimum of R-3. 72 |  | - |  |  | - | All | Required | Checklist
| Footnote 72. In accordance with Section 7.4.3 of ASHRAE 90.1-2016, the following in-unit DHW piping requires insulation: a. Recirculating system piping, including the supply and return piping of a circulating tank type water heater. b. The first 8 feet of outlet piping of a constant-temperature nonrecirculating storage system. c. The first 8 feet of branch piping connecting to recirculated, heat-traced, or impedance heated piping. d. The inlet piping between the storage tank and a heat trap in a nonrecirculating storage system. e. Piping that is externally heated (such as heat trace or impedance heating). | [5 empty] | All | Required | Footnote 72 - 11.4
| 11.5 Rater-measured delivery temperatures at faucets and showerheads do not exceed 125°F. 73 |  | - | - |  | - | All | Required | Checklist
| Footnote 73. To measure the delivery temperature, turn the hot water at a fixture completely on and place a digital thermometer in the stream of water. Observe the thermometer and when no additional rise in temperature occurs after 10 seconds, confirm this temperature does not exceed 125°F. | [5 empty] | All | Required | Footnote 73 - 11.5
| 12. Lighting | [5 empty] | All | Required | Section Header
| 12.1 Common Space 2 Lighting Controls: | [5 empty] | All | Required | Checklist
| Footnote 2. The term ‘common space’ refers to any spaces in the building being certified that serve a function in support of the residential part of the building that is not part of a dwelling or sleeping unit. This includes spaces used by residents, such as corridors, stairs, lobbies, laundry rooms, exercise rooms, residential recreation rooms, and dining halls, as well as offices and other spaces used by building management, administration or maintenance in support of the residents. | [5 empty] | All | Required | Footnote 2 - 12.1
| 12.1.1 ERI and Prescriptive Path: All common spaces 2 (including shared garages), except the building lobby and where automatic shutoff would endanger the safety of occupants, have occupancy sensors or automatic bi-level lighting controls installed and operation has been verified. |  | - |  |  |  | ERI, Prescriptive | Required | Checklist
| Footnote 2. The term ‘common space’ refers to any spaces in the building being certified that serve a function in support of the residential part of the building that is not part of a dwelling or sleeping unit. This includes spaces used by residents, such as corridors, stairs, lobbies, laundry rooms, exercise rooms, residential recreation rooms, and dining halls, as well as offices and other spaces used by building management, administration or maintenance in support of the residents. | [5 empty] | ERI, Prescriptive | Required | Footnote 2 - 12.1.1
| 12.1.2 ASHRAE path only: All common spaces 2 (including shared garages), except the building lobby, corridors, and stairwells and where automatic shutoff would endanger the safety of occupants, have occupancy sensors or automatic bi-level lighting controls installed and operation has been verified. |  | - |  |  |  | ASHRAE | Required | Checklist
| Footnote 2. The term ‘common space’ refers to any spaces in the building being certified that serve a function in support of the residential part of the building that is not part of a dwelling or sleeping unit. This includes spaces used by residents, such as corridors, stairs, lobbies, laundry rooms, exercise rooms, residential recreation rooms, and dining halls, as well as offices and other spaces used by building management, administration or maintenance in support of the residents. | [5 empty] | ASHRAE | Required | Footnote 2 - 12.1.2
| 12.2 Common Space 2 Lighting Power Density Maximum (except garages): 74 | [5 empty] | All | Required | Checklist
| Footnote 74. Senior housing projects can use the space-by-space allowances for ‘facilities for the visually impaired’ in ASHRAE 90.1-2016 Appendix G Table G3.7 for spaces used primarily by building residents. For example, 1.15 W/SF lighting power allowance may be used for the corridors in the baseline. To qualify for the increased allowance, the project must be designed to comply with the light levels in ANSI / IES RP-28 and must provide housing for seniors and/or people with special visual needs. Prescriptive Path dwelling unit overall in-unit lighting power density is permitted to be ≤ 1.3 W/SF, using 1.65 W/SF where lighting is not installed. | [5 empty] | All | Required | Footnote 74 - 12.2
| 12.2.1 ERI and Prescriptive Path: Total installed lighting power for the combined common spaces 2 must not exceed ASHRAE 90.1-2007 allowances for those combined spaces, using the Space-by-Space or Building Area Method. See Footnote 75 for allowances. 75 |  | - |  |  |  | ERI, Prescriptive | Required | Checklist
| Footnote 2. The term ‘common space’ refers to any spaces in the building being certified that serve a function in support of the residential part of the building that is not part of a dwelling or sleeping unit. This includes spaces used by residents, such as corridors, stairs, lobbies, laundry rooms, exercise rooms, residential recreation rooms, and dining halls, as well as offices and other spaces used by building management, administration or maintenance in support of the residents. | [5 empty] | ERI, Prescriptive | Required | Footnote 2 - 12.2.1
| Footnote 75. Lighting power density values from ASHRAE 90.1-2007 Section 9 for Space-by-Space Method for typical common spaces in multifamily properties are shown in the table below. Projects following the Building Area method, the lighting power density is 0.7 W/ft2. For spaces not shown, refer to ASHRAE 90.1-2007 Section 9. SEE TABLE IN REFERENCE TABLES TAB - Lighting Power Density | [5 empty] | ERI, Prescriptive | Required | Footnote 75 - 12.2.1
| 12.2.2 ASHRAE path only: Total installed lighting power for the combined common spaces 2 must not exceed ASHRAE 90.1-2007 allowances for those combined spaces, using the Space-by-Space or Building Area Method, by more than 20%. See Footnote 75 for allowances. 75 |  | - |  |  |  | ASHRAE | Required | Checklist
| Footnote 2. The term ‘common space’ refers to any spaces in the building being certified that serve a function in support of the residential part of the building that is not part of a dwelling or sleeping unit. This includes spaces used by residents, such as corridors, stairs, lobbies, laundry rooms, exercise rooms, residential recreation rooms, and dining halls, as well as offices and other spaces used by building management, administration or maintenance in support of the residents. | [5 empty] | ASHRAE | Required | Footnote 2 - 12.2.2
| Footnote 75. Lighting power density values from ASHRAE 90.1-2007 Section 9 for Space-by-Space Method for typical common spaces in multifamily properties are shown in the table below. Projects following the Building Area method, the lighting power density is 0.7 W/ft2. For spaces not shown, refer to ASHRAE 90.1-2007 Section 9. SEE TABLE IN REFERENCE TABLES TAB - Lighting Power Density | [5 empty] | ASHRAE | Required | Footnote 75 - 12.2.2
| 12.3 Shared garages: Lighting power density does not exceed 0.24 W/ft2. |  | - |  |  |  | All | Required | Checklist
| 12.4 Exterior lighting controls: Fixtures, including parking lot fixtures, must include automatic switching on timers or photocell controls except fixtures intended for 24-hour operation, required for security, or located on dwelling unit balconies. |  | - |  |  |  | All | Required | Checklist
| 12.5 ERI Path: All exterior and common space lighting fixtures meet the efficiency requirements in the ENERGY STAR Multifamily Reference Design, except fixtures located on dwelling unit balconies. 76, 77 |  | - | - |  |  | ERI | Required | Checklist
| Footnote 76. This requirement applies to exterior lighting fixtures that are attached to the building, but does not apply to landscape or parking lot lighting fixtures. | [5 empty] | ERI | Required | Footnote 76 - 12.5
| Footnote 77. For Prescriptive Path dwelling units, ENERGY STAR certified fixtures or light bulbs are required; however, the Rater is only responsible for verifying that the installed lighting meets the Tier I or Tier II definition specified in ANSI / RESNET / ICC Std. 301. For locations outside the dwelling unit, as an alternative to ENERGY STAR certified fixtures or light bulbs, lighting that meets the Tier I or Tier II definition specified in ANSI / RESNET / ICC Std.301 is permitted. | [5 empty] | ERI | Required | Footnote 77 - 12.5
| 12.6 Prescriptive Path: All lighting fixtures (i.e., dwelling units, common spaces, and exterior) meet the efficiency requirements in the ENERGY STAR Multifamily Reference Design. 76, 77 |  | - | - |  |  | Prescriptive | Required | Checklist
| Footnote 76. This requirement applies to exterior lighting fixtures that are attached to the building, but does not apply to landscape or parking lot lighting fixtures. | [5 empty] | Prescriptive | Required | Footnote 76 - 12.6
| Footnote 77. For Prescriptive Path dwelling units, ENERGY STAR certified fixtures or light bulbs are required; however, the Rater is only responsible for verifying that the installed lighting meets the Tier I or Tier II definition specified in ANSI / RESNET / ICC Std. 301. For locations outside the dwelling unit, as an alternative to ENERGY STAR certified fixtures or light bulbs, lighting that meets the Tier I or Tier II definition specified in ANSI / RESNET / ICC Std.301 is permitted. | [5 empty] | Prescriptive | Required | Footnote 77 - 12.6
| 12.7 Prescriptive Path: Dwelling unit overall in-unit lighting power density ≤ 0.75 W/ft2. When calculating overall lighting power density, use 1.1 W/ft2 where lighting is not installed. 74 |  | - | - |  |  | Prescriptive | Required | Checklist
| Footnote 74. Senior housing projects can use the space-by-space allowances for ‘facilities for the visually impaired’ in ASHRAE 90.1-2016 Appendix G Table G3.7 for spaces used primarily by building residents. For example, 1.15 W/SF lighting power allowance may be used for the corridors in the baseline. To qualify for the increased allowance, the project must be designed to comply with the light levels in ANSI / IES RP-28 and must provide housing for seniors and/or people with special visual needs. Prescriptive Path dwelling unit overall in-unit lighting power density is permitted to be ≤ 1.3 W/SF, using 1.65 W/SF where lighting is not installed. | [5 empty] | Prescriptive | Required | Footnote 74 - 12.7
| 13. Appliances, Ceiling Fans, and Plumbing Fixtures | [5 empty] | All | Required | Section Header
| 13.1 Prescriptive Path: Installed appliances and plumbing fixtures in dwelling units and common spaces meet the criteria in the ENERGY STAR Multifamily Reference Design. 78 |  | - | - |  |  | Prescriptive | Required | Checklist
| Footnote 78. Where an appliance type is not eligible for ENERGY STAR certification, (e.g., commercial dryers) the appliance is exempt from this requirement. Where a bathroom faucet or aerator is not eligible for WaterSense certification, (e.g., public use lavatory faucets) the fixture is exempt from this requirement. | [5 empty] | Prescriptive | Required | Footnote 78 - 13.1
| 13.2 ERI Path: Installed appliances and plumbing fixtures in common spaces, and not included in the ERI model, meet the criteria in the ENERGY STAR Multifamily Reference Design. 78 |  | - | - |  |  | ERI | Required | Checklist
| Footnote 78. Where an appliance type is not eligible for ENERGY STAR certification, (e.g., commercial dryers) the appliance is exempt from this requirement. Where a bathroom faucet or aerator is not eligible for WaterSense certification, (e.g., public use lavatory faucets) the fixture is exempt from this requirement. | [5 empty] | ERI | Required | Footnote 78 - 13.2
| 13.3 Prescriptive Path: Shower compartments with multiple fixtures cannot be operated simultaneously OR the total flow rate per shower compartment must not exceed 1.75 gallons per minute, as rated at 80 psi. |  | - | - |  |  | Prescriptive | Required | Checklist
| 14. Whole Building Energy Consumption Data Acquisition | [5 empty] | All | Required | Section Header
| 14.1 For buildings 50,000 ft2 and larger, a strategy that enables the collection of monthly or annual building-level energy consumption data (electricity, natural gas, chilled water, steam, fuel oil, propane, etc.) has been confirmed. 79 |  | - | - |  |  | All | Required | Checklist
| Footnote 79. Strategies include: an agreement with the utility companies to provide the aggregated building-level data, in a spreadsheet format or directly through Portfolio Manager; OR evidence that securing signed utility data release forms will be a mandatory component of all lease agreements; OR installation of a building-level energy monitor, data acquisition system, or utility-owned energy meter. If an energy monitor is installed, the builder shall provide the building operator with the manufacturer’s documentation and operations manual. EPA recommends, but does not require, that one of these strategies also be implemented in buildings 25,000-49,999 ft2. | [5 empty] | All | Required | Footnote 79 - 14.1
Rater Name: |  | Rater Pre-Drywall Inspection Date(s): |  |  | Rater Initials:
Rater Company Name:
Rater Name: |  | Rater Final Inspection Date(s): |  |  | Rater Initials:
Rater Company Name:
Builder/Developer Employee: |  | Builder Inspection Date(s): |  |  | Builder Initials:
Builder/Developer Name:
Licensed Professional: |  | LP Inspection Date(s): |  |  | LP Initials:
SELECT PATHWAY
(Reset to All Paths)
(Reset to All Available)
Rater Field Checklist
(Reset All)
ERI
ASHRAE
Prescriptive
Required Only
Optional Only
Show all Footnotes
Hide all Footnotes
Title 24: Dwelling Unit Models
Title 24: Whole Building Models
Show Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Show Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)
Show Footnote(s)
Hide Footnote(s)

## ES 2. Unit Testing Results
Instructions: | Using Tables: Prior to the Proposed Design submittal, the yellow cells in the "Unit Types" table should be filled out for the unique floorplans in the project. Prior to testing, each unit in the project should be defined and assigned a unit type in the "Unit Details" table. These two tables will enable the generation of the testing targets and allow the user to track testing results of all items on an individual apartment basis. Prior to the As-Built submittal or as testing is completed, enter test values into all orange cells in the Testing Results section. Pass/Fail values will display at the unit level and for the entire checklist item. Additionally, prior to As-Built submittal, complete the orange cells in the "Label Printing Data Entry" table. Printing: Optimized for Landscape view
UNIT TYPES | [17 empty] | Label Printing Data Entry - this area should be populated during the As-Built Submittal to facilitate label & certificate printing
UNIT TYPE | BEDROOMS | BATHROOMS | AREA | PERIMETER | DWELLING UNIT HEIGHT | ENCLOSURE AREA | # RETURNS | VENTILATION (CFM) | ASHRAE 62.2 - 2010 | Ventilation > ASHRAE 62.2 | KITCHEN VENTILATION | KITCHEN VOLUME(ft3) | BATHROOM 1 VENTILATION | BATHROOM 2 VENTILATION | BATHROOM 3 VENTILATION | AC SIZE (Tons) |  | Ceiling Insulation (R-Value) | Wall Insulation (R-Value) |  | Floor Insulation (R-Value) |  | Slab Insulation (R-Value) |  | Window U-Factor |  | Window SHGC |  | Primary Heating System Type |  | Primary Heating Fuel |  | Primary Heating Efficiency |  | Primary Heating Efficiency Unit | Primary Cooling System Type | Primary Cooling Fuel |  | Primary Cooling Efficiency |  | Primary Cooling Efficiency Unit |  | Primary Hot Water System Type |  | Primary Hot Water Fuel |  | Primary Hot Water Efficiency (EF) |  | % ENERGY STAR Certified Lighting | # ES Refrigerators | # ES Ceiling Fans | # ES Dishwashers | # ES Exhaust Fans
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14 | Column15 | Column16 | Column17 | Column18 | Column19 | Column20 | Column21 | Column22 | Column23 | Column24 | Column25 | Column26 | Column27 | Column28 | Column29 | Column30 | Column31 | Column32 | Column33 | Column34 | Column35 | Column36 | Column37 | Column38 | Column39 | Column40 | Column41 | Column42 | Column43 | Column44 | Column45 | Column46 | Column47 | Column48 | Column49 | Column50 | Column51 | Column52 | Column53 | Column54
NOTES | bar: Column1 to Column6; Column8 to Column9; Column12; Column14 to Column17; Column19; Column21; Column23; Column25; Column27; Column29; Column31; Column33; Column35; Column39; Column41; Column43; Column45; Column47 to Column54
Enter Number of Units in Project Information tab
UNIT DETAILS |  |  |  | TESTING TARGETS | [7 empty] | SAMPLING | TESTING RESULTS
UNIT | UNIT TYPE | SQUARE FOOTAGE | ENCLOSURE AREA | TOTAL DUCT LEAKAGE (6.4.1/6.4.2) | Duct Leakage to Outdoors (Townhouses Only) (6.5) | UNIT INFILTRATION (4.10) | DWELLING UNIT VENTILATION (7.2) | KITCHEN VENTILATION (8.1) | BATH 1 VENTILATION (8.2) | BATH 2 VENTILATION (8.2) | BATH 3 VENTILATION (8.2) | SAMPLE SET ID | TESTING DATE | TOTAL DUCT LEAKAGE (6.4.1 / 6.4.2) |  | TEST (ROUGH-IN/FINAL) | PRESSURE DIFFERENCE FOR NON-DUCTED RETURNS (6.4.1/6.4.2) |  | DUCT LEAKAGE TO OUTSIDE (TOWNHOUSES ONLY) (6.5) |  | UNIT INFILTRATION (4.10) |  | PRESSURE DIFFERENTIAL FOR AHU CLOSETS (4.10.1) |  | DWELLING UNIT VENTILATION (7.2) |  | KITCHEN VENTILATION (8.1) |  | BATH 1 VENTILATION (8.2) |  | BATH 2 VENTILATION (8.2) |  | BATH 3 VENTILATION (8.2) |  | RETURN SIDE STATIC PRESSURE (IWC) (5.4) | SUPPLY SIDE STATIC PRESSURE (IWC) (5.4) | TEMP AT SHOWER (11.5) |  | TEMP AT FAUCETS (11.5) |  | PRESSURE BALANCING (BEDROOM 1) (6.2) |  | PRESSURE BALANCING (BEDROOM 2) (6.2) |  | PRESSURE BALANCING (BEDROOM 3) (6.2)
[14 empty] | Value | Pass/Fail |  | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail |  |  | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail | Value | Pass/Fail
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14 | Column15 | Column16 | Column17 | Column18 | Column19 | Column20 | Column21 | Column22 | Column23 | Column24 | Column25 | Column26 | Column27 | Column28 | Column29 | Column30 | Column31 | Column32 | Column33 | Column34 | Column35 | Column36 | Column37 | Column38 | Column39 | Column40 | Column41 | Column42 | Column43 | Column44 | Column45 | Column46 | Column47
NOTES
[12 empty] | Checklist Item PASS/FAIL |  | PASS |  | N/A | PASS |  | PASS |  | PASS |  | PASS |  | PASS |  | PASS |  | PASS |  | PASS |  | PASS |  | N/A | N/A | PASS |  | PASS |  | PASS |  | PASS |  | PASS
+
-
+
-
Note on G5: Measured in accordance with ANSI/RESNET/ICC 380. Typically floor to floor, and in the case of 2-story units, finished floor of the 1st floor to the underside of the floor of the unit above it. The dwelling unit height shall extend from the finished floor to the bottom side of the floor decking above the subject Dwelling Unit for non-top floor level Dwelling Units and to the exterior enclosure air barrier for top floor level Dwelling Units.

## ES 3a. Common Area Ventilation
Instructions: | Using Tables: Prior to the Proposed Design submittal, enter space names and design CFM values in yellow cells, and enter a description of your sampling plan below each table. Add additional columns or rows as needed. (Note: Workbook does not allow you to remove columns after adding. Please save a copy of your workbook before adding new columns.) Prior to the As-Built Submittal, enter tested CFM values in the orange cells. Total airflow will calculate automatically and a Pass/Fail value will display. Printing: Optimized for both views (Portrait/Landscape).
Common Space Outdoor Air Ventilation Rates (7.3): This section can be expanded; copy and insert columns as needed for additional spaces. Copy and insert rows as needed for multiple registers serving a space
Enter Space >>> | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | NOTES
Ventilation Airflow Designed by ASHRAE 62.1, per Item 2.9 of HVAC Design Report
Tested CFM
Tested CFM
Tested CFM
Tested CFM
Tested CFM
Tested CFM
Tested CFM
Tested CFM
Total Airflow: | 0 | 0 | 0 | 0 | 0 | 0 | 0
15% ASHRAE | 0 | 0 | 0 | 0 | 0 | 0 | 0
Range (Upper) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Range (Lower) | -15 | -15 | -15 | -15 | -15 | -15 | -15
PASS/FAIL
Sampling Plan:
Common Space Exhaust Airflow Rates (8.3): This section can be expanded, copy and insert rows/columns as needed, to represent additional spaces.
Enter Space >>> | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | NOTES
Design CFM
Tested CFM
Tested CFM
Tested CFM
Tested CFM
Total Airflow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15% ASHRAE | 0 | 0 | 0 | 0 | 0 | 0 | 0
Range (Upper) | 15 | 15 | 15 | 15 | 15 | 15 | 15
Range (Lower) | -15 | -15 | -15 | -15 | -15 | -15 | -15
PASS/FAIL
Sampling Plan:
+
-
+
-
+
+

## ES 3b.Central Exhaust Duct Test
Instructions: | Using Tables: Prior to the Proposed Design submittal, enter values in yellow cells. This section can be expanded; copy and insert rows as needed. CFM allowances will calculate automatically. Enter a description of your sampling plan and the total number of risers below the table. Prior to the As-Built submittal, enter CFM Leakage results from Single Point tests into the orange cells. Printing: Optimized for printing in Landscape view.
Central Exhaust Ventilation Duct Leakage Summary (Single-Point tests):
Instructions: | Central exhaust systems that serve four or more dwelling units tested for duct leakage, where the leakage at rough-in (e.g. including trunks, branches, and take-offs) does not exceed 25% of exhaust fan flow or 30% of exhaust fan flow at final (e.g. inclusive of all ductwork between the fan and the grilles). Note: For the purpose of computing leakage allowance, exhaust fan flow shall be the lesser of the rated fan flow and at rough-in, 133% of the sum of the design exhaust airflow of the dwelling units that are exhausted by that central fan or at final, 143% of the sum of the design exhaust airflow of the dwelling units that are exhausted by that central fan. Duct leakage shall be tested at the design or average operating pressure and shall use the procedures in the RESNET Guidelines for Multifamily Energy Ratings, available at www.resnet.us/blog/resnet-adoptsguidelines-for-multifamily-energy-ratings/. Where testing at the design or average operating pressure is not feasible, testing at 50 Pa is permitted, however the following flow equation must be used to determine the leakage allowance at 50 Pa. CFM50 = CFMdesign / Pdesign(0.65) / 50(0.65)
Fan/Shaft ID | # of units/grilles | Rate per unit/grille (CFM) | Rated Fan Flow CFM | CFM50 | Design/Operating Pressure | Testing Pressure | CFM Leakage from Single-Point Test | Test at Final or Rough-in | % Leakage of Design CFM | Rough-in MAX CFM | Final MAX CFM | PASS/FAIL | Comments | NOTES
50
50
50
50
50
50
50
50
Sampling Plan:
Total # of risers:
+
-

## ES 4. Appliances
Instructions: | Using Tables: Providing data in orange cells on this tab prior to the Proposed Design submittal is optional, but recommended. Prior to As-Built submittal, enter installed appliance details into all orange cells. If make and model numbers were entered at the Proposed Design submittal, mark any changes from the Proposed Design in 'Inspection Comments' (Column K). Printing: Optimized for both views (Portrait/Landscape).
1. ASHRAE Path
Provide photo of each unique appliance model number AND provide the Energy Guide label or other documentation that confirms energy use consistent with ASHRAE Path Calculator.
2. Prescriptive Path
Provide photo of each unique appliance model number AND either list MFR/model in table below OR submit evidence of listing in the ENERGY STAR Product Search at time of purchase. | [9 empty] | NOTES
APPLIANCE | LOCATION | QUANTITY | MFR | MODEL # | ENERGY STAR (Yes/No) | LOCATION (dwg/spec) | PLAN REVIEW | INSPECTION? | INSPECTION COMMENTS
+
-

## ES 6. Fenestration
Instructions: | Using Tables: Providing data in yellow cells on this tab prior to the Proposed Design submittal is optional, but recommended. Prior to As-Built submittal, complete all yellow cells based on installed fenestration. If Prescriptive Path or utilizing weighted average for U-factor compliance, complete Qty & Area for each window. Printing: Optimized for Landscape view.
Fenestration Verification
Select ENERGY STAR:
Pathway | Complete Project Information Tab |  | Prescriptive Path only | [5 empty] | Total UA Meets ENERGY STAR Requirements?
Climate Zone | Complete Project Information Tab |  | Wall Area |  |  | Window Area | Window-to-Wall Ratio |  | PASS
Version | Complete Project Information Tab
NOTES
Windows - Dwelling Units | [9 empty] | hide | hide | hide
ID | WINDOW TYPE | Fixed or Operable? (Prescriptive & Class AW Only) | Qty | Area | Total Area | Window Frame (ERI/ASHRAE & Class AW only) | ENERGY STAR Requirement U-FACTOR | ENERGY STAR Requirement UA | ENERGY STAR Requirement SHGC | WindowFrame_UIndex | WindowFrame_SHGCIndex | CZ_Index | PROJECTION FACTOR (PF) (ERI/ASHRAE & Class AW only) | ASSEMBLY U-FACTOR | Total UA | SHGC | LOCATION (dwg/spec) | PLAN REVIEW | INSPECTION? | INSPECTION COMMENTS
|  |  |  | 0 | 0 |  |  | 0 | [6 empty] | 0
Weighted U-factor:
NOTES
Windows - Common Spaces | [9 empty] | hide | hide | hide
ID | WINDOW TYPE (optional) | Fixed or Operable? (ERI & Prescriptive Only) | Qty | Area | Total Area | Window Frame (ASHRAE only) | ENERGY STAR Requirement U-FACTOR | ENERGY STAR Requirement UA | ENERGY STAR Requirement SHGC | WindowFrame_UIndex | WindowFrame_SHGCIndex | CZ_Index | PROJECTION FACTOR (PF) (ASHRAE only) | ASSEMBLY U-FACTOR | Total UA | SHGC | LOCATION (dwg/spec) | PLAN REVIEW | INSPECTION? | INSPECTION COMMENTS
|  |  |  | 0 | 0 |  |  | 0 | [6 empty] | 0
Weighted U-factor:
NOTES
All Exterior Doors (Opaque, Glazed, Partially Glazed) | [9 empty] | hide | hide | hide
ID | Door Type | Dwelling/ Common? | Qty | Area | Total Area | Space Served (optional) | ENERGY STAR Requirement U-FACTOR | ENERGY STAR Requirement UA | ENERGY STAR Requirement SHGC | Door Type_Uindex | Door Type_SHGCIndex | CZ_Index | PROJECTION FACTOR (PF) (ASHRAE only) | ASSEMBLY U-FACTOR | Total UA | SHGC | LOCATION (dwg/spec) | PLAN REVIEW | INSPECTION? | INSPECTION COMMENTS
|  |  |  | 0 | 0 |  |  | 0 | [6 empty] | 0
Weighted U-factor:
Footnote 5. All windows, doors and skylights must meet or exceed the U-factor and SHGC requirements specified in the table below. If no NFRC rating is noted on the window or in product literature (e.g., for site-built fenestration), select the U-factor and SHGC value from Tables 4 and 10, respectively, in 2013 ASHRAE Handbook of Fundamentals, Chapter 15. Select the highest U-factor and SHGC value among the values listed for the known window characteristics (e.g., frame type, number of panes, glass color, and presence of low-e coating). Note that the U-factor requirement applies to all fenestration while the SHGC only applies to the glazed portion.
| Dwelling unit doors and windows that are not classified “Class AW”* |  |  |  |  | Dwelling unit windows and doors that are classified as “Class AW”* | [5 empty] | Common Space†
ERI | 2009 IECC Table 402.1.1 |  |  |  |  | 2009 IECC Table 502.3 | [5 empty] | ENERGY STAR MF Reference Design – for Class AW
ASHRAE | 2009 IECC Table 402.1.1 |  |  |  |  | 2009 IECC Table 502.3 | [5 empty] | 2009 IECC Table 502.3
Prescriptive | ENERGY STAR MF Reference Design |  |  |  |  | ENERGY STAR MF Reference Design – for Class AW | [5 empty] | ENERGY STAR MF Reference Design – for Class AW
* Classified as “Class AW” under the North American Fenestration Standard (AAMA / WDMA / CSA 101 / I.S.2 / A440).
† Opaque doors in common spaces in CZ1-6 shall not exceed U-0.70, and in CZ 7-8, shall not exceed U-0.5.
The following exemptions apply:
i. An area-weighted average of fenestration products shall be permitted to satisfy the U-factor requirements;
ii. An area-weighted average of fenestration products ≥ 50% glazed shall be permitted to satisfy the SHGC requirements; and
iii. 5% of all combined fenestration area (glazed and opaque) shall be exempt from the U-factor and SHGC requirements, and shall be excluded from area-weighted averages calculated using i) and ii), above.
In PHIUS+ or PHI certified buildings, where triple-glazed window assemblies with thermal breaks / spacers between the panes are used, such windows meet the intent of Items 2.1 and 2.2 and shall be excluded when assessing compliance of i) through iii), above.
+
-
+
-
+
-

## ES 7. Heated Plenum or Garage
Instructions: | Using Tables: Providing data in yellow cells on this tab prior to the Proposed Design submittal is optional, but recommended. Prior to As-Built submittal, where heated plenum or heated garages are present, list the installed R-value, if not clearly shown in photo documentation. Exception: Per Rater Field Checklist, footnote 9, compliance with Items 1.5 and 1.6 is not required for ASHRAE projects, but the energy used by the heating systems must be modeled following the requirements in the Simulation Guidelines, available at www.energystar.gov/mfnc. Printing: Optimized for Portait view.
Select ENERGY STAR Version | Complete Project Information Tab | Select ENERGY STAR Climate Zone | Complete Project Information Tab |  | << CZ Reference Table Index
|  |  |  | 2 | << Mass Floors Index in the IECC2009_O_Floors Table
NOTES
Heated Plenum Insulation Verification
| ENERGY STAR Requirement | Specified/Installed R-value
Plenum Wall Insulation
Top of Plenum Insulation
Bottom of Plenum Insulation
Heated Garage Insulation Verification
| ENERGY STAR Requirement | Specified/Installed R-value
Garage Above Grade or First Floor Below Grade Wall Insulation
Garage Ceiling Insulation

## ES 8. DHW_SHW Schedule
Instructions: | Using Tables: Providing data in orange cells on this tab prior to the Proposed Design submittal is optional, but recommended. Prior to As-Built submittal, complete all orange cells. See below for specific instructions on using the Domestic Hot Water System Verification and the Low-Flow Fixture Verification tables. If make and model numbers were entered at the Proposed Design submittal, mark any changes from the Proposed Design in 'Inspection Comments' (Column M). Printing: Optimized for printing in Landscape view.
Domestic Hot Water / Service Hot Water System Verification
Instructions: | Complete entire table OR complete columns B, C, D and provide AHRI Certificate for each DHW/SHW system. | [10 empty] | NOTES
ID -DHW/SHW System | DESCRIPTION | LOCATION | MFR | MODEL # | AHRI CERT # |  |  | LOCATION (dwg/spec) | PLAN REVIEW | INSPECTION? | INSPECTION COMMENTS
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12
Low-Flow Fixture Verification
Instructions: | Prescriptive Path: Complete table and provide cut sheet/WaterSense documentation for each bath faucet, aerator, and showerhead. ASHRAE Path: (if taking credit for low-flow fixture) Complete table and provide cut sheet/WaterSense documentation for each faucet and showerhead, where credit is taken, that clearly identifies flow rate.
For shower compartments with multiple fixtures:
Column2: Operated simultaneously (Y/N)? | NOTES
|  |  | ASHRAE PATH ONLY | PRESCRIPTIVE PATH ONLY
ID - Low-Flow Fixtures | DESCRIPTION | Quantity | GPM | MFR | MODEL # | WaterSense? |  | LOCATION (dwg/spec) | PLAN REVIEW | INSPECTION? | INSPECTION COMMENTS
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12
+
-
+
-

## ES 9. Heating Cooling Schedule
Instructions: | Using Tables: Providing data in orange cells on this tab prior to the Proposed Design submittal is optional, but recommended. Prior to As-Built submittal, complete all orange cells. See below for specific instructions on using the Heating & Cooling System Verification and the Circulating Pump Motor Verification (non-DHW/SHW) tables. If make and model numbers were entered at the Proposed Design submittal, mark any changes from the Proposed Design in 'Inspection Comments' (Column M). Printing: Optimized for printing in Landscape view.
Heating & Cooling System Verification
Instructions: | Complete table OR provide schedule with AHRI certificate for each system in schedule. | [10 empty] | NOTES
ID | DESCRIPTION | HEATING/ COOLING | LOCATION/ SERVES | QUANTITY | MFR | AHRI CERT# | Column1 | LOCATION (dwg/spec) | PLAN REVIEW | INSPECTION? | INSPECTION COMMENTS
Circulating Pump Motor Verification (non-DHW/SHW)
Instructions: | Record manufacturer and model number of 3-phase pump motors over 1 HP, to confirm NEMA. If over 5 HP, confirm presence of VFD and provide photo of VFD. | [10 empty] | NOTES
ID | DESCRIPTION | LOCATION | MFR | MODEL # | HORSE POWER (HP) | NEMA PREMIUM? | VFD? | LOCATION (dwg/spec) | PLAN REVIEW | INSPECTION? | INSPECTION COMMENTS
+
-
+
-

## ES 10. Lighting
Instructions: | Using Tables: Providing data in orange cells on this tab prior to the Proposed Design submittal is optional, but recommended. Prior to As-Built submittal, use the As-Built lighting schedule and floor plans to complete all orange cells. Pass/Fail values will calculate automatically. Printing: Optimized for printing in Portrait view.
Lighting Verification (Lighting Power Density Calculation and 90% Efficient Fixtures)
Qualifying Tier I Light Fixture – A light fixture located in a Qualifying Light Fixture Location that contains fluorescent lamps. Qualifying Tier II Light Fixture – A light fixture located in a Qualifying Light Fixture Location that contains LED lamps; an integrated LED fixture; an outdoor light fixture that is controlled by a photocell; or an indoor fixture controlled by a motion sensor.
Dwelling Unit (Prescriptive Path only; ASHRAE Path can enter into APC)
Count All Fixtures | [5 empty] | Fixture Label | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
Are 90% Tier I/II or ES? | [5 empty] | Fixture Watts
Prescriptive Only: < 0.75? | [5 empty] | Efficacy
[34 empty] | hide | hide | hide | hide
Multiplier | Unit Plan | Room Type | Lit Area (SF) | Unlit Area (SF) | Watts/SF |  | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z |  | Total Fixtures | TierI/TierII/ES Fixtures | Watts (Lit Area) 3x | Warning?
Multiplier | Unit Plan | Room Type | Lit Area (SF) | Unlit Area (SF) | Watts/SF | Column20 | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z | Column19 | Total Fixtures | TierI/TierII/ES Fixtures | Watts (Lit Area) 3x | Warning?
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | 0
TOTALS | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Common Space (Prescriptive and ERI Path only; ASHRAE Path can enter into APC) | bar: A A to G G
Count All Fixtures |  | 0 |  |  |  | Fixture Label | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
Are 90% Tier I/II or ES? | [5 empty] | Fixture Watts | A: 10; B: 10; C: 15; D: 20; E: 30
Is it less than 90.1-2007? |  | PASS |  |  |  | Efficacy | A: ES; B: ES; C: ES; D: Tier II; E: ES
Are you using Space-by-Space Method or Building Area Method?
[34 empty] | hide | hide | hide | hide | hide | delete column | hide | hide
Multiplier | Space | ASHRAE Space Type | Lit Area (SF) | Automatic Controls? | Watts/SF | ASHRAE LPD (W/SF) | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z |  | Total Fixtures | Tier1/ES Fixtures | Lit Area * Multiplier | ASHRAE W | Installed Watts | PASS/FAIL
Multiplier | Space | ASHRAE Space Type | Lit Area (SF) | Automatic Controls? | Watts/SF | ASHRAE LPD (W/SF) | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z | Column14 | Total Fixtures | Tier1/ES Fixtures | Lit Area * Multiplier | ASHRAE W | Installed Watts | PASS/FAIL | 30%ASHRAE calc | ASHRAE LPD P/F
[34 empty] | 0 | 0 | [5 empty] | #VALUE!
[34 empty] | 0 | 0 | [5 empty] | #VALUE!
[34 empty] | 0 | 0 | [5 empty] | #VALUE!
[34 empty] | 0 | 0 | [5 empty] | #VALUE!
[34 empty] | 0 | 0 | [5 empty] | #VALUE!
[34 empty] | 0 | 0 | [5 empty] | #VALUE!
[34 empty] | 0 | 0 | [5 empty] | #VALUE!
[34 empty] | 0 | 0 | [5 empty] | #VALUE!
TOTALS | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Common Space Garage (Prescriptive and ERI Path only; ASHRAE Path can enter into APC) | bar: A A to G G
Less than 0.24 W/sf? | [5 empty] | Fixture Label | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
Fixture Watts
Efficacy
[34 empty] | hide | hide | hide | hide | hide | hide
Multiplier | Space | ASHRAE Space Type | Lit Area (SF) | Automatic Controls? | Watts/SF | MFNC LPD (W/SF) | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z |  | Total Fixtures | Tier1/ES Fixtures | ASHRAE W | Installed Watts | Column1 | PASS/FAIL
Multiplier | Space | ASHRAE Space Type | Lit Area (SF) | Automatic Controls? | Watts/SF | MFNC LPD (W/SF) | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z | Column17 | Total Fixtures | Tier1/ES Fixtures | ASHRAE W | Installed Watts | Column1 | PASS/FAIL
| Garage | Garage |  |  |  | 0.24 | [27 empty] | 0 | 0 | 0 |  | PASS
Exterior Lighting Fixtures (Prescriptive and ERI Path only; ASHRAE Path can enter into APC) | bar: A A to G G
Count All Fixtures | [5 empty] | Fixture Label | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z
Are 90% Tier I/II or ES? | [5 empty] | Efficacy
[34 empty] | hide | hide
[5 empty] | Space | Automatic Controls? | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z |  | Total Fixtures | TierI/TierII/ES Fixtures
[5 empty] | Space | Automatic Controls? | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z | Column20 | Total Fixtures | TierI/TierII/ES Fixtures
[34 empty] | 0 | 0
[34 empty] | 0 | 0
[34 empty] | 0 | 0
[34 empty] | 0 | 0
+
-
+
-
+
+
+
-
+
-
+
-

## ES 11. Ventilation Schedule
Instructions: | Using Tables: Providing data in orange cells on this tab prior to the Proposed Design submittal is optional, but recommended. Prior to As-Built submittal, complete all orange cells. See specific instructions below for completing the "In-Unit Dwelling Unit Ventilation and Local Exhaust Fans" and the "Central/Shared Dwelling Unit Ventilation and Local Exhaust Fans" tables. If make and model numbers were entered at the Proposed Design submittal, mark any changes from the Proposed Design in 'Inspection Comments' (Column O). Printing: Optimized for printing in Landscape view.
In-Unit Dwelling Unit Ventilation and Local Exhaust Fans
Instructions: | Complete table. In lieu of entering MFR/model, provide photo with model number, that lists ID in the file name of the photo, AND where applicable, submit evidence of listing in the ENERGY STAR Product Search at time of purchase. Note: In-unit bathroom fans or in-line fans are ENERGY STAR certified if used as part of the dwelling-unit mechanical ventilation system.
ID | DESCRIPTION (bath exhaust, range hood, inline fan, balanced, other) | PURPOSE | CONTINUOUS/ INTERMITTENT | MFR | MODEL # | Sones (7.5, 8.2) | ENERGY STAR? | Column1 | Column2 | LOCATION (dwg / spec) | PLAN REVIEW | INSPECTION | INSPECTION COMMENTS (Problems, sample details/apt #s, etc.)
NOTES
Central/Shared Dwelling Unit Ventilation and Local Exhaust Fans
Instructions: | Complete table or provide cut sheet with photo of fan nameplate that clearly identifies features meet requirements. Note: If central exhaust fans, ≤ 1 HP, are specified as part of the dwelling-unit mechanical ventilation system, then they are direct-drive, ECM, with variable speed controllers. If greater than 1 HP, they are specified with NEMA Premium Motors.
ID | DESCRIPTION | PURPOSE | MFR | MODEL # | Greater than 1 HP? | NEMA PREMIUM? | ECM? | DIRECT-DRIVE? | VARIABLE SPEED CONTROLLERS | LOCATION (dwg / spec) | PLAN REVIEW | INSPECTION | INSPECTION COMMENTS (Problems, sample details/apt #s, etc.)
NOTES
+
-
+
-

## ES Reference Tables
This tab contains tables related to the ENERGY STAR Multifamily New Construction Program
| TableRaterDF4 |  |  |  | TableRaterDF11 | [5 empty] | ESRefDesign_Insulation_V1 | [9 empty] | ESRefDesign_Insulation_V11 | [9 empty] | ESRefDesign_Insulation_V12 |  | ESRefDesign_Fenestration_V1 | [9 empty] | ESRefDesign_Fenestration_V11 | [9 empty] | ESRefDesign_Fenestration_V12
| ENERGY STAR Multifamily New Construction Rater Design Review Checklist - Footnote 4 |  |  |  | ENERGY STAR Multifamily New Construction Rater Design Review Checklist - Footnote 11 | [5 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1 Insulation Levels modeled to 2009 IECC levels (Commercial, wood frame) and Grade I installation per ANSI / RESNET / ICC Standard | [9 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1.1 Insulation Levels modeled to 2012 IECC levels (Commercial, wood frame) and Grade I installation per ANSI / RESNET / ICC Standard | [9 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1.2 Insulation Levels modeled at the levels below and Grade I installation per ANSI / RESNET / ICC Standard |  | ENERGY STAR Multifamily New Construction Reference Design, Version 1 Dwelling Unit Windows Infiltration rates modeled as follows: <0.30 CFM50/ft2 of enclosure. Windows and doors modeled, as illustrated below: | [9 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1.1 Dwelling Unit Windows Infiltration rates modeled as follows: <0.30 CFM50/ft2 of enclosure. Windows and doors modeled, as illustrated below: | [9 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1.2 Dwelling Unit Windows Infiltration rates modeled as follows: <0.30 CFM50/ft2 of enclosure. Windows and doors modeled, as illustrated below:
| Pathway | Dwelling unit doors and windows that are not classified “Class AW”* | Dwelling unit windows and doors that are classified as “Class AW”* | Common Space† |  | Number of Bedrooms |  |  |  |  | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | Insulation Level | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 4 C | CZ 5 | CZ 6
| ERI | 2009 IECC Table 402.1.1 | 2009 IECC Table 502.3 | ENERGY STAR MF Reference Design – for Class AW | Floor area | 1 | 2 | 3 | 4 | 5 | Slab Insulation R-Value: | NR | NR | NR | R-10 | R-10 | R-10 | R-15 | R-15 | R-20 | Slab Insulation R-Value: | NR | NR | NR | R-10 | R-10 | R-10 | R-15 | R-15 | R-20 | Above-Grade Wall | R-21 | Window U-Factor: | 0.6 | 0.6 | 0.35 | 0.32 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Window U-Factor: | 0.4 | 0.4 | 0.3 | 0.3 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | Window U-Factor: | 0.27 | 0.27 | 0.27
| ASHRAE | 2009 IECC Table 402.1.1 | 2009 IECC Table 502.3 | 2009 IECC Table 502.3 | <500 | 45 | 57 | 67.5 | 79.5 | 90 | Slab Insulation Depth (ft): | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | Slab Insulation Depth (ft): | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | Ceiling | R-49 | Window SHGC: | 0.27 | 0.27 | 0.3 | 0.4 | Any | Any | Any | Any | Any | Window SHGC: | 0.25 | 0.25 | 0.25 | 0.4 | Any | Any | Any | Any | Any | Window SHGC: | 0.3 | 0.3 | 0.3
| Prescriptive | ENERGY STAR MF Reference Design | ENERGY STAR MF Reference Design – for Class AW | ENERGY STAR MF Reference Design – for Class AW | 501-1000 | 67.5 | 79.5 | 90 | 102 | 112.5 | Basement Wall Continuous Insulation R-Value: | 0 | 0 | 0 | 7.5 | 7.5 | 7.5 | 7.5 | 10 | 12.5 | Basement Wall Continuous Insulation R-Value: | 0 | 0 | 0 | 7.5 | 7.5 | 7.5 | 7.5 | 10 | 12.5 | Floor | R-38 | Opaque Door U-Factor | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | Opaque Door U-Factor | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | Opaque Door U-Factor | 0.17 | 0.17 | 0.17
| * Classified as “Class AW” under the North American Fenestration Standard (AAMA / WDMA / CSA 101 / I.S.2 / A440). |  |  |  | 1001-1500 | 90 | 102 | 112.5 | 124.5 | 135 | Floor Assembly U-Factor: | 0.282 | 0.052 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | Floor Assembly U-Factor: | 0.066 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | Basement Wall | R-15 continuous or R-21 cavity | ≤½ lite Door U-Factor | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | ≤½ lite Door U-Factor | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | ≤½ lite Door U-Factor | 0.25 | 0.25 | 0.25
| † Opaque doors in common spaces in CZ1-6 shall not exceed U-0.70, and in CZ 7-8, shall not exceed U-0.5. |  |  |  | 1501-2000 | 112.5 | 124.5 | 135 | 147 | 157.5 | Wall Assembly U-Factor: | 0.089 | 0.089 | 0.089 | 0.064 | 0.064 | 0.064 | 0.051 | 0.051 | 0.036 | Wall Assembly U-Factor: | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.051 | 0.051 | 0.036 | On-Grade & Below Grade Slab | R-10 at perimeter for entire depth of slab and under entire slab area | >½ lite Door U-Factor: | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | >½ lite Door U-Factor: | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | >½ lite Door U-Factor: | 0.3 | 0.3 | 0.3
[5 empty] | 2001-2500 | 135 | 147 | 157.5 | 169.5 | 180 | Ceiling Assembly U-Factor: | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | Ceiling Assembly U-Factor: | 0.027 | 0.027 | 0.027 | 0.027 | 0.021 | 0.021 | 0.021 | 0.021 | 0.021 |  |  | Opaque Door SHGC | Any | Any | Any | Any | Any | Any | Any | Any | Any | Opaque Door SHGC | Any | Any | Any | Any | Any | Any | Any | Any | Any | Opaque Door SHGC | Any | Any | Any
|  | TableRaterFF68 |  |  | 2501-3000 | 157.5 | 169.5 | 180 | 192 | 202.5 | [22 empty] | ≤½ lite Door SHGC | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | ≤½ lite Door SHGC | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | ≤½ lite Door SHGC | 0.25 | 0.25 | 0.25
|  | ENERGY STAR Multifamily New Construction Rater Field Checklist - Footnote 68 |  |  | 3001-3500 | 180 | 192 | 202.5 | 214.5 | 225 | [22 empty] | >½ lite Door SHGC | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | >½ lite Door SHGC | 0.25 | 0.25 | 0.25 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | >½ lite Door SHGC | 0.3 | 0.3 | 0.3
|  | ASHRAE Space Type | Lighting Power Densities (W/ft2) |  | 3501-4000 | 202.5 | 214.5 | 225 | 237 | 247.5 | IECC2009_R_Roofs | [9 empty] | IECC2012_R_Roofs | [31 empty] | IECC2009_RU_Roof | [9 empty] | IECC2009_OU_Roof | [9 empty] | IECC2012_OU_Roof
|  | Lobby / Elevator | 1.3 |  | 4001-4500 | 225 | 237 | 247.5 | 259.5 | 270 | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - Group R - Roofs | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - Group R - Roofs | [11 empty] | ESRefDesign_FenestrationAW_V1 | [9 empty] | ESRefDesign_FenestrationAW_V11 | [9 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - Group R - Roofs | [9 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Roofs | [9 empty] | 2012 IECC Table C402.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Roofs
|  | Active Storage (e.g., trash chute / room, janitor closet) | 0.8 |  | 4501-5000 | 247.5 | 259.5 | 270 | 282 | 292.5 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 |  |  | ENERGY STAR Multifamily New Construction Reference Design, Version 1, Class AW Common Area - Class AW Windows in Dwelling Units Exception: Class AW windows modeled to 2012 IECC levels (Commercial window U-Factor requirements) | [9 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1.1, Class AW Common Area - Class AW Windows in Dwelling Units Exception: Class AW windows modeled to 2012 IECC levels (Commercial window U-Factor requirements) | [9 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
|  | Inactive Storage (e.g., tenant storage) | 0.3 | [7 empty] | Insulation entirely above deck | R-37ci | R-37ci | R-37ci | R-37ci | R-37ci | R-37ci | R-37ci | R-37ci | R-37ci | Insulation entirely above deck | R-37ci | R-37ci | R-37ci | R-37ci | R-48ci | R-48ci | R-48ci | R-48ci | R-48ci |  |  | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Insulation entirely above deck | U-0.048 | U-0.048 | U-0.048 | U-0.048 | U-0.048 | U-0.048 | U-0.048 | U-0.039 | U-0.039 | Insulation entirely above deck | U-0.063 | U-0.048 | U-0.048 | U-0.048 | U-0.048 | U-0.048 | U-0.048 | U-0.039 | U-0.039 | Insulation entirely above deck | U-0.048 | U-0.048 | U-0.048 | U-0.039 | U-0.039 | U-0.039 | U-0.032 | U-0.028 | U-0.028
|  | Exercise Area / Room | 0.9 | [7 empty] | Metal buildings (with R-5 thermal blocksa,b) | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | Metal buildings (with R-5 thermal blocksa,b) | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-13 | R-10 + R-19 + R-24 | R-10 + R-19 + R-24 | R-10 + R-19 + R-24 | R-10 + R-19 + R-24 | R-10 + R-19 + R-24 |  |  | Fixed Window U-Factor | 0.5 | 0.5 | 0.46 | 0.38 | 0.38 | 0.38 | 0.36 | 0.29 | 0.29 | Fixed Window U-Factor | 0.48 | 0.48 | 0.44 | 0.36 | 0.36 | 0.36 | 0.34 | 0.28 | 0.28 | Metal buildings | U-0.065 | U-0.055 | U-0.055 | U-0.055 | U-0.055 | U-0.055 | U-0.049 | U-0.049 | U-0.035 | Metal buildings | U-0.065 | U-0.055 | U-0.055 | U-0.055 | U-0.055 | U-0.055 | U-0.049 | U-0.049 | U-0.035 | Metal buildings | U-0.044 | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.031 | U-0.029 | U-0.029
|  | Corridor / Transition | 0.5 | [7 empty] | Attic and other | R-38 | R-38 | R-38 | R-38 | R-38 | R-38 | R-38 | R-38 | R-49 | Attic and other | R-38 | R-38 | R-38 | R-38 | R-49 | R-49 | R-49 | R-49 | R-49 |  |  | Operable Window U-Factor | 0.65 | 0.65 | 0.6 | 0.45 | 0.45 | 0.45 | 0.43 | 0.37 | 0.37 | Operable Window U-Factor | 0.62 | 0.62 | 0.57 | 0.43 | 0.43 | 0.43 | 0.41 | 0.35 | 0.35 | Attic and other | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | Attic and other | U-0.034 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | Attic and other | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.027 | U-0.021 | U-0.021 | U-0.021
|  | Stairs - Active | 0.6 | [29 empty] | SHGC | 0.27 | 0.27 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | Any | Any | SHGC | 0.25 | 0.25 | 0.25 | 0.4 | 0.4 | 0.4 | 0.4 | Any | Any
|  | Restroom | 0.9 | [7 empty] | IECC2009_R_WallsAboveGrade | [9 empty] | IECC2012_R_WallsAboveGrade | [31 empty] | IECC2009_RU_WallAboveGrade | [9 empty] | IECC2009_OU_WallAboveGrade | [9 empty] | IECC2012_OU_WallAboveGrade
|  | Laundry Room | 1.3 | [7 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - Group R - Walls, Above Grade | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - Group R - Walls, Above Grade | [11 empty] | IECC2009_Fenestration_NotAW_Windows | [9 empty] | ESRefDesign_FenestrationAW_V12 | [9 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - Group R - Walls, Above Grade | [9 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Walls, Above Grade | [9 empty] | 2012 IECC Table C402.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Walls, Above Grade
|  | Office | 1.1 | [7 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 |  |  | 2009 IECC Table 402.1.1 - Insulation and Fenestration Requirements by Component Dwelling unit doors and windows that are not classified “Class AW”* | [9 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1.2, Class AW Common Area - Class AW Windows in Dwelling Units Exception: Class AW windows modeled to 2012 IECC levels (Commercial window U-Factor requirements) | [9 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
|  | Lounge / Recreation / Community Room / Computer Room | 1.2 | [7 empty] | Mass | R-12.5ci | R-12.5ci | R-12.5ci | R-18.8ci | R-18.8ci | R-18.8ci | R-25.2ci | R-25.2ci | R-37ci | Mass | R-18.8ci | R-18.8ci | R-18.8ci | R-18.8ci | R-18.8ci | R-18.8ci | R-25.2ci | R-25.2ci | R-37ci |  |  | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 4 C | CZ 5 | CZ 6 | [6 empty] | Mass | U-0.151 | U-0.123 | U-0.104 | U-0.090 | U-0.080 | U-0.080 | U-0.071 | U-0.071 | U-0.052 | Mass | U-0.58 | U-0.151 | U-0.123 | U-0.104 | U-0.090 | U-0.090 | U-0.080 | U-0.071 | U-0.071 | Mass | U-0.142 | U-0.142 | U-0.110 | U-0.104 | U-0.078 | U-0.078 | U-0.078 | U-0.061 | U-0.061
|  | Electrical / Mechanical | 1.5 | [7 empty] | Metal buildingb | R-16 + R-5.5ci | R-16 + R-5.5ci | R-19 + R-5.2ci | R-19 + R-8.9ci | R-13 + R-9.6ci | R-13 + R-9.6ci | R-13 + R-13.5ci | R-19 + R-12.7ci | R-19 + R-30.6ci | Metal building | R-13 + R-9.6ci | R-13 + R-9.6ci | R-13 + R-9.6ci | R-13 + R-9.6ci | R-13 + R-9.6ci | R-13 + R-9.6ci | R-13 + R-13.5ci | R-19 + R-12.7ci | R-19 + R-30.6ci |  |  | Fenestration U-Factor | 1.2 | 0.65 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | Fixed Window U-Factor | 0.36 | 0.36 | 0.34 | [6 empty] | Metal building | U-0.093 | U-0.093 | U-0.084 | U-0.084 | U-0.069 | U-0.069 | U-0.069 | U-0.057 | U-0.057 | Metal building | U-0.093 | U-0.093 | U-0.084 | U-0.084 | U-0.069 | U-0.069 | U-0.069 | U-0.057 | U-0.057 | Metal building | U-0.079 | U-0.079 | U-0.079 | U-0.052 | U-0.052 | U-0.052 | U-0.052 | U-0.052 | U-0.052
|  | Workshop | 1.9 | [7 empty] | Metal framed | R-13 + R-3.3ci OR R-19 + R-2.1ci | R-13 + R-3.3ci OR R-19 + R-2.1ci | R-13 + R-3.3ci OR R-19 + R-2.1ci | R-13 + R-7.5ci OR R-19 + R-6.5ci | R-13 + R-7.5ci OR R-19 + R-6.5ci | R-13 + R-7.5ci OR R-19 + R-6.5ci | R-13 + R-11.5ci OR R-19 + R-10.5ci | R-13 + R-11.5ci OR R-19 + R-10.5ci | R-13 + R-20ci OR R-19 + 18.6ci | Metal framed | R-13 + R-7.5ci OR R-19 + R-6.5ci | R-13 + R-7.5ci OR R-19 + R-6.5ci | R-13 + R-7.5ci OR R-19 + R-6.5ci | R-13 + R-7.5ci OR R-19 + R-6.5ci | R-13 + R-7.5ci OR R-19 + R-6.5ci | R-13 + R-7.5ci OR R-19 + R-6.5ci | R-13 + R-11.5ci OR R-19 + R-10.5ci | R-13 + R-11.5ci OR R-19 + R-10.5ci | R-13 + R-20ci OR R-19 + 18.6ci |  |  | Skylight U-Factor | 0.75 | 0.75 | 0.65 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | Operable Window U-Factor | 0.43 | 0.43 | 0.41 | [6 empty] | Metal framed | U-0.124 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.057 | U-0.052 | U-0.037 | Metal framed | U-0.124 | U-0.124 | U-0.084 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | Metal framed | U-0.077 | U-0.077 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.045
|  | Garage | 0.24 | [7 empty] | Wood framed and other | R-13 | R-13 | R-13 | R-13 + R-3.8ci | R-13 + R-3.8ci | R-13 + R-3.8ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-15.6ci | Wood framed and other | R-13 + R-3.8ci or R-20 | R-13 + R-3.8ci or R-20 | R-13 + R-3.8ci or R-20 | R-13 + R-3.8ci or R-20 | R-13 + R-7.5ci or R-20 + R-3.8ci | R-13 + R-7.5ci or R-20 + R-3.8ci | R-13 + R-7.5ci or R-20 + R-3.8ci | R-13 + R-7.5ci or R-20 + R-3.8ci | R-13 + R-15.6ci or R-20 + R-10ci |  |  | Glazed Fenestration SHGC | 0.3 | 0.3 | 0.3 | NR | NR | NR | NR | NR | NR | SHGC | 0.3 | 0.3 | 0.3 | [6 empty] | Wood framed and other | U-0.089 | U-0.089 | U-0.089 | U-0.064 | U-0.051 | U-0.051 | U-0.051 | U-0.051 | U-0.036 | Wood framed and other | U-0.089 | U-0.089 | U-0.089 | U-0.089 | U-0.064 | U-0.064 | U-0.051 | U-0.051 | U-0.036 | Wood framed and other | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.064 | U-0.051 | U-0.051 | U-0.036
[33 empty] | Ceiling R-Value | 30 | 30 | 30 | 38 | 38 | 38 | 49 | 49 | 49
|  | ExhibitX | [8 empty] | IECC2009_R_WallsBelowGrade | [9 empty] | IECC2012_R_WallsBelowGrade | [11 empty] | Wood Frame Wall R-Value | 13 | 13 | 13 | 13 | 20 or 13+5h | 20 or 13+5h | 20 or 13+5h | 21 | 21 | [10 empty] | IECC2009_RU_WallBelowGrade | [9 empty] | IECC2009_OU_WallBelowGrade | [9 empty] | IECC2012_OU_WallBelowGrade
|  | ENERGY STAR Multifamily New Construction Rater Field Checklist - Exhibit X | [8 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - Group R - Walls, Below Grade | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - Group R - Walls, Below Grade | [11 empty] | Mass Wall R-Value | 3/4 | 4/6 | 5/8 | 5/10 | 13/17 | 13/17 | 13/17 | 15/19 | 19/21 | [10 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - Group R - Walls, Below Grade | [9 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Walls, Below Grade | [9 empty] | 2012 IECC Table C402.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Walls, Below Grade
|  | Equipment Type | Minimum Efficiency | [7 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 |  |  | Floor R-Value | 13 | 13 | 19 | 19 | 30g | 30g | 30g | 38g | 38g | [10 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
|  | Room AC ( window, through-wall, ductless mini-splits) | ENERGY STAR certified | [7 empty] | Below grade walld | NR | NR | NR | R-7.5ci | R-7.5ci | R-7.5ci | R-7.5ci | R-10ci | R-12.5ci | Below grade walld | NR | NR | NR | R-7.5ci | R-7.5ci | R-7.5ci | R-7.5ci | R-10ci | R-12.5ci |  |  | Basement Wall R-Value | 0 | 0 | 5/13f | 10/13 | 10/13 | 10/13 | 15/19 | 15/19 | 15/19 | [10 empty] | Below grade wall | C-1.140 | C-1.140 | C-1.140 | C-0.119 | C-0.119 | C-0.119 | C-0.119 | C-0.092 | C-0.075 | Below grade wall | C-1.140 | C-1.140 | C-1.140 | C-1.140 | C-0.119 | C-0.119 | C-0.119 | C-0.119 | C-0.119 | Below grade wall | C-1.140 | C-1.140 | C-1.140 | C-0.119 | C-0.119 | C-0.119 | C-0.119 | C-0.092 | C-0.092
|  | Air conditioners, air cooled (<13 KBtu/h) | 13 SEER | [29 empty] | Slab R-Value & Depth | NR | NR | NR | R-10, 2 ft | R-10, 2 ft | R-10, 2 ft | R-10, 4 ft | R-10, 4 ft | R-10, 4 ft
|  | Air conditioners, air cooled (≥13 and <65 KBtu/h) | See Reference Design | [7 empty] | IECC2009_R_Floors | [9 empty] | IECC2012_R_Floors | [11 empty] | Crawl Space Wall R-Value | 0 | 0 | 5/13 | 10/13 | 10/13 | 10/13 | 10/13 | 10/13 | 10/13 | [10 empty] | IECC2009_RU_Floor | [9 empty] | IECC2009_OU_Floor | [9 empty] | IECC2012_OU_Floor
|  | Air conditioners, air cooled (≥65 and <240 KBtu/h) | 11.5 EER/12.0 IEER | [7 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - Group R - Floors | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - Group R - Floors | [31 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - Group R - Floors | [9 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Floors | [9 empty] | 2012 IECC Table C402.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Floors
|  | Air conditioners, air cooled (≥240 and < 760 KBtu/h) | 10.0 EER/10.5 IEER | [7 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 |  |  | IECC2009_Fenestration_AW_Windows | [19 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
|  | Electric resistance space heating | · Not permitted in any dwelling unit using the Prescriptive Path · Electric resistance heating specified in common spaces has a total heating capacity ≤ 12 kBtu/h (3.5 kW) per enclosed space and has automatic thermostatic controls | [7 empty] | Mass | NR | R-16.3ci | R-27.5ci | R-27.5ci | R-27.5ci | R-27.5ci | R-27.5ci | R-27.5ci | R-27.5ci | Mass | R-12ci | R-27.5ci | R-27.5ci | R-27.5ci | R-27.5ci | R-27.5ci | R-27.5ci | R-27.5ci | R-27.5ci |  |  | 2009 IECC Table 502.3 - Building Envelope Requirements: Fenestration | [19 empty] | Mass | U-0.322 | U-0.087 | U-0.087 | U-0.074 | U-0.064 | U-0.064 | U-0.057 | U-0.051 | U-0.051 | Mass | U-0.322 | U-0.107 | U-0.107 | U-0.087 | U-0.074 | U-0.074 | U-0.064 | U-0.064 | U-0.057 | Mass | U-0.322 | U-0.107 | U-0.076 | U-0.076 | U-0.074 | U-0.074 | U-0.064 | U-0.055 | U-0.055
|  | Warm-Air Furnace (<225 KBtu/h, common spaces) | 78% AFUE or 80% Et | [7 empty] | Joist/framing Steel/(wood) | NR | R-30 | R-30 | R-30 | R-30 | R-30 | R-30e | R-30e | R-30e | Joist/framing Steel/(wood) | NR | R-30 | R-30 | R-30 | R-30 | R-30 | R-30e | R-30e | R-30e |  |  | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | [10 empty] | Joist/framing | U-0.282 | U-0.052 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | Joist/framing | U-0.282 | U-0.052 | U-0.052 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | Joist/framing | U-0.066 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.033
|  | Warm-Air Furnace (<225 KBtu/h, dwelling units) | See Reference Design | [29 empty] | Non-Metal | 1.2 | 0.75 | 0.65 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
|  | Warm-Air Furnace (≥225 KBtu/h) | 80% Et (gas) or 81% Et (oil) | [7 empty] | IECC2009_R_SlabOnGradeFloors | [9 empty] | IECC2012_R_SlabOnGradeFloors | [11 empty] | Metal - Curtainwall/storefront | 1.2 | 0.7 | 0.6 | 0.5 | 0.45 | 0.45 | 0.45 | 0.4 | 0.4 | [10 empty] | IECC2009_RU_SlabOnGradeFloor | [9 empty] | IECC2009_OU_SlabOnGradeFloor | [9 empty] | IECC2012_OU_SlabOnGradeFloor
|  | Packaged Terminal Air Conditioner (PTAC) | 13.8 – (0.300 X Cap/1000) EER | [7 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - Group R - Slab-on-Grade Floors | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - Group R - Slab-on-Grade Floors | [11 empty] | Metal - Entrance door | 1.2 | 1.1 | 0.9 | 0.85 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [10 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - Group R - Slab-on-Grade Floors | [9 empty] | 2009 IECC Table 502.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Slab-on-Grade Floors | [9 empty] | 2012 IECC Table C402.1.2 - Building Envelope Requirements - Opaque Element - Maximum U-Factors - All Other - Slab-on-Grade Floors
|  | Packaged Terminal Heat Pump (PTHP) | Cooling: 14.0– (0.3 X Cap/1000) EER Heating: 3.7– (0.052 X Cap/1000) COP | [7 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 |  |  | Metal - Other | 1.2 | 0.75 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.45 | [10 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
|  | Air cooled heat pump (≥13 and <65 KBtu/h) | See Reference Design | [7 empty] | Unheated slabs | NR | NR | NR | R-10 for 24 in. below | R-10 for 24 in. below | R-10 for 24 in. below | R-15 for 24 in. below | R-15 for 24 in. below | R-20 for 24 in. below | Unheated slabs | NR | NR | NR | R-10 for 24 in. below | R-10 for 24 in. below | R-10 for 24 in. below | R-15 for 24 in. below | R-15 for 24 in. below | R-20 for 24 in. below |  |  | Skylights | 0.75 | 0.75 | 0.65 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | [10 empty] | Unheated slabs | F-0.730 | F-0.730 | F-0.730 | F-0.540 | F-0.540 | F-0.540 | F-0.520 | F-0.520 | F-0.510 | Unheated slabs | F-0.730 | F-0.730 | F-0.730 | F-0.730 | F-0.730 | F-0.730 | F-0.540 | F-0.520 | F-0.520 | Unheated slabs | F-0.73 | F-0.73 | F-0.73 | F-0.54 | F-0.54 | F-0.54 | F-0.54 | F-0.40 | F-0.40
|  | Air cooled heat pump (≥65 and <240 KBtu/h) | Cooling: 11.1 EER/11.6 IEER Heating: 3.3 COP (@47°F DB) | [7 empty] | Heated slabs | R-7.5 for 12 in. below | R-7.5 for 12 in. below | R-10 for 24 in. below | R-15 for 24 in. below | R-15 for 24 in. below | R-15 for 24 in. below | R-20 for 48 in. below | R-20 for 48 in. below | R-20 for 48 in. below | Heated slabs | R-7.5 for 12 in. below | R-7.5 for 12 in. below | R-10 for 24 in. below | R-15 for 24 in. below | R-15 for 36 in. below | R-15 for 36 in. below | R-20 for 48 in. below | R-20 for 48 in. below | R-20 for 48 in. below |  |  | SHGC PF < 0.25 | 0.25 | 0.25 | 0.25 | 0.4 | 0.4 | 0.4 | 0.4 | 0.45 | 0.45 | [10 empty] | Heated slabs | F-1.020 | F-1.020 | F-0.900 | F-0.860 | F-0.860 | F-0.860 | F-0.688 | F-0.688 | F-0.688 | Heated slabs | F-1.020 | F-1.020 | F-0.900 | F-0.860 | F-0.860 | F-0.860 | F-0.860 | F-0.830 | F-0.688 | Heated slabs | F-0.70 | F-0.70 | F-0.70 | F-0.65 | F-0.58 | F-0.58 | F-0.58 | F-0.55 | F-0.55
|  | Air cooled heat pump (≥240 KBtu/h) | Cooling: 9.6 EER/9.6 IEER Heating: 3.2 COP (@47°F DB) | [29 empty] | SHGC 0.25 < PF < 0.5 | 0.33 | 0.33 | 0.33 | NR | NR | NR | NR | NR | NR
|  | Water-source heat pump (<135 KBtu/h) | Cooling: 14.0 EER(86°F entering water) Heating: 4.2 COP(68°F entering water) | [7 empty] | IECC2009_R_OpaqueDoors | [9 empty] | IECC2012_R_OpaqueDoors | [11 empty] | SHGC PF >= 0.5 | 0.4 | 0.4 | 0.4 | NR | NR | NR | NR | NR | NR
|  | Boilers, hot water (<300,000 Btu/h) | See Reference Design | [7 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - Group R - Opaque Doors | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - Group R - Opaque Doors | [11 empty] | SHGC Skylights | 0.35 | 0.35 | 0.35 | 0.4 | 0.4 | 0.4 | 0.4 | NR | NR
|  | Boilers, hot water (≥300,000 Btu/h) | 86% Et (89% Et if using heat pumps) | [7 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
|  | VRF Air Conditioners and Heat Pumps | See Tables 6.8.1I and 6.8.1J of ASHRAE 90.1-2010 | [7 empty] | Swinging | U-0.70 | U-0.70 | U-0.70 | U-0.70 | U-0.70 | U-0.70 | U-0.50 | U-0.50 | U-0.50 | Swinging | U-0.61 | U-0.61 | U-0.61 | U-0.61 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37 |  |  | IECC2009_Equivalent_Ufactors
|  | Air-cooled chillers with or without condenser | 10.0 EER / 12.5 IPLV | [7 empty] | Roll-up or sliding | U-1.45 | U-1.45 | U-1.45 | U-0.50 | U-0.50 | U-0.50 | U-0.50 | U-0.50 | U-0.50 | Roll-up or sliding | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75 |  |  | 2009 IECC Table 402.1.3 - Equivalent U-Factors
|  | Water-cooled chiller, positive displacement (<75 tons) | 0.780 kW/ton (Full load) / 0.630 kW/ton (IPLV) | [29 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
|  | Water-cooled chiller, positive displacement (75-150 tons) | 0.775 kW/ton (Full load) / 0.615 kW/ton (IPLV) | [7 empty] | For SI: 1 inch = 25.4 mm. | [9 empty] | For SI: 1 inch = 25.4 mm. | [11 empty] | Fenestration U-Factor | 1.2 | 0.65 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
|  | Water-cooled chiller, positive displacement (150-300tons) | 0.680 kW/ton (Full load) / 0.580 kW/ton (IPLV) | [7 empty] | ci = Continuous insulation | [9 empty] | ci = Continuous insulation | [11 empty] | Skylight U-Factor | 0.75 | 0.75 | 0.65 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
|  | Water-cooled chiller, positive displacement (>300 tons) | 0.620 kW/ton (Full load) / 0.540 kW/ton (IPLV) | [7 empty] | NR = No requirement | [9 empty] | NR = No requirement | [11 empty] | Ceiling U-Factor | 0.035 | 0.035 | 0.035 | 0.03 | 0.03 | 0.03 | 0.026 | 0.026 | 0.026
|  | Water-cooled, centrifugal (<300 tons) | 0.634 kW/ton (Full load) / 0.596 kW/ton (IPLV) | [7 empty] | a. When using R-value compliance method, a thermal spacer block is required, otherwise use the U-factor complaince method. [see Tables 502.1.2 and 502.2(2)]. | [9 empty] | a. Assembly descriptions can be found in ANSI/ASHRAE/IESNA Appendix A. | [11 empty] | Frame Wall U-Factor | 0.082 | 0.082 | 0.082 | 0.082 | 0.057 | 0.057 | 0.057 | 0.057 | 0.057
|  | Water-cooled, centrifugal (≥300 and <600 tons) | 0.576 kW/ton (Full load) / 0.549 kW/ton (IPLV) | [7 empty] | b. Assembly descriptions can be found in Table 502.2(2). | [9 empty] | b. Where using R-vale compliance method, a thermal spacer block shall be provided, otherwise use the U-factor compliance method in Table C402.1.2. | [11 empty] | Mass Wall U-Factor | 0.197 | 0.165 | 0.141 | 0.141 | 0.082 | 0.082 | 0.060 | 0.057 | 0.057
|  | Water-cooled, centrifugal (≥600 tons) | 0.570 kW/ton (Full load) / 0.539 kW/ton (IPLV) | [7 empty] | c. R-5.7 ci is allowed to be substituted with concrete block walls complying with ASTM C 90, ungrouted or partially grouted at 32 inches or less on vertically and 48 inches or less on center horizontally, with ungrouted cores filled with materials having a maximum thermal coductivity of 0.44 Btu-in./h-f2 F | [9 empty] | c. R-5.7 ci is allowed to be substituted with concrete block walls complying with ASTM C 90, ungrouted or partially grouted at 32 inches or less on vertically and 48 inches or less on center horizontally, with ungrouted cores filled with materials having a maximum thermal coductivity of 0.44 Btu-in./h-f2 F | [11 empty] | Floor U-Factor | 0.064 | 0.064 | 0.047 | 0.047 | 0.033 | 0.033 | 0.033 | 0.028 | 0.028
|  | Air-cooled absorption single effect chiller | 0.6 COP | [7 empty] | d. When heated slabs are placed below grade, below-grade walls must meet the exterior insulation requirements for permimeter insulation according to heated slab-on-grade construction. | [9 empty] | d. Where heated slabs are placed below grade, below-grade walls shall comply with the exterior insulation requirements for heated slabs. | [11 empty] | Basement Wall U-Factor | 0.36 | 0.36 | 0.091c | 0.059 | 0.059 | 0.059 | 0.050 | 0.050 | 0.050
|  | Water-cooled absorption single effect chiller | 0.7 COP | [7 empty] | e. Steel floor joist systems shall be R-38. | [9 empty] | e. Steel floor joist systems shall be insulated to R-38. | [11 empty] | Crawl Space Wall U-Factor | 0.477 | 0.477 | 0.136 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
|  | Absorption double effect indirect-fired chiller | 1.0 COP (Full load) / 1.05 COP (IPLV)
|  | Absorption double effect direct-fired chiller | 1.0 COP (Full load) / 1.00 COP (IPLV)
|  | Open-loop propeller or axial fan cooling towers* | >40 gpm/hp (@95°F entering water, 85°F leaving water, 75°F wb entering air) | [7 empty] | IECC2009_O_Roofs | [9 empty] | IECC2012_O_Roofs
|  | Closed-loop propeller or axial fan cooling towers* | >15 gpm/hp (@102°F entering water, 90°F leaving water, 75°F wb entering air) | [7 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - All Other - Roofs | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - All Other - Roofs
|  | Open-loop centrifugal fan cooling towers* | >22 gpm/hp (@95°F entering water, 85°F leaving water, 75°F wb entering air) | [7 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
|  | Closed-loop centrifugal fan cooling towers* | >8 gpm/hp (@102°F entering water, 90°F leaving water, 75°F wb entering air) | [7 empty] | Insulation entirely above deck | R-15ci | R-20ci | R-20ci | R-20ci | R-20ci | R-20ci | R-20ci | R-25ci | R-25ci | Insulation entirely above deck | R-20ci | R-20ci | R-20ci | R-25ci | R-25ci | R-25ci | R-30ci | R-35ci | R-35ci
|  | Cap means the rated capacity of the product in Btu/h. If < 7,000 Btu/h, use 7,000; if > 15,000, use 15,000 in calculation. | [8 empty] | Metal buildings (with R-5 thermal blocksa,b) | R-19 | R-13 + R-13 | R-13 + R-13 | R-13 + R-13 | R-13 + R-13 | R-13 + R-13 | R-13 + R-19 | R-13 + R-19 | R-11 + R-19 | Metal buildings (with R-5 thermal blocksa,b) | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS | R-25 + R-11 LS | R-30 + R-11 LS | R-30 + R-11 LS
|  | *Cooling tower fan motors must be equipped with VFD controlled by a temperature sensor on the condenser water supply pipe. | [8 empty] | Attic and other | R-30 | R-38 | R-38 | R-38 | R-38 | R-38 | R-38 | R-38 | R-49 | Attic and other | R-38 | R-38 | R-38 | R-38 | R-38 | R-38 | R-49 | R-49 | R-49
[11 empty] | IECC2009_O_WallsAboveGrade | [9 empty] | IECC2012_O_WallsAboveGrade
[11 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - All Other - Walls, Above Grade | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - All Other - Walls, Above Grade
[11 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
[11 empty] | Mass | NR | R-5.7ci | R-7.6ci | R-9.5ci | R-11.4ci | R-11.4ci | R-13.3ci | R-15.2ci | R-25ci | Mass | R-5.7ci | R-5.7ci | R-7.6ci | R-9.5ci | R-11.4ci | R-11.4ci | R-13.3ci | R-15.2ci | R-25ci
[11 empty] | Metal buildingb | R-16 | R-16 | R-19 | R-19 | R-13 + R-5.6ci | R-13 + R-5.6ci | R-13 + R-5.6ci | R-19 + R-5.6ci | R-19 + R-5.6ci | Metal building | R-13 + R-6.5ci | R-13 + R-6.5ci | R-13 + R-6.5ci | R-13 + R-13ci | R-13 + R-13ci | R-13 + R-13ci | R-13 + R-13ci | R-13 + R-13ci | R-13 + R-13ci
[11 empty] | Metal framed | R-13 | R-13 | R-13 + R-3.8ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | Metal framed | R-13 + R-5ci | R-13 + R-5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-7.5ci
[11 empty] | Wood framed and other | R-13 | R-13 | R-13 | R-13 | R-13 + R-3.8ci | R-13 + R-3.8ci | R-13 + R-7.5ci | R-13 + R-7.5ci | R-13 + R-15.6ci | Wood framed and other | R-13 + R-3.8ci or R-20 | R-13 + R-3.8ci or R-20 | R-13 + R-3.8ci or R-20 | R-13 + R-3.8ci or R-20 | R-13 + R-3.8ci or R-20 | R-13 + R-3.8ci or R-20 | R-13 + R-7.5ci or R-20 +R-3.8ci | R-13 + R-7.5ci or R-20 +R-3.8ci | R-13 + R-15.6ci or R-20 +R-10ci
[11 empty] | IECC2009_O_WallsBelowGrade | [9 empty] | IECC2012_O_WallsBelowGrade
[11 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - All Other - Walls, Below Grade | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - All Other - Walls, Below Grade
[11 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
[11 empty] | Below grade walld | NR | NR | NR | NR | R-7.5ci | R-7.5ci | R-7.5ci | R-7.5ci | R-7.5ci | Below grade walld | NR | NR | NR | R-7.5ci | R-7.5ci | R-7.5ci | R-7.5ci | R-10ci | R-10ci
[11 empty] | IECC2009_O_Floors | [9 empty] | IECC2012_O_Floors
[11 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - All Other - Floors | [9 empty] | 2012 IECC TTable C402.2 - Building Envelope Requirements - Opaque Assemblies - All Other - Floors
[11 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
[11 empty] | Mass | NR | R-6.3ci | R-6.3ci | R-10ci | R-10ci | R-10ci | R-12.5ci | R-15ci | R-15ci | Mass | NR | R-6.3ci | R-10ci | R-10ci | R-10ci | R-10ci | R-12.5ci | R-15ci | R-15ci
[11 empty] | Joist/framing Steel/(wood) | NR | R-19 | R-19 | R-30 | R-30 | R-30 | R-30 | R-30 | R-30e | Joist/framing Steel/(wood) | NR | R-30 | R-30 | R-30 | R-30 | R-30 | R-30 | R-30e | R-30e
[11 empty] | IECC2009_O_SlabOnGradeFloors | [9 empty] | IECC2012_O_SlabOnGradeFloors
[11 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - All Other - Slab-on-Grade Floors | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - All Other - Slab-on-Grade Floors
[11 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
[11 empty] | Unheated slabs | NR | NR | NR | NR | NR | NR | R-10 for 24 in. below | R-15 for 24 in. below | R-15 for 24 in. below | Unheated slabs | NR | NR | NR | R-10 for 24 in. below | R-10 for 24 in. below | R-10 for 24 in. below | R-10 for 24 in. below | R-15 for 24 in. below | R-15 for 24 in. below
[11 empty] | Heated slabs | R-7.5 for 12 in. below | R-7.5 for 12 in. below | R-10 for 24 in. below | R-15 for 24 in. below | R-15 for 24 in. below | R-15 for 24 in. below | R-15 for 24 in. below | R-20 for 24 in. below | R-20 for 48 in. below | Heated slabs | R-7.5 for 12 in. below | R-7.5 for 12 in. below | R-10 for 24 in. below | R-15 for 24 in. below | R-15 for 36 in. below | R-15 for 36 in. below | R-15 for 36 in. below | R-20 for 24 in. below | R-20 for 48 in. below
[11 empty] | IECC2009_O_OpaqueDoors | [9 empty] | IECC2012_O_OpaqueDoors
[11 empty] | 2009 IECC Table 502.2(1) - Building Envelope Requirements - Opaque Assemblies - All Other - Opaque Doors | [9 empty] | 2012 IECC Table C402.2 - Building Envelope Requirements - Opaque Assemblies - All Other - Opaque Doors
[11 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8
[11 empty] | Swinging | U-0.70 | U-0.70 | U-0.70 | U-0.70 | U-0.70 | U-0.70 | U-0.70 | U-0.50 | U-0.50 | Swinging | U-0.61 | U-0.61 | U-0.61 | U-0.61 | U-0.37 | U-0.37 | U-0.37 | U-0.37 | U-0.37
[11 empty] | Roll-up or sliding | U-1.45 | U-1.45 | U-1.45 | U-0.50 | U-0.50 | U-0.50 | U-0.50 | U-0.50 | U-0.50 | Roll-up or sliding | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75 | R-4.75
[11 empty] | ESRefDesign_InsulationU_V1 | [9 empty] | ESRefDesign_InsulationU_V11 | [9 empty] | ESRefDesign_InsulationU_V12
[11 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1 Insulation Levels modeled to 2009 IECC levels (Commercial, wood frame) and Grade I installation per ANSI / RESNET / ICC Standard | [9 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1.1 Insulation Levels modeled to 2012 IECC levels (Commercial, wood frame) and Grade I installation per ANSI / RESNET / ICC Standard | [9 empty] | ENERGY STAR Multifamily New Construction Reference Design, Version 1.2 Insulation Levels modeled at the levels below and Grade I installation per ANSI / RESNET / ICC Standard
[11 empty] | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | CZ 1 | CZ 2 | CZ 3 | CZ 4 | CZ 4 C | CZ 5 | CZ 6 | CZ 7 | CZ 8 | Climate Zone: | Insulation Level
[11 empty] | Slab Insulation R-Value: | NR | NR | NR | R-10 | R-10 | R-10 | R-15 | R-15 | R-20 | Slab Insulation R-Value: | NR | NR | NR | R-10 | R-10 | R-10 | R-15 | R-15 | R-20 | Above-Grade Wall | R-21
[11 empty] | Slab Insulation Depth (ft): | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | Slab Insulation Depth (ft): | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | Ceiling | R-49
[11 empty] | Basement Wall Continuous Insulation R-Value: | 0 | 0 | 0 | 7.5 | 7.5 | 7.5 | 7.5 | 10 | 12.5 | Basement Wall Continuous Insulation R-Value: | 0 | 0 | 0 | 7.5 | 7.5 | 7.5 | 7.5 | 10 | 12.5 | Floor | R-38
[11 empty] | Floor Assembly U-Factor: | 0.282 | 0.052 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | Floor Assembly U-Factor: | 0.066 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | 0.033 | Basement Wall | R-15 continuous or R-21 cavity
[11 empty] | Wall Assembly U-Factor: | 0.089 | 0.089 | 0.089 | 0.064 | 0.051 | 0.051 | 0.051 | 0.051 | 0.036 | Wall Assembly U-Factor: | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.064 | 0.051 | 0.051 | 0.036 | On-Grade & Below Grade Slab | R-10 at perimeter for entire depth of slab and under entire slab area
[11 empty] | Ceiling Assembly U-Factor: | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | Ceiling Assembly U-Factor: | 0.027 | 0.027 | 0.027 | 0.027 | 0.021 | 0.021 | 0.021 | 0.021 | 0.021
Note on N16: Interpolated from Table A2.2.3.
Note on Y16: Interpolated from Table A2.2.3.
Note on N17: Values interpolated from "Filled Cavity with Spacer Blocks" in Table A2.3.3 which implies a base roof of two insulations plus additional cont. insulation. Perhaps the latter two terms of insulation could be combined into one cont. value.
Note on Y17: Values interpolated from "Filled Cavity with Spacer Blocks" in Table A2.3.3 which implies a base roof of two insulations plus additional cont. insulation. Perhaps the latter two terms of insulation could be combined into one cont. value.
Note on N23: Table A3.1-1, 1 in. metal clips at 24" OC horiz., medium weight.
Note on Y23: Table A3.1-1, 1 in. metal clips at 24" OC horiz., medium weight.
Note on N24: Table A3.2.3, kept original cavity insulation value and added the necessary continuous; other combinations are available.
Note on Y24: Table A3.2.3, kept original cavity insulation value and added the necessary continuous; other combinations are available.
Note on N25: Table A3.3.3.1, 16 OC, 3.5 in depth / R-13 AND 6.0 in depth / R-19
Note on Y25: Table A3.3.3.1, 16 OC, 3.5 in depth / R-13 AND 6.0 in depth / R-19
Note on N36: Table A5.2.3.1, concrete with rigid foam continuous insulation.
Note on Y36: Table A5.2.3.1, concrete with rigid foam continuous insulation.