## Intro
Phius Single Family Quality Assurance Workbook - v4.2 (November 2021)
[10 empty] | AL Alabama | United States
| Project Name |  | Project Permit Date | Phius Project Registration # | Phius Certified Rater Name | Rater Company | CPHC Name | CPHC Company | Yes | AK Alaska | Canada
[9 empty] | No | AS American Samoa | Mexico
| Street Address | City | State/Province | Zip Code | Country | Builder Company Name |  | Builder Responsible Individual |  | AZ Arizona | Afghanistan
| [type address] | [type city] | AZ Arizona | [type Zip Code] | United States |  |  |  | Yes | AR Arkansas | Albania
| Total # Dwelling Units | HVAC Company name |  | HVAC Responsible Individual | Ducted heating/cooling systems in dwelling units (more than 10')? | Builder/HVAC contractor partnerships needed? | EPA ENERGY STAR / DOE ZERH Certification required? | HVAC Contractor must be ESTAR credentialed? | Heating/Cooling Only | CA California | Andorra
[5 empty] | Yes | No | YES | YES | No | CT Connecticut | Angola
| Builder or HVAC contractor are DOE/EPA partners when necessary |  |  |  | Yes | Project Certification Path |  | Phius CORE |  | FM Fed. States of Micronesia | Argentina
Welcome to the Phius Quality Control Workbook for Single Family Projects v4.2! Certification Criteria The Phius Certification process for single family projects includes energy modeling and design consulting performed by a Certified Passive House Consultant (CPHC) to demonstrate compliance with Phius program energy performance metrics, as well as on-site verification of all crtiical project energy features by a Phius Certified Rater. Additionally, all projects must meet the mandatory criteria and be certified under the EPA ENERGY STAR Single-Family New Homes (ESTAR), DOE Zero Energy Ready Homes (ZERH), and EPA Indoor airPLUS (IAP) programs.(1) Projects must be certified under these complimentary programs in order to help ensure that projects seeking Phius Certification are not only energy efficient, but also a durable, comfortable and healthy buildings. For full program requirements, please see the Phius Certification Guidebok.(http://www.phius.org/phius-certification-for-buildings-products/project-certification/documents-for-download) | [9 empty] | FL Florida | Armenia
Using This Workbook The goal of this workbook is to create a single, organized data collection form that shall be used by Phius Certified Raters to document required on-site verification measures that are required for Phius Certification. As such, the workbook incorporates the various program requirements of the Phius certification, including the best practices for building envelope design/installation, HVAC design/instalaltion, domestic hot water distribution, moisture durability management, and indoor air quality. In addition, information regarding testing protocols, exceptions to requirements and links to outside information are included throughout the document using the red "comments" flags that are embedded at the top right of various cells in the workbook. This workbook shall be used only for Phius projects encompassing single family homes and small attached residential developments (duplexes, townhomes, etc). For multifamily apartment/condo projects, the Phius Multifamily Checklist shall be used and verified by a Phius Certified Verifier.(2) | [9 empty] | GU Guam | Australia
There are six worksheets to complete (see the green tabs below). | [9 empty] | HI Hawaii | Azerbaijan
| Responsible parties for completing each workbook are listed here. | [8 empty] | IN Indiana | Bahamas, The
| Building Envelope |  | Phius Certified Rater | [6 empty] | IA Iowa | Bahrain
| Ventilation |  | Phius Certified Rater | [7 empty] | Bangladesh
| Heat, Cool, & DHW |  | Phius Certified Rater | [6 empty] | KY Kentucky | Barbados
| Lights, Appliances, & Renewables |  | Phius Certified Rater | [6 empty] | LA Louisiana | Belgium
| Water Management & IAQ |  | Builder AND/OR Phius Certified Rater | [6 empty] | MH Marshall Islands | Benin
[10 empty] | MA Massachusetts | Bhutan
Data entry cells (for the Rater, builder, HVAC contractor, or designer are in light blue. Calculated cells are in light gray. Do not change the calculation cells! | [9 empty] | MI Michigan | Bolivia
Phius Certified Raters are welcome to add their own custom sheets to this workbook for instance, to track project notes. | [9 empty] | MN Minnesota | Bosnia & Herzegovina
Questions regarding particular checklist items should be directed first to the Phius Certified Rater for the project. For questions on the nuances between certifying an entire building under Phius and certifying individual dwelling units within such buildings under ESTAR/ZERH, please contact the PHIUS at QA@phius.org. For general questions regarding Phius Certification, please contact certification@phius.org . | [9 empty] | MS Mississippi | Botswana
Footnotes (1) Projects located outside of the United States, or in California or Alaska, will not be required to earn ESTAR and ZERH certifications, but must still meet all certification criteria. (2) Refer to the Phius Rater/Verifier Manual for specifc guidance on eligibility of Raters to serve as Verifiers on a project. | [10 empty] | Brunei
[10 empty] | NE Nebraska | Bulgaria
[10 empty] | NV Nevada | Burkina Faso
[10 empty] | NH New Hampshire | Burma
[10 empty] | NJ New Jersey | Burundi
[10 empty] | NM New Mexico | Cambodia
[10 empty] | NY New York | Cameroon
[10 empty] | NC North Carolina | Cape Verde
[10 empty] | ND North Dakota | Cayman Islands
[10 empty] | MP Northern Mariana Is. | Central African Rep.
[10 empty] | OH Ohio | Chad
[10 empty] | OK Oklahoma | Chile
[10 empty] | OR Oregon | China
[10 empty] | PW Palau | Colombia
[10 empty] | PA Pennsylvania | Comoros
[10 empty] | PR Puerto Rico | Congo, Dem. Rep.
[10 empty] | RI Rhode Island | Congo, Repub. of the
[10 empty] | SC South Carolina | Cook Islands
[10 empty] | SD South Dakota | Costa Rica
[10 empty] | TN Tennessee | Cote d'Ivoire
[10 empty] | TX Texas | Croatia
[10 empty] | UT Utah | Cuba
[10 empty] | VT Vermont | Cyprus
[10 empty] | VA Virginia | Czech Republic
[10 empty] | VI Virgin Islands | Denmark
[10 empty] | WA Washington | Djibouti
[10 empty] | WV West Virginia | Dominica
[10 empty] | WI Wisconsin | Dominican Republic
[10 empty] | WY Wyoming | East Timor
[10 empty] | AB Alberta | Ecuador
[10 empty] | BC British Columbia | Egypt
[10 empty] | MB Manitoba | El Salvador
[10 empty] | NB New Brunswick | Equatorial Guinea
[10 empty] | NF Newfoundland | Eritrea
[10 empty] | NT Northwest Territories | Estonia
[10 empty] | NS Nova Scotia | Ethiopia
[10 empty] | ON Ontario | Faroe Islands
[10 empty] | PE Prince Edward Island | Fiji
[10 empty] | QC Quebec | Finland
[10 empty] | SK Saskatchewan | France
[10 empty] | YT Yukon | French Guiana
French Polynesia
Gabon
Gambia, The
Gaza Strip
Georgia
Germany
Ghana
Gibraltar
Greece
Greenland
Grenada
Guadeloupe
Guam
Guatemala
Guernsey
Guinea
Guinea-Bissau
Guyana
Haiti
Honduras
Hong Kong
Hungary
Iceland
India
Indonesia
Iran
Iraq
Ireland
Isle of Man
Israel
Italy
Jamaica
Japan
Jersey
Jordan
Kazakhstan
Kenya
Kiribati
Korea, North
Korea, South
Kuwait
Kyrgyzstan
Laos
Latvia
Lebanon
Lesotho
Liberia
Libya
Liechtenstein
Lithuania
Luxembourg
Macau
Macedonia
Madagascar
Malawi
Malaysia
Maldives
Mali
Malta
Marshall Islands
Martinique
Mauritania
Mauritius
Mayotte
Micronesia, Fed. St.
Moldova
Monaco
Mongolia
Montserrat
Morocco
Mozambique
Namibia
Nauru
Nepal
Netherlands
Netherlands Antilles
New Caledonia
New Zealand
Nicaragua
Niger
Nigeria
N. Mariana Islands
Norway
Oman
Pakistan
Palau
Panama
Papua New Guinea
Paraguay
Peru
Philippines
Poland
Portugal
Puerto Rico
Qatar
Reunion
Romania
Russia
Rwanda
Saint Helena
Saint Kitts & Nevis
Saint Lucia
St Pierre & Miquelon
Saint Vincent and the Grenadines
Samoa
San Marino
Sao Tome & Principe
Saudi Arabia
Senegal
Serbia
Seychelles
Sierra Leone
Singapore
Slovakia
Slovenia
Solomon Islands
Somalia
South Africa
Spain
Sri Lanka
Sudan
Suriname
Swaziland
Sweden
Switzerland
Syria
Taiwan
Tajikistan
Tanzania
Thailand
Togo
Tonga
Trinidad & Tobago
Tunisia
Turkey
Turkmenistan
Turks & Caicos Is
Tuvalu
Uganda
Ukraine
United Arab Emirates
United Kingdom
Uzbekistan
Vanuatu
Venezuela
Vietnam
Virgin Islands
Wallis and Futuna
West Bank
Western Sahara
Yemen
Zambia
Zimbabwe
Note on J9: AUTO CALCULATED

## Building Envelope
Building Envelope Phius On-site Quality Control
The Rater is responsible for verifying all items on this worksheet. Any additional content needed for clarification of building and its construction shall be added to the spreadsheet.
1 | Site Photos and Verification | Rater Verified | N/A | PROG REQ.
1.1 | Take as many exterior photos as needed to appropriately depict all building elevations and significant architectural features of building |  |  | ALL
1.2 | Take pictures of surrounding site on all sides of building, including significant shading elements |  |  | ALL
1.3 | Take representative pictures of all unique insulated assemblies and window/door installations |  |  | ALL
1.4 | Perform thorough IR scan of entire building from interior and exterior and document representative photos |  |  | Phius
1.5 | If installed, describe operable shading. Include photo/s in documentation folder |  |  | ALL
Rater Notes on site, photos, etc.:
2 | Verification of Architectural Features | Rater Verified | N/A | PROG REQ.
2.1 | Drawings Check - describe any significant variations in construction from the construction drawings and specifications (insulation, window sizes, window performance, fixed shading etc.) |  |  | ALL
Rater Notes:
2.2 | Insulation R-Value: All insulation R-values match those listed on architectural plans. If not, please describe in notes section below. |  |  | ALL
Rater Notes:
2.3 | Framing Inspection: Framing matches architectural plans. If not, please describe in notes section below. |  |  | ALL
Rater Notes:
3 | Mandatory Envelope Criteria Check | Rater Verified | N/A | PROG REQ.
3.1a | Air Barrier Integrity: Air barrier is contiguous, including behind stairs, porch roofs, fireplaces, showers/tubs, attic knee walls, walls/ceilings adjacent to vented attics, and floors over unconditioned basements and vented crawlspaces. |  |  | ENERGY STAR
Rater Notes:
3.1b | Air Sealing: All penetrations (wire/pipe/HVAC/etc.) between conditioned and unconditioned space sealed, service chases capped at exterior, exterior/doors to garages weather-stripped, rough opening of doors/windows sealed, multifamily drywall shaft walls sealed at exterior, recessed lights ICAT and gasketed, etc. |  |  | ENERGY STAR
Rater Notes:
3.2 | Insulation Quality Check: All insulated assemblies have achieved a RESNET Grade I cavity insulation level, or alternatively GII with continuous insulation. |  |  | ENERGY STAR
Rater Notes:
3.3 | Window Performance: Windows are ENERGY STAR certified, and/or triple-glazed with thermally broken frames/spacers, and meets project the design specs |  |  | DOE ZERH
Rater Notes:
3.4 | Vented Attic Reduced Thermal Bridging: Vent baffles installed in bays with soffit vents to prevent wind-washing; Insulation extends over top plates and under attic walkways/platforms ≥ R-21in CZ 1-5; ≥ R-30in CZ 6-8 |  |  | ENERGY STAR
Rater Notes (identify percentage of attic with reduced R-value due to walkways/platforms, or other restriction of full-depth R-value):
3.5 | Slab Edge Insulation: For slabs on-grade in CZ 4-8, 100% of slab edge insulated to ≥ R-5 at the depth specified by the 2009 IECC |  |  | ENERGY STAR
3.6 | Above-Grade Wall Reduced Thermal Bridging: AGWs achieve at least one of the strategies for Reduced Thermal Bridging listed in Section 3.4 of the ENERGY STAR Rater Field Checklist (Rev 09) |  |  | ENERGY STAR
Rater Notes (identify the strategy achieved):
3.7 | Other Thermal Bridging/mitigation strategy identification: Note any other meaningful thermal bridges observed on the project, as well as thermal bridging mitigation strategy identification. Special effort should be made to clearly document such bridging and mitigation strategies, or where such details are missed. |  |  | Phius
Rater Notes (thermal bridges present and/or mitigation strategies)
4 | Building Air Tightness Testing
4 | Blower Door Test Threshold Calculator
| A preliminary blower door test is | OPTIONAL |  | 1
Building Envelope Area (ft2)
Project Net Volume (ft3)
Project Threshold
(CFM50)
| CFM50/Building Envelope Area (CFM50/ft2) | 0.06
4.1 | Preliminary whole building blower door test in accordance with ANSI/RESNET/ICC 380-2019
Depressurization Test Result (Preliminary)
(CFM50)
CFM50/Building Envelope Area (CFM50/ft2)
(ACH50)
Pressurization Test Result (Preliminary)
(CFM50)
CFM50/Building Envelope Area (CFM50/ft2)
(ACH50 )
Average Test Result (Preliminary)
(CFM50)
CFM50/Building Envelope Area (CFM50/ft2)
(ACH50 )
4.2 | Final whole building blower door test in accordance with ANSI/RESNET/ICC 380-2019
Depressurization Test Result
(CFM50)
CFM50/Building Envelope Area (CFM50/ft2)
(ACH50)
Pressurization Test Result
(CFM50)
CFM50/Building Envelope Area (CFM50/ft2)
(ACH50 )
Average Test Result
(CFM50)
CFM50/Building Envelope Area (CFM50/ft2)
(ACH50 )
| Project Meets Requirement? |  |  | Phius
Note on D7: These photos are used to help verify the site shading reduction factors used by the CPHC
Note on D9: Follow RESNET Infrared inspection guidelines for minimum delta-T. Images should include walls, insulated ceilings, slabs, windows. Use picture in picture if camera has the capability. Enter "n/a" if conditions do not allow the minimum delta-T
Note on D22: See ENERGY STAR Rater Field Checklist Section 2 for further details and criteria.
Note on D24: See ENERGY STAR Rater Field Checklist Section 4 for further details and criteria.
Note on D26: See ENERGY STAR Rater Field Checklist Section 1 for further details and criteria. Please see ANSI/RESNET/ICC Standard 301-2019 for information on insulation Grading.
Note on D28: Per DOE ZERH footnote 13: Fenestration shall meet the applicable ENERGY STAR Windows Eligibility Criteria for U and SHGC, with the following exceptions: a. An area-weighted average of fenestration products shall be permitted to satisfy the U-factor requirements; b. An area-weighted average of fenestration products ≥ 50% glazed shall be permitted to satisfy the SHGC requirements; c. 15 square feet of glazed fenestration per dwelling unit shall be exempt from the U-factor and SHGC requirements, and shall be excluded from area-weighted averages calculated using a) and b), above; d. One side-hinged opaque door assembly up to 24 square feet in area shall be exempt from the U-factor requirements and shall be excluded from area-weighted averages calculated using a) and b), above; e. Fenestration utilized as part of a passive solar design shall be exempt from the U-factor and SHGC requirements, and shall be excluded from area-weighted averages calculated using a) and b), above. Exempt windows shall be facing within 45 degrees of true South and directly coupled to thermal storage mass that has a heat capacity > 20 btu / ft3x◦F and provided in a ratio of at least 3 sq. ft. per sq. ft. of South facing fenestration. Generally, thermal mass materials will be at least 2 in. thick.
Note on D32: Per ENERGY STAR Rev 11 Rater Checklist footnotes 15 & 16: 15. Consistent with the 2009 IECC, slab edge insulation is only required for slab-on-grade floors with a floor surface less than 12 inches below grade. Slab insulation shall extend to the top of the slab to provide a complete thermal break. If the top edge of the insulation is installed between the exterior wall and the edge of the interior slab, it shall be permitted to be cut at a 45-degree angle away from the exterior wall. Alternatively, the thermal break is permitted to be created using ≥ R-3 rigid insulation on top of an existing slab (e.g., in a home undergoing a gut rehabilitation). In such cases, up to 10% of the slab surface is permitted to not be insulated (e.g., for sleepers, for sill plates). Insulation installed on top of slab shall be covered by a durable floor surface (e.g., hardwood, tile, carpet). 16. Where an insulated wall separates a garage, patio, porch, or other unconditioned space from the conditioned space of the house, slab insulation shall also be installed at this interface to provide a thermal break between the conditioned and unconditioned slab. Where specific details cannot meet this requirement, partners shall provide the detail to EPA to request an exemption prior to the home’s certification. EPA will compile exempted details and work with industry to develop feasible details for use in future revisions to the program. A list of currently exempted details is available at: energystar.gov/slabedge.
Note on D33: Most Phius Projects will easily meet this requirement. Where any doubt or question exists about the strategy to meet this requirement, see the ENERGY STAR Rater Field Checklist (Rev 11) footnotes relating to section 3.4
Note on D35: Phius Certified Rater shall discuss the presence of known thermal bridges with CPHC prior to inspection, as well as specific mitigation strategies. Any significant bridging observed on a project not accounted for by the CPHC must be brought to the attention of Phius immediately.
Note on D40: MANDATORY for Prescriptive Path projects. OPTIONAL (but recommended) for Performance Path projects.
Note on D59: Automated multi-point testing using RESNET testing protocol, set up building according to RESNET standard. See Phius Certification Guidebook. Include testing report/s in documentation folder

## Ventilation
Ventilation Phius On-site Quality Control
The Rater is responsible for verifying all items on this worksheet. Ventilation air volume measurements may be verified by a third-party air balancing contractor (i.e., not the installing contractor but a separate third-party commissioning agent) so long as the Rater verifies a minimum of 10% of all measurements.
1 | Ventilation System Installation | [9 empty] | Rater Verified | N/A | PROG. REQ.
1.1 | System Type |  | Individual system or shared (attached housing only)? |  |  | Manufacturer |  | Model # |  |  |  |  | Phius
1.2 | Take photo/s of equipment for documentation folder | [11 empty] | Phius |  |  |  | HRV | Individual
1.3a | All ventilation air inlets located at least 10' ("stretched-string distance") from known contamination sources not exiting the roof, and ≥ 3 ft. distance from dryer exhausts and sources exiting the roof. | [11 empty] | ENERGY STAR |  |  |  | ERV | Shared
1.3b | All ventilation air inlets located minimum 5' from ventilation exhaust outlet, recommended 10' | [11 empty] | Phius
1.4 | Ventilation air inlets are at least 2' above grade and/or roof deck, and are not obstructed by snow, plantings, outdoor equipment, etc. at the time of inspection | [11 empty] | ENERGY STAR |  |  |  | Exhaust Only
1.5 | Ventilation air comes directly from outdoors, not from adjacent dwelling units, common spaces, garages, crawlspaces or attics | [11 empty] | ENERGY STAR |  |  |  | Supply Only
1.6 | Outside air passes through a minimum MERV 8 filter prior to distribution, is changed at final and home is ventilated prior to occupancy | [11 empty] | EPA IAP |  |  |  | Air Cycler
1.7 | Outside air filter is located to facilitate regular service by the occupant and/or building superintendent | [11 empty] | ENERGY STAR
1.8 | Air-sealed, class 1 vapor retarder shall be installed over all air-permeable insulation (such as fiberglass duct wrap) on ventilation ducts connected to outside | [7 empty] | Enter R-Value |  |  |  | Phius
1.9 | Bedrooms are pressure balanced to achieve a Rater-measured pressure difference of no more than 1Pa with respect to the main body of the house/apartment when all bedroom doors are closed and just the ventilation system is operating at 24/7 design speed | [11 empty] | Phius
1.1 | Dedicated Fresh Air supply to all bedrooms | [11 empty] | Phius
1.11 | Rater-measured bathroom exhaust rates meets one of the following: >=20cfm continuous or 50 cfm intermittent | [11 empty] | ENERGY STAR
1.12 | Direct exhaust bath fans ENERGY STAR rated; <= 1 sone | [11 empty] | ENERGY STAR
1.13 | Rater-measured kitchen exhaust rates meets one of the following: >=25cfm continuous, 100cfm intermittent for range hoods, or 5ACH based on kitchen volume | [11 empty] | ENERGY STAR
1.14 | If kitchen exhaust connected to ERV/HRV, register is min. 6' from cooktop, MERV 3 or washable mesh filter for trapping grease, and recirc hood over range | [11 empty] | Phius
1.15 | Clothes dryer is a condensing/heat pump dryer, or exhaust dryer with exhaust ducted to the outside | [11 empty] | EPA IAP
2 | Ventilation system airflow testing | [5 empty] | Design (cfm) | Test (cfm) | % +/- Design | +/- cfm Design | OK? | Room pressure difference | OK?
Maximum Rate Test Values
2.1 | Total supply airflow at unit (HRV/ERV) at maximum speed setting
2.2 | Total exhaust airflow at unit (HRV/ERV) at maximum speed setting
2.3 | Ventilation system at max has capacity to exchange 0.30 ACH |  |  | Net volume | ACH
Typical / 24/7 Design Rate Test Values
2.4 | enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
| enter supply branch name here | [12 empty] | 0 | 5 | 5
Sum of supply branches (for reference only)
2.5 | Total supply airflow at unit (HRV/ERV) for typical operation
2.6 | enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
| enter exhaust branch name here | [12 empty] | 0 | 5 | 5
Sum of exhaust branches (for reference only)
2.7 | Total exhaust airflow at unit (HRV/ERV) for typical operation
2.8 | Total supply and exhaust are within 10% of each other?
2.9 | Net pressure across envelope no greater than +/-5 Pascals? |  |  | Net pressure
2.1 | Measure power input (Watts) at typical 24/7 airflow setting
2.11 | Watt/cfm for final input into consultant's energy model
3 | Ventilation - Auxiliary Systems | [9 empty] | Rater Verified | N/A | PROG. REQ.
3.1 | If installed, enter type of ERV/HRV defrost - electric, hot water loop from DHW tank, ground loop | [11 empty] | Phius
3.2 | Project team has demonstrated the defrost control logic is set up properly | [11 empty] | Phius
3.3 | Is there a ground loop ("brine loop") or earth tube installed? | [11 empty] | Phius
| A | Enter loop length and approximate depth | [10 empty] | Phius
| B | Measure loop pump power | [10 empty] | Phius
| C | Project team has demonstrated the ground loop / earth tube control logic is set up properly | [10 empty] | Phius
Note on D9: Examples of contamination sources include: plumbing vents, bath/kitchen exhaust vents, combustion exhaust, vehicle exhaust. Exception: ventilation air inlets in the wall at least 3 ft. from clothes dryer exhaust or contamination sources exiting through the roof. Please note that ERV/HRV exhaust is not necessarily a "contaminant". Thus it is not subject to this provision. However, exhaust/intake separation shall meet manufacturer specifications.
Note on D11: Care should be taken by projects to position fresh air inlets additional appropriate distance above grade or roof deck where snow loads or plantings may be a greater concern
Note on D17: ​e.g., supply to living room only, in a one-bedroom apt, is not acceptable.
Note on D24: Where ventilation system has independent ductwork for supply and/or exhaust, branch airflow testing is to be performed by Phius Certified Rater or Phius Certified Verifier. Ventilation air volume measurements may be verified by a third-party air balancing contractor (i.e., not the installing contractor but a separate third-party commissioning agent) so long as the Rater verifies a minimum of 10% of all measurements.
Note on AC24: Must be +/- 20% of design value or 5cfm, whichever is greater
Note on AE24: Must be no more than 1Pa pressure difference
Note on D30: Enter additional rows as needed
Note on D39: The 'mode' should be the same as was used to measure individual supply branches in Section 2.5 above. Must be within +/- 10% of design
Note on D40: Enter additional rows as needed
Note on D49: The 'mode' should be the same as was used to measure individual exhaust branches in Section 2.7 above. Must be within +/- 10% of design
Note on D50: If ventilation supply/exhaust not within 10%, Rater shall verify net pressurization /depressurization across envelope to verify less than +/- 5 Pa while ventilation running. Phius reserves right to degrade performance of unbalanced ventilation systems
Note on D51: Measured by pressure probe across envelope, baseline adjusted value while all ventilation equipment turned on, including whole-house mechanical ventilation, local exhaust systems or supply only ventilation systems.
Note on D52: Must be based either off of field measured Power Factor adjusted wattage measurement, or through another scientific method of deriving wattage, such as comparing an External Static Pressure measurement to a manufacturer fan curbe table. Recommended devises are the Kill-A-Watt plug-in meter for 120V plug-in systems, or the Amprobe NAV-51 clamp meter. If Rater unable to measure, must be measured and documented by licensed electrician or mechanical contractor.
Note on D57: This is to ensure the defrost system does not operate unnecessarily. This should be a simple check. If the ERV/HRV calls for defrost below 25F, then the project team should be able to show the Rater that the system is set up correctly.

## Heat, Cool & DHW
Heating, Cooling & DHW Phius On-site Quality Control
Complete form for each piece of heating/cooling equipment with air distribution. For example, if a house has more than one ducted heating/cooling system, complete one form for each apartment. Copy and past additional forms/sheets into this workbook as needed.
1 | Heating/Cooling Equipment | [16 empty] | Rater Verified | N/A | PROG. REQ.
1.1 | Describe primary system type (split heat pump, water source heat pump, fan coil, furnace, hydronic, etc.) | [18 empty] | Phius
1.2 | System description (i.e., ducted vs ductless, individual vs shared system) | [18 empty] | Phius
1.3 | Manufacturer |  | Company name |  |  |  | Model # | [12 empty] | Phius
1.4 | AHRI certificate and/or manufacturer's detailed specs for heating/cooling equipment are included in documentation folder | [18 empty] | Phius
1.5 | Describe any supplemental heating/cooling systems installed | [18 empty] | Phius
1.6 | Photos of equipment (including model numbers) are included in documentation folder | [18 empty] | Phius
1.7 | If a combustion equipment for space heating, the building has provided a designated exterior location(s) in accordance with the following | [18 empty] | Phius
| A | Natural drainage for condensate from cooling equipment operation or a condensate drain located within 3 feet | [17 empty] | Phius
| B | A dedicated branch circuit in compliance with IRC Section E3702.11 based on heat pump space heating equipment sized in accordance with R403.7 and terminating within 3 feet of the location with no obstructions. Both ends of the branch circuit shall be labeled “For Future Heat Pump Space Heater.” | [17 empty] | Phius
2 | Heating/Cooling Distribution - Ducted Systems Only | [16 empty] | Rater Verified | N/A | PROG. REQ.
2.1 | Rater has collected ENERGY STAR HVAC Design Checklist, and has completed appropriate review items on Rater Design Review Checklist | [18 empty] | Phius
2.2 | Duct layout drawing, total system design airflow and branch design airflows are included in documentation folder | [18 empty] | Phius
2.3 | Rater review of duct installation:
| A | Duct installation reasonably matches design layout | [17 empty] | Phius
| B | Building cavities not used as supply or return ducts | [17 empty] | EPA IAP
| C | Duct systems protected from construction debris during mid- construction | [17 empty] | EPA IAP
| D | Temporary filter installed to protect unit from construction dust during mid-construction | [17 empty] | EPA IAP
| E | HVAC system and ducts clean at final | [17 empty] | EPA IAP
2.4 | All return air passes through a min. MERV 8 filter which is located to facilitate regular service by the occupant and/or building superintendent | [18 empty] | EPA IAP
2.5 | Filter access panel includes a gasket or comparable sealing mechanism, and new filter installed at final before occupancy | [18 empty] | ENERGY STAR
2.6 | Equipment selected to keep relative humidity < 60% in “Warm-Humid” climates OR install additional dehumidification | [18 empty] | EPA IAP
2.7 | Bedrooms are pressure balanced to achieve a Rater-measured pressure difference of no more than 3Pa with respect to the main body of the house when all bedroom doors are closed, all heating/cooling air handlers are operating at full speed and ventilation system is operating at design speed | [18 empty] | ENERGY STAR
2.8 | Ducts and air handlers located entirely within building thermal envelope | [18 empty] | DOE ZERH
2.9 | Duct leakage to outside |  |  | ## | CFM25 | % per Floor Area |  | Total Duct Leakage |  |  | ## | CFM25 | % per Floor Area | [6 empty] | ENERGY STAR
2.1 | Total External Static Pressure: |  |  | Return test location |  |  |  | Return test result | [11 empty] | ENERGY STAR
|  |  |  | Supply test location |  |  |  | Supply test result | [11 empty] | ENERGY STAR
2.11 | Total system and branch airflow testing - to be performed by Phius Certified Rater. Rater-conducted balancing is optional. | [7 empty] | Design (cfm) | Test (cfm) |  | % +/- Design |  | cfm +/- Design |  | OK? | Room pressure difference |  | OK? | PROG. REQ.
|  | Total System Airflow | [13 empty] | NO
|  | enter supply branch name here | [6 empty] | 50 | 60 |  | 20% |  | 10 |  | YES |  |  | YES | ENERGY STAR | 10 | 25 | 25 | -25
|  | enter supply branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter supply branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter supply branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter supply branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter supply branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter supply branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter exhaust branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter exhaust branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter exhaust branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter exhaust branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter exhaust branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter exhaust branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
|  | enter exhaust branch name here | [11 empty] | 0 |  | YES |  |  | YES | ENERGY STAR | 0 | 25 | 25 | -25
3 | Refrigerant Testing, Controls + Electrical Measurements | [16 empty] | Rater Verified | N/A | PROG. REQ.
3.1 | Rater has collected ENERGY STAR HVAC Contractor Commissioning Checklist | [18 empty] | ENERGY STAR
3.2 | Fan - air flow is produced when thermostat is set to "fan on", Heated air flow is produced when thermostat is set to "heat", Cooling air flow is produced when thermostat is set to "cool" | [18 empty] | Phius
3.3 | Ground-source heat pump (where installed) pump: Manufacturer | [9 empty] | Model # |  |  |  | Watts |  |  |  |  | Phius
4 | Combustion Safety and Condensation Management | [16 empty] | Rater Verified | N/A | PROG. REQ.
4.1 | Combustion heating/water heating systems located within the buildings' pressure boundary are sealed combustion, direct-vent appliances | [18 empty] | ENERGY STAR
4.2 | Natural draft fireplaces are not installed | [18 empty] | ENERGY STAR
4.3 | Installed fireplaces and woodstoves have a combustion air inlet connected to the firebox | [18 empty] | ENERGY STAR
4.4 | No unvented combustion fireplaces installed in home | [18 empty] | ENERGY STAR
4.5 | Corrosion-resistant drain pan, properly sloped to drainage system is included with each HVAC component that produces condensate | [18 empty] | Phius
5 | Heating/Cooling Distribution - Hydronics | [16 empty] | Rater Verified | N/A | PROG. REQ.
5.1 | Pipe layout drawing + schedule showing pipe sizes and insulation is included in documentation folder | [18 empty] | Phius
5.2 | Rater review of pipe + pump installation:
| A | Pipe installation reasonably matches design layout | [17 empty] | Phius
| B | Pipe insulation matches design specs | [17 empty] | Phius
| C | Pump/s Manufacturer + Model # | [17 empty] | Phius
| D | Is pump single speed or variable? | [17 empty] | Phius
| E | Design hydronic loop flow rate (GPM) | [17 empty] | Phius
| F | Measured hydronic loop flow rate (GPM) | [17 empty] | Phius
| G | Measure pump power input | [17 empty] | Phius
6 | Domestic Hot Water Systems | [16 empty] | Rater Verified | N/A | PROG. REQ.
6.1 | Describe hot water system type (i.e., gas tankless, heat pump, etc.) | [18 empty] | Phius
6.2 | Photo and/or AHRI certificate included of water heater | [18 empty] | Phius
6.3 | Manufacturer | [5 empty] | Model # | [12 empty] | Phius
6.4 | Continuous, time, or temperature-based hot water recirculation systems not installed | [18 empty] | DOE ZERH
6.5 | Hot water temperature-rise test: |  |  |  | Highest volume hot water fixture location | [5 empty] | Gallons emitted prior to 10 sec. temp rise? | [8 empty] | DOE ZERH
6.6 | Pipe layout drawing + schedule showing pipe sizes and insulation is included in documentation folder | [18 empty] | Phius
6.7 | Pipe installation and insulation reasonably matches design layout
6.8 | If combustion water heating and water heater capacity is less than or equal to 300,000 Btu/h (88 kW) the following are met:
| A | A dedicated 240-volt branch circuit with a minimum capacity of 30 amps shall terminate within 3 feet from the water heater and be accessible to the water heater with no obstructions. Both ends of the branch circuit shall be labeled with the words "For Future Heat Pump Water Heater" and be electrically isolated.
| B | A condensate drain is installed within 3 feet of the water heater. It is no more than 2 inches higher than the base of the installed water heater and allows natural draining without pump assistance.
| C | The water heater is installed in a space with minimum dimensions of 3 feet x 3 feetx 7 feet high.
| D | The water heater is installed in a space with a minimum volume of 700 cubic feet or the equivalent of one 16-inch x 24-inch grill to a heated space and one 8-inch duct of no more than 10 feet in length for cool exhaust air. | [17 empty] | Phius
Note on D13: Exception: Where an electrical circuit in compliance with IRC Section E3702.11 exists for space cooling equipment.
Note on D28: Exception: Climate Zones 4-8 3B, 3C and the portions of 3A and 2B above the white line as shown by 2009 IECC Figure 301
Note on D30: Per DOE ZERH, Exceptions and alternative compliance paths to locating 100% of forced-air ducts in home’s thermal and air barrier boundary are a. Up to 10’ of total duct length is permitted to be outside of the home’s thermal and air barrier boundary. b. Ducts are located in an unvented attic, regardless of whether this space is conditioned with a supply register c. Ducts are located in a vented attic with all of the following characteristics: i. In Moist climates (Zones1A, 2A, 3A, 4A, 5A, 6A and 7A per 2012 IECC Figure R301.1) and Marine climates (all “C” Zones per 2012 IECC Figure R301.1), minimum R-8 duct insulation with an additional minimum 1.5” of closed-cell spray foam insulation encapsulating the ducts; duct leakage to outdoors ≤ 3 CFM25 per 100 ft2 of conditioned floor area (in addition to meeting total duct leakage requirements from ENERGY STAR requirements) and ductwork buried under at least 2” of blown-in insulation. ii. In Dry climates (all “B” Zones per 2012 IECC Figure R301.1), minimum R-8 duct insulation; duct leakage to outdoors ≤ 3 CFM25 per 100 ft2 of conditioned floor area (in addition to meeting total duct leakage requirements from ENERGY STAR requirements) and ductwork buried under at least 3.5” of blown-in insulation. Note that in either of these designs the HVAC equipment must still be located within the home’s thermal and air barrier boundary. d. Jump ducts which do not directly deliver conditioned air from the HVAC unit may be located in attics if all joints, including boot-to-drywall, are fully air sealed with mastic or foam, and the jump duct is fully buried under the attic insulation. e. Ducts are located in a basement or unvented crawlspace which is within the home’s thermal boundary f. Ductless HVAC system is used
Note on AE34: TOTAL SYSTEM AIRFLOW: +/- 15% of design value BRANCHES: +/- 20% or 25cfm of the design value, whichever is greater
Note on AG34: For rooms with doors and supply airflow
Note on AI34: Must be no more than 3Pa pressure difference
Note on E35: Using pressure matching w/ duct tester, airflow grid, total external static pressure and manufacturer fan curve, or other equivalent scientific method
Note on E36: insert additional rows as needed
Note on D53: Unlike for EPA ENERGY STAR Single-Family New Homes Rev 11 requirements, Phius requires this to be collected by the Rater
Note on E72: Either Rater measured or measurement / balancing report provided by licensed professional
Note on E73: Must be based either off of field measured Power Factor adjusted wattage measurement, or through another scientific method of deriving wattage, such as comparing an External Static Pressure measurement to a manufacturer fan curve table. Recommended devises are the Kill-A-Watt plug-in meter for 120V plug-in systems, or the Amprobe NAV-51 clamp meter. If Rater unable to measure, must be measured and documented by licensed electrician or mechanical contractor.

## Lights, Appliances & Renewables
Lighting, Appliances and Renewables Phius On-site Quality Control
1 | Lighting | [9 empty] | Rater Verified | N/A | PROG. REQ.
1.1 | 80% of lighting fixtures are ENERGY STAR qualified or ENERGY STAR lamps (bulbs) in minimum 80% of sockets | [11 empty] | DOE ZERH
2 | Appliances | [9 empty] | Rater Verified | N/A | PROG. REQ.
2.1 | Refrigerator Manufacturer |  |  |  |  | Model # |  | ENERGY STAR? |  | kwh/yr |  |  | DOE ZERH
2.2 | Dishwasher Manufacturer |  |  |  |  | Model # |  | ENERGY STAR? |  | kwh/yr |  |  | DOE ZERH
2.3 | Clothes washer Manufacturer |  |  |  |  | Model # |  | ENERGY STAR? |  | kwh/yr |  |  | DOE ZERH
2.4 | A | Clothes dryer Manufacturer |  |  |  | Model # |  | Vented, heat pump or condensing? |  |  |  |  | DOE ZERH
| B | Clothes dryers vented to the outdoors or plumbed to a drain according to manufacturer's instructions
| C | If combustion clothes drying. A dedicated 240-volt branch circuit with a minimum capacity of 30 amps shall terminate within 6 feet of natural gas clothes dryers and shall be accessible with no obstructions. Both ends of the branch circuit shall be labeled with the words “For Future Electric Clothes Drying” and be electrically isolated. | [10 empty] | EPA IAP
2.5 | A | Range/Oven Manufacturer |  |  |  | Model # |  | Electric resistance, induction or fossil fuel? |  |  |  |  | DOE ZERH
| B | If combustion cooking. A dedicated 240-Volt, 40A branch circuit shall terminate within 6 feet of natural gas ranges, cooktops and ovens and be accessible with no obstructions. Both ends of the branch circuit shall be labeled with the words “For Future Electric Range'' and be electrically isolated.
2.6 | Ceiling fan Manufacturer |  |  |  |  | Model # |  | ENERGY STAR? |  | CFM/watt (med) |  |  | DOE ZERH
2.7 | Other Combustion Equipment |  |  | All combustion equipment shall be provided with a branch circuit sized for an electric appliance, equipment or end use with an equivalent capacity that terminates within 6 feet of the appliance or equipment. | [8 empty] | DOE ZERH
3 | Additional Major Electrical/Other Loads | [9 empty] | Rater Verified | N/A | PROG. REQ.
3.1 | Describe any other additional significant energy uses loads on the property, including items like pools, hot tubs, home automation systems, fire pits, etc. | [11 empty] | Phius
4 | Renewable Energy Systems | [9 empty] | Rater Verified | N/A | PROG. REQ.
4.1 | Solar thermal system installed? |  |  |  | Area |  | Orientation | Tilt | System type |  |  |  | N/A
4.2 | Solar photovoltaic system installed? |  |  |  | Area |  | Orientation | Tilt | Peak production (W) |  |  |  | N/A
4.3 | If solar photovoltaic (PV) system not installed, document home's compliance with the DOE ZERH Home PV-ready checklist
| A | Site does not have significant adjacent shading of south side of roof. Describe and take photos if so | [10 empty] | DOE ZERH
| B | Home has adequate roof area within +/-45° of true south based on table below | [10 empty] | DOE ZERH
|  |  | CFA | Min roof area within +/-45° of true south
|  |  | <= 2000 | 110 sqft
|  |  | <= 4000 | 220 sift
|  |  | <= 6000 | 330 sqft
|  |  | >6000 | 440 sqft
4.4 | If either of the above is false, the home is not required to meet the following requirements
| A | Provide code-compliant documentation of the maximum allowable dead load and live load ratings of the existing roof; recommended: allowable dead load rating can support an additional 6 lbs/sq. ft. for future solar system. | [10 empty] | DOE ZERH
| B | Provide architectural drawing of solar PV system components | [10 empty] | DOE ZERH
| C | Install a 1” metal conduit for the DC wire run from the designated array location to the designated inverter location (cap and label both ends) | [10 empty] | DOE ZERH
| D | Install a 1” metal conduit from designated inverter location to electrical service panel (cap and label both ends) | [10 empty] | DOE ZERH
| E | Install and label a 4’ x 4’ plywood panel (or alternatively blocking) area for mounting an inverter and balance of system components. | [10 empty] | DOE ZERH
| F | Install a 70-amp dual pole circuit breaker in the electrical service panel for use by the PV system (label the service panel) | [10 empty] | DOE ZERH
5 | Electric Vehicle Charging Infrastructure | [9 empty] | Rater Verified | N/A | PROG. REQ.
5.1 | One EV-Ready space shall be provided for each dwelling unit where parking is required, or if there are attached or detached garages, on-site parking spaces and new detached garages. | [11 empty] | Phius
5.2 | The branch circuit has wiring capable of supporting a 40-amp, 208/240-volt circuit | [11 empty] | Phius
5.3 | The branch circuit terminates at a junction box or receptacle located within 3 feet of the parking space | [11 empty] | Phius
5.4 | The electrical panel directory has designated the branch circuit as “For electric vehicle charging” and the junction box or receptacle shall be labeled “For electric vehicle charging”. | [11 empty] | Phius
#REF!
4
#REF!
Note on AA9: Use values in HERS Model- Typically from EPA database or Energy Guide tag
Note on AA10: Use values in HERS Model- Typically from EPA database or Energy Guide tag
Note on AA11: Use values in HERS Model- Typically from EPA database or Energy Guide tag
Note on J28: The following inputs are not needed if a HERS model documents the installed system.
Note on J29: The following inputs are not needed if a HERS model or solar installer PV Watts or equivalent report documents the installed system.
Note on D30: Please note Phius has moved to requiring homes to be solar PV-ready regardless of average daily solar radiation kWh/m2/day
Note on D38: Please note Phius has moved to requiring homes to be solar PV-ready regardless of average daily solar radiation kWh/m2/day
Note on E40: Alternative: Provide home buyer with the following information:  List of renewable-ready features Available free roof area within +/- 45° of true south Location of panel or blocking for future mounting of PV system components Location of Breaker or slot for future breaker in electrical service panel  Copy of the PV-Ready Checklist A copy of the RERH Solar PV Specification Guide
Note on E48: ====== ID#AAAAQ2DLLwk Chris McTaggart (2021-11-10 22:35:34) Alternative: Provide home buyer with the following information:  List of renewable-ready features Available free roof area within +/- 45° of true south Location of panel or blocking for future mounting of PV system components Location of Breaker or slot for future breaker in electrical service panel  Copy of the PV-Ready Checklist A copy of the RERH Solar PV Specification Guide

## Water Management & IAQ
Water Management and Indoor Air Quality
1 | Water/Moisture Managed Site/Foundation | Rater Verified | Builder Verified | N/A | PROG. REQ.
1.1 | Impermeable surfaces (patio/porch slabs/sidewalks/ramps/driveways) sloped ≥ 0.25"/ft from home to edge of surface or 10 ft Back-fill has been tamped, and permeable surfaces sloped ≥ 0.5"/ft from home for 10 ft |  |  |  | ENERGY STAR
1.2 | Layer of aggregate or sand (4 in.) with geotextile matting & capillary break beneath all slabs using either: ≥ 6 mil polyethylene sheeting, lapped 6-12 in., or ≥ 1 in. extruded polystyrene insulation with taped joints |  |  |  | EPA IAP
1.3 | Basements/crawlspaces insulated, sealed, dampproofed and conditioned |  |  |  | EPA IAP
1.4 | Class 1 vapor retarder not installed on interior side of air permeable insulation in exterior below-grade walls |  |  |  | ENERGY STAR
1.5 | Drain or sump pump installed in basements and crawlspaces ; sump pump covers mechanically attached with full gasket seal or equivalent. |  |  |  | EPA IAP
1.6 | Drain tile installed at basement/crawlspace walls, with the top of the drain tile pipe below the bottom of the concrete slab or crawlspace floor |  |  |  | ENERGY STAR
2 | Water Managed Walls/Roofs | Rater Verified | Rater Verified | N/A | PROG. REQ.
2.1 | Flashing at bottom of exterior walls with weep holes included for masonry veneer and weep screed for stucco cladding systems |  |  |  | Phius
2.2 | Fully sealed continuous drainage plane behind exterior cladding that laps over flashing in Item 2.1 and fully sealed at all penetrations. Additional bond-break drainage plane layer provided behind all stucco and non-structural masonry cladding wall assemblies. |  |  |  | ENERGY STAR
2.3 | Window and door openings fully flashed |  |  |  | Phius
2.4 | Step and kick-out flashing at all roof-wall intersections, extending ≥ 4” on wall surface above roof deck and integrated shingle-style with drainage plane above; boot / collar flashing at all roof penetrations |  |  |  | Phius
2.5 | Non-slab on-grade homes shall have gutters/downspouts with discharge on sloping final grade ≥ 5 ft. from foundation. See footnotes and additional details from ENERGY STAR and IAP for other circumstances |  |  |  | EPA IAP
2.6 | Self-adhering polymer-modified bituminous membrane at all valleys & roof deck penetrations AND in CZ 5+, over sheathing at eaves from the edge of the roof line to > 2 ft. up roof deck from the interior plane of the exterior wall |  |  |  | ENERGY STAR
2.7 | Piping in exterior walls insulated with pipe wrap. |  |  |  | EPA IAP
3 | Water Managed and Low-Emitting Building Materials | Rater Verified | Rater Verified | N/A | PROG. REQ.
3.1 | Hard-surface flooring in kitchens, baths, entry, laundry and utility rooms AND carpet not installed within 2.5 ft. of toilets, tubs, and showers. |  |  |  | EPA IAP
3.2 | Cement board or equivalent moisture-resistant backing material installed on all walls behind tub and shower enclosures composed of tile or panel assemblies with caulked joints. Paper-faced backerboard shall not be used |  |  |  | ENERGY STAR
3.3 | In Warm-Humid climates, Class 1 vapor retarders not installed on the interior side of air permeable insulation in above-grade walls |  |  |  | ENERGY STAR
3.4 | Materials w/ visible signs of water damage/mold not installed; framing members/insulation products w/ high moisture content not enclosed |  |  |  | ENERGY STAR
3.5 | All composite wood products, interior paints/finishes, carpet/carpet adhesive/padding certified low-emission. |  |  |  | EPA IAP
4 | Radon, Pest & Combustion Pollutant Mitigation | Rater Verified | Rater Verified | N/A | PROG. REQ.
4.1 | Radon-resistant features installed in Radon Zone 1 homes in accordance with IAP Construction Specification 2.1. |  |  |  | EPA IAP
4.2 | Corrosion-proof rodent/bird screens installed at all openings that cannot be fully sealed (Exception: dryer vents) |  |  |  | ENERGY STAR
4.3 | Emissions standards met for fuel-burning and space-heating appliances; CO alarms installed in each sleeping zone (e.g., common hallway) according to NFPA 720. |  |  |  | EPA IAP
4.4 | Multifamily buildings: Smoking restrictions implemented AND ETS transfer pathways minimized. |  |  |  | EPA IAP
4.5 | Attached garages: Door closer installed on all connecting doors |  |  |  | EPA IAP
Note on D5: The items below and associated comments are intended to give the highlights of requirements from the ENERGY STAR Water Management System Builder Requirements Rev 09 and EPA Indoor airPLUS Rev 04 documents. For additional information on these requirements, and more detailed exemptions please read the ENERGY STAR Water Management Requirements and Indoor airPLUS Construction Specifications document.
Note on D6: See footnote 3 of the ENERGY STAR Water Management System Builder Requirements Rev. 11
Note on D7: Exceptions to the aggregate OR sand requirement (Not applicable in EPA Radon Zone 1)  Dry climates, as defined by 2009 IECC Figure 301.1. (Also exempt from capillary break requirement)  Areas with free-draining soils – identified as Group 1 (Table R405.1, 2009 IRC) by a certified hydrologist, soil scientist, or engineer through a site visit.  Slab-on-grade foundations
Note on D8: Exceptions  Homes built in areas designated as flood zones (conditioned crawlspaces not recommended for use in flood zones).  Raised pier foundations with no walls.  Dry climates, as defined by 2009 IECC Figure 301.1.  Marine climates, as defined by 2009 IECC Figure 301.1, if no air handler or return ducts are installed in the crawlspace
Note on D9: See footnote 7 of ENERGY STAR Water Management requirements
Note on D10: See item 1.1 of IAP specs
Note on D11: See footnote 8 of ENERGY STAR Water Management requirements
Note on D14: Or equivalent system
Note on D15: See footnote 9 & 10 of ENERGY STAR Water Management requirements
Note on D16: Apply pan flashing over the rough sill framing, inclusive of the corners of the sill framing; side flashing that extends over pan flashing; and top flashing that extends over side flashing or equivalent details for structural masonry walls.
Note on D17: Intersecting wall siding shall terminate 1 in. above the roof or higher, per manf. recommendations. Continuous flashing shall be installed in place of step flashing for metal and rubber membrane roofs.
Note on D18: See item 1.7 of IAP specs and footnotes 3, 13 & 14 from ENERGY STAR Water Management requirements
Note on D19: See footnote 3 & 15 of ENERGY STAR Water Management requirements
Note on D24: See footnote 16 of ENERGY STAR Water Management requirements
Note on D25: Except at shower and tub walls. See footnote 7 of ENERGY STAR Water Management Requirements.
Note on D26: See footnotes 17 &18 of ENERGY STAR Water Management Requirements
Note on D27: See IAP construction specs for Section 6
Note on D32: Except at shower and tub walls. See footnote 7 of ENERGY STAR Water Management Requirements.
Note on D33: See item 1.7 of IAP specs and footnotes 3, 13 & 14 from ENERGY STAR Water Management requirements
Note on D34: AND in homes with exhaust-only whole-house ventilation EITHER a 70 cfm exhaust fan installed in garage OR a pressure test conducted to verify the effectiveness of the garage-to-house air barrier. See IAP spec for details.

## DOE
BE 3.2
BE 3.3
HCD 2.8
HCD 6.5
LAR 1.1
#REF! | EPA F8
#REF! | LAR 4.2A, 4.2B, 4.4A-E | #REF!
4
#REF!
Note on D8: ====== ID#AAAAQ2DLLw4 Lisa (2021-11-10 22:35:34) 17 -- Hot water delivery systems in single family homes and distributed (individual water heater) systems in multifamily buildings shall meet efficiency requirements found in Section 3.3 of the EPA WaterSense Single-Family New Home Specification along with the following added provisions and allowances. To minimize water wasted while waiting for hot water, the hot water distribution system shall store no more than 0.5 gallons (1.9 liters) of water in any piping/manifold between the hot water source and any hot water fixture. In the case of on-demand recirculation systems, the 0.5 gallon (1.9 liter) storage limit shall be measured from the point where the branch feeding the fixture branches off the recirculation loop, to the fixture itself. To verify that the system stores no more than 0.5 gallons (1.9 liters), verifiers shall calculate the stored volume using the piping or tubing inside diameter and the length of the piping/tubing. System options include manifold-fed systems; core plumbing layouts, and on-demand recirculation systems. The following requirements apply to recirculation systems: a. Recirculation systems must be based on an occupant-controlled switch or an occupancy sensor, installed in each bathroom which is located beyond a 0.5 gallon stored-volume range from the water heater. b. Recirculation systems which operate based on “adaptive” scheduling, meaning that they “learn” the hot water demand profile in the home and adapt their operation to anticipate this profile, are permitted at this time, and do not require the use of occupant-controlled switches or occupancy sensors. c. Recirculation systems that are activated based solely on a timer and/or temperature sensor are not eligible. No more than 0.6 gallons (2.3 liters) of water shall be collected from the hot water fixture before hot water is delivered. To verify that the system meets the 0.6 gallon (2.3 liter) limit, verifiers shall first initiate operation of ondemand recirculation systems, if present, and let such systems run for at least 40 seconds. If an Adaptive Scheduling system cannot be “forced” into recirculation mode, contact DOE for further guidance. Next, a bucket or flow measuring bag (pre-marked for 0.6 gallons) shall be placed under the hot water fixture. The hot water shall be turned on completely and a digital temperature sensor used to record the initial temperature of the water flow. Once the water reaches the pre-marked line at 0.6 gallons (approximately 24 seconds for a lavatory faucet), the water shall be turned off and the ending temperature of the water flow (not the collection bucket) shall be recorded. The temperature of the water flow must increase by ≥ 10 °F. Only the fixture with the greatest stored volume between the fixture and the hot water source (or recirculation loop) needs to be tested. Under the DOE Zero Energy Ready Home program, the approved verifier may confirm compliance with these requirements.

## Revision log
3.0.1 (3-4-14)
1) Ventilation - cells AB42, AC42, AB51, AC51 - added formula to sum the individual branch measurments for reference only
2) Ventilation - cell AF2 - added comment describing the "in balance" specification (+/-20% or 5cfm, whichever is greater)
3) DHW+Lights+Appliances - added item #3 for DHW model #, AHRI certificate and photo
4) Renewable Energy Ready - For item #1, updated the PV Watts hyperlink to the new PV Watts site…and added screen shot examples over to the right from PV Watts
5) Heating-Cooling: added note to item 1 "HVAC installer is required to be an accredited installer approved by Energy Star (for example, ACCA) if the heating or cooling system is a split air conditioner, unitary (packaged outside) air conditioner, air-source heat pump, water/ground source ("geothermal") heat pump up to 65,000Btu/hr with a ducted distribution system or a furnace up to 225,000Btu/hr with a ducted distribution system. All other permutations of equipment (e.g. boilers, mini-split / multi-split systems) and distribution systems are exempt."
3.0.2 (3-13-14)
1) Added more footnotes to Building Envelope 6.2 and 6.3
4.0.2 (5/18/17)
1) Totally revamped workbook to reflect newest ENERGY STAR, IAP and ZERH requirements
4.0 (8/10/17)
1) Requirement to supply fresh air to all bedrooms
2) Revised the previous 10' requirement for 'stretched string' distance between exhaust/suppy ports on exterior of building. Now, recommend 10', requirement is a minimum 5' separation but must follow manufacturer's recommendations.
4.1 (1/2019)
1) Updated entire workbook to coincide with PHIUS 2018 Standard; Energy Star V3.1, Rev09; Indoor AirPLUS v1, Rev04 & DOE ZERH Requirements
4.2 (7/2021)
1) Updated to add Electric Vehicle Readiness Checklist items
2) Updated to add Electrification Readiness Checklist items
3) Updated to Phius Certified Rater/Verifier from PHIUS+ Rater/Verifer
4) Updated to align with ENERGY STAR v3.1 (Rev11)

## Appendix Calculators
spreadsheet created by John Semmelhack
send comments to semmelhack@think-little.com
Estimate depressurization, given an exhaust airflow rate and an estimated cfm50 blower door test result:
dP = 50*((cfmfan/cfm50)^(1/0.65))
cfmfan | cfm50 | dP
#DIV/0!
Estimate airflow with a given pressure difference and a known cfm50 result
cfm50 | dP | cfmdp
0
Airflow in cfm of an unrestricted hole at a known pressure difference:
Airflow = (area of hole in2) x (Pa^0.5)
Hole | Pa | Airflow
0
Volume of standing water calculator
| Size |  | Type | Oz. per ft | Length | Ozs.
Trunk | [5 empty] | 0
Branch | [5 empty] | 0
Twig | [5 empty] | 0
TOTAL | [5 empty] | 0
TOTAL in gallons | [5 empty] | 0