## Calculator
Latent Cooling Load Calculator v2.3
| SOURCE: ASHRAE Fundamentals 2013 |  | Default
| Chapter 17 |  | Input
Calc'd value
| Description | Value | Units | Source
| Location | Chicago, IL (Midway) |  | WUFI / Project Data
| Dehumidification design humidity ratio (0.4%) | 134 | grains/lb | ASHRAE
| Mean Coincident DB @ Design dehum ratio | 84.1 | F | ASHRAE
| Net Volume | 63545 | ft3 | WUFI / Project Data
| Occupancy | 24 | people | WUFI / Project Data
| iCFA | 9177 | ft2 | WUFI / Project Data
| Qvi (combined infiltration/ventilation flow rate, not including balanced component) - NATURAL infiltration rate | 0.13 | 1/hr | WUFI / Project Data
| Qvi | 137.6808 | cfm | Calc
| HRV/ERV? (YES/NO) | YES |  | WUFI / Project Data
| Es, ERV/HRV sensible effectiveness | 84% | % (0-1) | WUFI / Project Data
| Qbal, hr | 480 | cfm | WUFI / Project Data
| Qbal, oth | 14.16 | cfm | WUFI / Project Data
| Indoor Temp | 77 | F | Default
| Outdoor Temp (MCDB @ DDHR) | 84.1 | F | ASHRAE
| delta T | 7.1 | F | Calc
| Outdoor moisture | 134 | grains/lb | ASHRAE
| Outdoor moisture | 0.019143 | lbw/lbda | Calc
| Indoor Moisture (default to 77F, 60% RH) | 83.2734 | grains/lb | Default
| Indoor Moisture (default to 77F, 60% RH) | 0.011896 | lbw/lbda | Default
| delta W | 0.0072467 | humidity ratio difference | Calc
| Et, ERV/HRV total effectiveness | 64% | % (0-1) | WUFI / Project Data ?
| Outdoor air enthalpy (with DB & Humidity Ratio) | 41.5 | BTU/lb | Psychometric Chart/Calc
| Indoor Air enthalpy (default to 77F, 60% RH) | 31.5086 | BTU/lb | Default
| delta h | 9.9914 | BTU/lb | Calc
| Cs (air sensible heat factor) default 1.1 @ sea level. Applicable up to 1000ft in elevation. More info in Chapter 18 | 1.1 | BTU/hr.F.cfm | Default
| Cl (air latent heat factor) | 4840 | BTU/hr.cfm | Default
| Ct (air total heat factor) | 4.5 | BTU/hr.cfm/BTU/lb | Default
(15) | qvi,s (sensible ventilation/infiltration load) | 1785.6849 | BTU/hr | Calc
(17) | qvi,t | 14596.3032 | BTU/hr | Calc
(16) | qvi,l NO HRV/ERV | 22161.0596 | BTU/hr | Calc
| qvi,l with HRV/ERV | 12810.6183 | BTU/hr | Calc
(18) | qvi, l (Ventilation/infiltration latent gain) | 12810.6183 | BTU/hr
(31) | qig, l (intenal latent gain) | 1694.39 | BTU/hr
(32) | TOTAL LATENT COOLING LOAD | 14505.0083 | BTU/hr
Note on C10: WUFI Passive Peak Cooling temp is 83.7 F

## WUFI Passive Latent Demand (hidden)
Latent Cooling Demand in WUFI Passive:
UsefullCoolingDemand_latent_kWh_m2a = 0.0
for (int i = 0; i < CountCoolingConditions; i++) // for each month, also regaring the –more detailed- June
{double absHumdidity_SupplyAir_Subresult = 0.0;
if (HeatAndMoistureRecoveryAktive[i])
{absHumdidity_SupplyAir _Subresult = AbsHumiditySupplyAirWithHeatRecovery[i];}
else
{absHumdidity_SupplyAir _Subresult = AbsHumiditySupplyAirWithoutHeatRecovery[i];}
VentilationHumdiditySourceAtSollHumidity_kg_h[i] =
MassflowrateSupplyAir_Cooling_kg_h * (absHumdidity_SupplyAir_Subresult) + (MassflowrateAmbientAir_Cooling_kg_h + MassflowrateWindowVentilation_Cooling_kg_h[i] + MassflowrateConstantVentilation_Cooling_kg_h[i]) * AbsHumidityAmbientAir_Cooling_kg_kg[i] - (MassflowrateSupplyAir_Cooling_kg_h + MassflowrateAmbientAir_Cooling_kg_h + MassflowrateWindowVentilation_Cooling_kg_h[i] + MassflowrateConstantVentilation_Cooling_kg_h[i]) * MaxHumidityRatio_Dehumidification_g_kg / 1000; // # kg/h
DehumidificationPowerStatic_W[i] = Math.Max(0, (VentilationHumdiditySourceAtSollHumidity_kg_h[i] + InternHumiditySource_kg_h) * EnthalpyOfVaporization_Designtemperature); //# W
DehumidificationEnergyDemand_kWh[i] = Math.Max(HoursInMonth_Cooling[i] * DehumidificationPowerStatic_W[i] / 1000, 0); // # kWh
if (double.IsNaN(DehumidificationEnergyDemand_kWh[i]))
{
DehumidificationEnergyDemand_kWh[i] = 0.0;
}
if (i != 6 && i != 16)
{
UsefullCoolingDemand_latent_kWh_m2a += DehumidificationEnergyDemand_kWh[i];
}
}
UsefullCoolingDemand_latent_kWh_m2a /= TreatedFloorArea_m2;