## Cover Sheet
Phius Quality Control Workbook for Multifamily Projects* - v24.1.0 (August 2024)
*For projects with multiple buildings, please create a Workbook for each building in the project.
Project Information
Project Name | Phius Project Number | Building Permit Date | Number of Stories | Total # Dwelling Units | Country
[Select]
Street Address | City |  | State/Province | Zip Code | Project Path | Project Certification Standard
|  |  | [Select] |  | [Select] | [Select]
Confirm most current set of building drawings used by Verifier have been included in the project documentation folder: |  |  |  |  | [Select]
Project Team | Company Name |  |  |  | Contact Name
Phius Certified Verifier:
Phius Certified Consultant (CPHC):
Architect:
General Contractor / Builder: |  |  | DOE ZERH Builder ID#:
Mechanical Systems Designer:
HVAC Contractor:
Functional Testing Agent (FTA):
Building Owner:
Ducted heating/cooling systems in dwelling units: |  |  | [Select]
HVAC Contractor must be H-QUITO / ESTAR Credentialed: |  |  | Pending input from cell G24
Functional Testing Agent (FTA) is qualified per: |  |  | [Select]
CO-REQUISITE PROGRAM ELIGIBILITY(1,2) |  |  |  | CO-REQUISITE PROGRAM VERSION(1,2)
Select the applicable eligibility based on the Phius Certification Guidebook Section 1.5.3 Program Eligibility Criteria |  |  |  | Input the applicable program version based on the project permit date and its geographic location based on co-requisite program guidelines.
Program | Program Eligibility |  |  | Program |  | Program Version & Revision Number
ENERGY STAR Multifamily New Construction (MFNC) | [Select] |  |  | ENERGY STAR Multifamily New Construction (MFNC) |  | [Select]
EPA Indoor airPLUS | Certification Required in the US |  |  | EPA Indoor airPLUS |  | [Select]
DOE ZERO ENERGY READY HOME (ZERH) | [Select] |  |  | DOE ZERO ENERGY READY HOME (ZERH) |  | [Select]
Welcome to the Phius Quality Assurance Workbook for Multifamily Projects!
Certification Criteria The Phius Certification process for multifamily projects includes energy modeling and design consulting performed by a Phius Certified Consultant (CPHC) to demonstrate compliance with Phius program energy performance metrics, as well as on-site verification of all critical project energy features by a Phius Certified Verifier. Projects within the United States must be certified under the EPA ENERGY STAR Multifamily New Construction (MFNC), DOE Zero Energy Ready Homes (ZERH), and EPA Indoor airPLUS (IAP) programs. Projects located outside of the United States must meet certification criteria from the National Version 3.2 for Single Family New Homes, and National Version 1.2 for Multifamily New Construction, even though certification is not required. For full program requirements, please see the Phius Certification Guidebook (https://www.phius.org/phius-certification-guidebook).
Using This Workbook This workbook shall be used for all eligible duplexes, townhouses, and multifamily projects, regardless of size.
There are ten worksheets to complete (see the tabs below).
Responsible parties for completing each tab are listed here.
0 - Key Documents |  |  |  | Phius Certified Verifier
1.1 - Building Envelope Whole Building (WB) |  |  |  | Phius Certified Verifier
1.2 - Building Envelope Compartmentalization (Comp) |  |  |  | Phius Certified Verifier
2.1 - Ventilation Centralized (Vent Cent) |  |  |  | Phius Certified Verifier
2.2 - Ventilation Decentralized-Dwelling Unit (Vent DCent_DU_) |  |  |  | Phius Certified Verifier
2.3 - Ventilation Decentralized-Common Space (Vent DCent_Common_ERV#) |  |  |  | Phius Certified Verifier
3 - Heating & Cooling |  |  |  | HVAC Designer/Contractor, Phius Certified Verifier
4 - Domestic Hot Water |  |  |  | Phius Certified Verifier
5 - Appliances & Electrical Loads |  |  |  | Phius Certified Verifier
6 - Renewables & Electrification |  |  |  | Phius Certified Verifier
Data entry cells are in teal. Checkbox cells are in white. Calculation cells are in light gray. Do not change the calculation cells!
Phius Certified Verifiers are welcome to add their own custom sheets to this workbook for instance, to track project notes.
Questions regarding particular checklist items should be directed first to the Phius Verifier for the project. - Contact the Phius QA/QC Manager at QA@phius.org for questions on the nuances between certifying an entire building under Phius and certifying individual dwelling units within such buildings under ESTAR/ZERH. - Contact https://www.phius.org/help for questions regarding the certification process for any project.

## 0-Key Documents
Key Documents Phius Quality Assurance
The Phius Certified Rater is responsible for providing these key documents in Section 4 of the Phius On-Site QA folder (*Coordinate with CPHC). Any additional content needed for clarification of building and its construction shall be added to Rater Notes in this spreadsheet.
0 | 0 - Certificates & Summaries / Co-requisite Programs | Rater Confirmed | N/A | PROG. REQ.
0.0.1 | Phius Quality Control Field Checklist Completed. |  |  | Phius
0.0.2 | Provide Energy Star Certificate or Home Report. |  |  | ESTAR
0.0.3 | Provide Indoor airPLUS Certificate. |  |  | IAP
0.0.4 | Provide DOE ZERH Certificate. |  |  | ZERH
0.0.5 | Provide Building Summary from HERS® Rating Software. |  |  | Phius
0.1 | 1 - Building Envelope | Rater Confirmed | N/A | PROG. REQ.
0.1.1 | Insulated Assemblies (Material & R-value verification)
0.1.1.1 | Provide insulation datasheets that were not submitted during Phius Design Review.* |  |  | Phius
0.1.1.2 | Provide insulation datasheets when a product has been changed since Phius Design Review. |  |  | Phius
0.1.2 | Windows & Doors
0.1.2.1 | If no NFRC sticker, provide Window Purchase Order or Shop Drawings. |  |  | Phius
0.1.2.2 | Provide datasheets of any product that has been changed since Phius Design Review. |  |  | Phius
0.1.3 | Airtightness
0.1.3.1 | Provide Air Tightness Test Report (depressurization and pressurization). |  |  | Phius
0.1.3.2 | Energy Star Multifamily New Construction Program (MFNC): Provide Energy Star Multifamily Workbook. |  |  | Phius
0.2 | 2 - Ventilation | Rater Confirmed | N/A | PROG. REQ.
0.2.1 | If ventilation system is a Minotair, provide a completed Phius MINOTAIR PentaCare calculator. |  |  | Phius
0.2.2 | Energy Star Multifamily New Construction (MFNC): Provide Testing and Balancing (TAB) report of ducted ventilation system. |  |  | Phius
0.3 | 3 - Heating & Cooling | Rater Confirmed | N/A | PROG. REQ.
0.3.1 | Provide AHRI certificate and/or manufacturer's detailed specs of each installed heating, cooling, and DHW system. |  |  | Phius
0.3.2 | Provide duct/pipe layout drawing, total system design airflow, branch design airflows, and schedule showing duct/pipe sizes and insulation. |  |  | Phius
0.3.3 | Energy Star Single Family New Home (SFNH): Provide Energy Star SFNH National HVAC Commissioning Checklist, Version 3 / 3.1 / 3.2 (Rev. 13), and all items under line 4, "Air Balancing of Supply Registers & Return Grilles," are required. |  |  | Phius
0.3.4 | Energy Star Multifamily New Construction (MFNC): All items under Line 4, "Air Balancing of Supply Registers & Return Grilles," of the National HVAC Functional Testing Checklist, Version 1 / 1.1 / 1.2 (Rev. 04) are required. |  |  | Phius
0.4 | 4 - Domestic Hot Water | Rater Confirmed | N/A | PROG. REQ.
0.4.1 | Provide Energy Star datasheet (https://www.energystar.gov/products) or AHRI Certificate for each installed DHW system. |  |  | Phius
0.5 | 5 - Appliances & Electrical Loads | Rater Confirmed | N/A | PROG. REQ.
0.5.1 | Provide Energy Star Certificate (https://www.energystar.gov/products) for each builder-installed appliance and dehumidifier. |  |  | Phius
0.5.2 | For all other appliances, provide equivalent documentation. |  |  | Phius
0.5.2 | Provide Project Team's detailed lighting plan. |  |  | Phius
0.6 | 6 - Renewables & Electrification | Rater Confirmed | N/A | PROG. REQ.
0.6.1 | Provide shop drawings or documentation that show the tilt, azimuth, and kW size of each installed PV system. |  |  | Phius
0.6.2 | Provide completed ZERH PV-Ready Checklist. |  |  | ZERH
0.6.3 | Provide completed ZERH SF Homes National Rater Checklist or ZERH MF EV Ready Checklist. |  |  | ZERH
0.6.4 | Provide contract documents for any off-site renewable production that align with Appendix N-13.3 (Renewable Energy) of the Phius 2024 Certification Guidebook. |  |  | ZERH
Rater Notes:

## 1.1-Building Envelope (WB)
Whole Building Airtightness Testing Phius Quality Assurance
The Phius Certified Verifier is responsible for verifying all items on this worksheet.
Any additional content needed for clarification of building and its construction shall be added to Verifier Notes in this spreadsheet.
| 1.1 | Whole Building Airtightness Testing
| 1.1.1 | Blower Door Test Threshold Calculator |  | Building is 5+ stories in height & non-combustible construction? |  | [Select]
Building Envelope Area (ft2)
|  |  |  | Project Threshold (CFM50/ft2) |  | Pending Input
Project Threshold (CFM50)
| 1.1.2 | Was a taped test performed during final blower door testing? (For more information on what is allowed on a taped test, see Phius Certification Guidebook 2024, Appendix C-2.3)1,2 |  | [Select]
| 1.1.3 | If taped test, please list those items taped:
| 1.1.4 | If untaped test, please list those items taped:
#REF! | 1.1.5 | Preliminary test: Preliminary whole building blower door test in accordance with ANSI/RESNET/ICC 380-20223 or latest version is: | Mandatory for Prescriptive Path Projects, optional for all others. | Preliminary Test | (CFM50/ft2) | CFM50
Depressurization Test Result
Pressurization Test Result
Average Test Result
| 1.1.6 | Untaped test: Final whole building blower door multi-point test in accordance with ANSI/RESNET/ICC 380-20223 or latest version. (an untaped test is mandatory) |  | Final Test (Untaped - mandatory) | (CFM50/ft2) | CFM50
Depressurization Test Result
Pressurization Test Result
Average Test Result
Criteria Passed?
| 1.1.7 | Taped test: Final whole building blower door multi-point test in accordance with ANSI/RESNET/ICC 380-2022* or latest version. (taped, if necessary) |  | Final Test (Taped - if necessary) | (CFM50/ft2) | CFM50
Depressurization Test Result
Pressurization Test Result
Average Test Result
Criteria Passed?
Verifier Notes:
1. The Phius requirement of 0.06 cfm50/sqft must be met through a taped test. If an untaped test result is less than 0.06 cfm50/sqft, a taped test is not necessary.
2. The result of the untaped test is always input into the WUFI model. An untaped test is always required.
3. NOTE: For Large MF or Non-Res. Bldgs- Alternative Test methods and building set up - per ABAA Standard Method for Building Enclosure Airtightness Compliance Testing, ASTM E-3158 or ASTM E-779.

## 1.2-Building Envelope (Comp)
Dwelling Unit Compartmentalization Testing Phius Quality Assurance
The Phius Certified Verifier is responsible for verifying all items on this worksheet.
Any additional content needed for clarification of building and its construction shall be added to Verifier Notes in this spreadsheet.
Dwelling Unit Compartmentalization Test: Compartmentalization testing shall be performed to test air tightness of individual dwelling units in accordance with ANSI/RESNET/ICC Std 380-2022. The test threshold shall be 0.3 CFM50 / sq ft of unit Shell/Envelope area expressed in CFM/SF. Testing may be performed using RESNET Chapter 6 and MINHERS Addendum 46 sampling protocols. Please discuss SAMPLING with your RESNET QA Provider and Phius PRIOR TO initiating sampling to ensure they will support sampling being applied to the project. Please document compartmentalization results below.
Testing protocol
Testing shall be performed following ANSI/RESNET/ICC Standard 380-2022 and RESNET MINHERS Standards for Multifamily Energy Ratings.
https://www.resnet.us/about/standards/resnet-ansi/
https://www.resnet.us/about/standards/minhers/2013-mortgage-industry-national-home-energy-rating-standards-and-addenda/
1.2.1 | Compartmentalization Airtightness Testing Sampling Documentation
1.2.1.1 | Total # of dwelling units in project:
1.2.1.2 | # Dwelling Units tested in Initial Sample Set [requirement minimum is five (5) Dwelling Units]
1.2.1.3 | # Dwelling Units tested in Qualification Set [requirement minimum is five (5) consecutive Dwelling Units without incidence of failure]:
1.2.1.4 | Airtightness Threshold Specifications have been verified in five (5) consecutive Dwelling Units without incidence of failure: |  |  | [Select]
1.2.1.5 | # Dwelling Units sampled [20% of remaining units]:
1.2.1.6 | # Dwelling Units sampled at 20% + X% [if X% is projected to be removed as Confirmed Ratings]:
1.2.2 | Compartmentalization Airtightness Testing Sampling Results
1.2.2.1 | Highest measured cfm50/sqft: |  | Dwelling Unit # with highest measured cfm50/sqft:
1.2.2.2 | Lowest measured cfm50/sqft: |  | Dwelling Unit # with lowest measured cfm50/sqft:
Verifier Notes:
Note on A1: Mark Smith:

## 2.1-Vent Cent_ERV#
Ventilation - Centralized Systems Phius Quality Assurance
This worksheet shall be completed for centralized E/HRV systems servicing multiple dwelling units or multiple common spaces.
The ventilation rates of the individual registers shall be measured at the design 24/7 ventilation rate.
Sampling: The Phius Certified Verifier is responsible for verifying* airflows in accordance with the steps below: Step 1: Count the number of centralized ventilation units. Step 2: For each ventilation unit, duplicate this tab, naming each successive tab: 2.1-Vent Cent_ERV1, 2, 3, etc. Step 3: Count the number of dwelling unit types (studio, 1 bdrm, 2 bdrm, etc.) served by each centralized ventilator. Step 4: Measure airflows in a minimum of 3 of each dwelling unit type per centralized ventilator.** Step 5: No fewer than 10% of the dwelling units shall be measured, per centralized ventilator. Step 6: Complete section 2.1 below. *Verification means either Verifier has measured or directly observed. **If there are fewer than 3 of any dwelling unit type, measure all dwelling units of that type.
Any additional content needed for clarification of building and its construction shall be added to Verifier Notes in this spreadsheet.
2.1 | Individual Dwelling Unit Airflow Rates Measured at each Register
| 2.1.1 | 2.1.2 |  | 2.1.3 |  | 2.1.4 |  |  | 2.1.5 | 2.1.6 | 2.1.7 | 2.1.8 | 2.1.9 | 2.1.10 | 2.1.11
| E/HRV # | System Type |  | Manufacturer |  | Model # |  |  | MERV Rating of Filter | Duct R-Value (Supply) | Duct R-Value (Exhaust) | Type of ERV/HRV defrost | Total Supply Airflow (cfm) from TAB report | Measured Fan Power (Watts) | Electric Efficiency (W/cfm)
|  | [Select] | [9 empty] | [Select] |  |  | -
| 2.1.12 | Supply Airflow (24/7) | [8 empty] | Airflow (cfm) |  | Room Pressure Difference [Pa] | Status
|  | Dwelling Unit # / Space # | Dwelling Unit / Space Type |  | Register Location (Supply) |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | <1 Pa Pressure Difference
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  |  | [Select] |  | enter supply register location here (Master Bed, Guest Bed, Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
| 2.1.13 | Exhaust Airflow (24/7) | [8 empty] | Airflow |  |  | Status
|  | Dwelling Unit # / Space # | Dwelling Unit / Space Type |  | Register Location (Exhaust) |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | ≥Minimum
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  |  | [Select] |  | enter exhaust register location here (Kitchen, Master Bath, Trash, Bike Room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
Auxiliary Ventilation Systems
| 2.1.14 | Auxiliary Ventilation Systems |  |  | Manufacturer |  | Model |  | Design Airflow (cfm) |  | Average Measured Airflow (cfm) |  | n/a
Direct Exhaust Range Hood
Direct Exhaust Bathroom Fan
Make-up Air System
Miscellaneous Exhaust
Ventilator Defrost Systems
| 2.1.15 | If a ground loop or earth tube was installed: | [8 empty] | Measurement |  | n/a
Enter loop length:
Enter approximate depth:
Measure loop pump power:
|  | Project team has demonstrated the ground loop / earth tube control logic is set up properly. | [8 empty] | [Select]
Verifier Notes:

## 2.2-Vent DCent_DU_
Ventilation - Decentralized Systems (servicing dwelling units only) Phius Quality Assurance
This worksheet to be completed for decentralized E/HRVs servicing individual dwelling unit (DU) types only.
The ventilation rates of the individual registers shall be measured at the design 24/7 ventilation rate.
Sampling: The Phius Certified Verifier is responsible for verifying* airflows in accordance with the steps below: Step 1: Count the number of dwelling unit types (studio, 1 bdrm, 2 bdrm, etc.). Step 2: For each dwelling unit type, duplicate this tab, naming each successive tab: 2.2-Vent DCent_DU_Studio, 1bdrm, 2bdrm, etc. Step 3: Measure airflows in a minimum of 3 of each dwelling unit type.** Step 4: No fewer than 10% of the total dwelling units shall be measured. Step 5: Complete section 2.2 below.*** *Verification means either Verifier has measured or directly observed. **If there are fewer than 3 of any dwelling unit type, measure all dwelling units of that type. ***If the ventilation system is a Minotair, sample units following the instructions above, complete sections 2.2.1-2.2.10, 2.2.15-2.2.16, and record measurements in the Phius MINOTAIR PentaCare calculator.
Any additional content needed for clarification of building and its construction shall be added to Verifier Notes in this spreadsheet.
2.2 | Individual Dwelling Unit Airflow Rates Measured at each Register
| 2.2.1 | 2.2.2 | 2.2.3 | 2.2.4 | 2.2.5 |  | 2.2.6 |  | 2.2.7 | 2.2.8 | 2.2.9 | 2.2.10 | 2.2.11 | 2.2.12
| Dwelling Unit Type | Dwelling Unit # | E/HRV # | System Type | Manufacturer |  | Model # |  | MERV Rating of Filter | Duct R-Value (Supply) | Duct R-Value (Exhaust) | Type of ERV/HRV defrost | Measured Fan Power (Watts) | Electric Efficiency (W/cfm)
| [Select] |  |  | [Select] | [7 empty] | [Select] |  | -
| 2.2.13 | Supply Airflow (24/7) | [7 empty] | Airflow (cfm) |  | Room Pressure Difference [Pa] | Status
|  | Register Location (Supply) |  |  |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | <1 Pa Pressure Difference
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
Sum of Supply Airflows by E/HRV:
| 2.2.14 | Exhaust Airflow (24/7) | [7 empty] | Airflow |  |  | Status
|  | Register Location (Exhaust) |  |  |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | ≥Minimum
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
Sum of Exhaust Airflows by E/HRV:
Auxiliary Ventilation Systems
| 2.2.15 | Auxiliary Ventilation Systems |  |  | Manufacturer |  | Model | Design Airflow (cfm) |  | Measured Airflow (cfm)
Direct Exhaust Range Hood
Direct Exhaust Bathroom Fan
Make-up Air System
Miscellaneous Exhaust
Ventilator Defrost Systems
| 2.2.16 | If a ground loop or earth tube was installed: | [7 empty] | Measurement
Enter loop length:
Enter approximate depth:
Measure loop pump power:
|  | Project team has demonstrated the ground loop / earth tube control logic is set up properly. | [7 empty] | [Select]
Verifier Notes:
2.2 | Individual Dwelling Unit Airflow Rates Measured at each Register
| 2.2.1 | 2.2.2 | 2.2.3 | 2.2.4 | 2.2.5 |  | 2.2.6 |  | 2.2.7 | 2.2.8 | 2.2.9 | 2.2.10 | 2.2.11 | 2.2.12
| Dwelling Unit Type | Dwelling Unit # | E/HRV # | System Type | Manufacturer |  | Model # |  | MERV Rating of Filter | Duct R-Value (Supply) | Duct R-Value (Exhaust) | Type of ERV/HRV defrost | Measured Fan Power (Watts) | Electric Efficiency (W/cfm)
| [Select] |  |  | [Select] | [7 empty] | [Select] |  | -
| 2.2.13 | Supply Airflow (24/7) | [7 empty] | Airflow (cfm) |  | Room Pressure Difference [Pa] | Status
|  | Register Location (Supply) |  |  |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | <1 Pa Pressure Difference
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
Sum of Supply Airflows by E/HRV:
| 2.2.14 | Exhaust Airflow (24/7) | [7 empty] | Airflow |  |  | Status
|  | Register Location (Exhaust) |  |  |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | ≥Minimum
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
Sum of Exhaust Airflows by E/HRV:
Auxiliary Ventilation Systems
| 2.2.15 | Auxiliary Ventilation Systems |  |  | Manufacturer |  | Model | Design Airflow (cfm) |  | Measured Airflow (cfm)
Direct Exhaust Range Hood
Direct Exhaust Bathroom Fan
Make-up Air System
Miscellaneous Exhaust
Ventilator Defrost Systems
| 2.2.16 | If a ground loop or earth tube was installed: | [7 empty] | Measurement
Enter loop length:
Enter approximate depth:
Measure loop pump power:
|  | Project team has demonstrated the ground loop / earth tube control logic is set up properly. | [7 empty] | [Select]
Verifier Notes:
2.2 | Individual Dwelling Unit Airflow Rates Measured at each Register
| 2.2.1 | 2.2.2 | 2.2.3 | 2.2.4 | 2.2.5 |  | 2.2.6 |  | 2.2.7 | 2.2.8 | 2.2.9 | 2.2.10 | 2.2.11 | 2.2.12
| Dwelling Unit Type | Dwelling Unit # | E/HRV # | System Type | Manufacturer |  | Model # |  | MERV Rating of Filter | Duct R-Value (Supply) | Duct R-Value (Exhaust) | Type of ERV/HRV defrost | Measured Fan Power (Watts) | Electric Efficiency (W/cfm)
| [Select] |  |  | [Select] | [7 empty] | [Select] |  | -
| 2.2.13 | Supply Airflow (24/7) | [7 empty] | Airflow (cfm) |  | Room Pressure Difference [Pa] | Status
|  | Register Location (Supply) |  |  |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | <1 Pa Pressure Difference
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Master Bed, Guest Bed, etc.) |  |  |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
Sum of Supply Airflows by E/HRV:
| 2.2.14 | Exhaust Airflow (24/7) | [7 empty] | Airflow |  |  | Status
|  | Register Location (Exhaust) |  |  |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | ≥Minimum
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Kitchen, Master Bath, etc.) |  |  |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
Sum of Exhaust Airflows by E/HRV:
Auxiliary Ventilation Systems
| 2.2.15 | Auxiliary Ventilation Systems |  |  | Manufacturer |  | Model | Design Airflow (cfm) |  | Measured Airflow (cfm) |  | n/a
Direct Exhaust Range Hood
Direct Exhaust Bathroom Fan
Make-up Air System
Miscellaneous Exhaust
Ventilator Defrost Systems
| 2.2.16 | If a ground loop or earth tube was installed: | [7 empty] | Measurement |  | n/a
Enter loop length:
Enter approximate depth:
Measure loop pump power:
|  | Project team has demonstrated the ground loop / earth tube control logic is set up properly. | [7 empty] | [Select]
Verifier Notes:

## 2.3-Vent DCent_Common_ERV#
Ventilation - Decentralized Systems (servicing common spaces only) Phius Quality Assurance
This worksheet to be completed for decentralized E/HRVs servicing a common space only.
The ventilation rates of the individual registers shall be measured at the design 24/7 ventilation rate.
Sampling: The Phius Certified Verifier is responsible for verifying* airflows in accordance with the steps below: Step 1: Count the number of E/HRVs servicing common spaces. Step 2: Complete section 2.3 below.** Step 3: For each E/HRV serving a common space, duplicate this tab, naming each successive tab: 2.3-Vent DCent_Common_ERV1, 2, 3,etc. *Verification means either Verifier has measured or directly observed. **If the ventilation system is a Minotair, sample units following the instructions above, complete sections 2.3.1-2.3.8, 2.3.13-2.3.14, and record measurements in the Phius MINOTAIR PentaCare calculator creating a separate tab for Common Spaces.
Any additional content needed for clarification of building and its construction shall be added to Verifier Notes in this spreadsheet.
2.3 | Individual Dwelling Unit Airflow Rates Measured at each Register
| 2.3.1 | 2.3.2 | 2.3.3 |  | 2.3.4 |  | 2.3.5 | 2.3.6 | 2.3.7 | 2.3.8 | 2.3.9 | 2.3.10
| E/HRV # | System Type | Manufacturer |  | Model # |  | MERV Rating of Filter | Duct R-Value (Supply) | Duct R-Value (Exhaust) | Type of ERV/HRV defrost | Measured Fan Power (Watts) | Electric Efficiency (W/cfm)
|  | [Select] | [7 empty] | [Select] |  | -
| 2.3.11 | Supply Airflow (24/7) | [5 empty] | Airflow (cfm) |  | Room Pressure Difference [Pa] | Status
|  | Register Location (Supply) |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | <1 Pa Pressure Difference
|  | enter supply register location here (Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
|  | enter supply register location here (Corridor, Office, etc.) |  |  | [Select Room Type - Supply] | [5 empty] | - | - | -
Sum of Supply Airflows by E/HRV:
| 2.3.12 | Exhaust Airflow (24/7) | [5 empty] | Airflow |  |  | Status
|  | Register Location (Exhaust) |  |  | Room Type |  |  | Design (cfm) | Verified (cfm) |  | ≥Design | Within +5cfm or +20% | ≥Minimum
|  | enter exhaust register location here (Trash, Bike room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Trash, Bike room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Trash, Bike room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Trash, Bike room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
|  | enter exhaust register location here (Trash, Bike room, etc.) |  |  | [Select Room Type - Exhaust] | [5 empty] | - | - | -
Sum of Exhaust Airflows by E/HRV:
Auxiliary Ventilation Systems
| 2.3.13 | Auxiliary Ventilation Systems |  | Manufacturer | Model | Design Airflow (cfm) |  | Measured Airflow (cfm) |  | n/a
Direct Exhaust Range Hood
Direct Exhaust Bathroom Fan
Make-up Air System
Miscellaneous Exhaust
Ventilator Defrost Systems
| 2.3.14 | If a ground loop or earth tube was installed: | [5 empty] | Measurement |  | n/a
Enter loop length:
Enter approximate depth:
Measure loop pump power:
|  | Project team has demonstrated the ground loop / earth tube control logic is set up properly. | [5 empty] | [Select]
Verifier Notes:

## 3-Heating & Cooling
Heating & Cooling Phius Quality Assurance
The Phius Certified Verifier is responsible for verifying all items on this worksheet.
Any additional content needed for clarification of building and its construction shall be added to Verifier Notes in this spreadsheet.
3 | Heating/Cooling System | [9 empty] | Verifier Confirmed | N/A | PROG. REQ.
3.0.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Manufacturer | Model# | Quantity | MERV Rating of Filter | Heating/Cooling System Type | Ducted or Ductless? | Individual or Shared? | AHRI Certificate Uploaded? | Photos Uploaded?
3.0.1.1 | [5 empty] | [Select] | [Select] | [Select] | [Select] | [Select] |  |  | Phius
3.0.1.2 | [5 empty] | [Select] | [Select] | [Select] | [Select] | [Select]
3.0.1.3 | [5 empty] | [Select] | [Select] | [Select] | [Select] | [Select]
3.0.1.4 | [5 empty] | [Select] | [Select] | [Select] | [Select] | [Select]
3.0.2 | Describe any supplemental heating/cooling systems installed:
Phius
Verifier Notes

## 4-Domestic Hot Water
Domestic Hot Water Phius Quality Assurance
The Phius Certified Verifier is responsible for verifying all items on this worksheet.
Any additional content needed for clarification of building and its construction shall be added to Verifier Notes in this spreadsheet.
4 | Domestic Hot Water Systems | [6 empty] | Verifier Confirmed | N/A | PROG. REQ.
4.0.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Hot Water System Type | Manufacturer | Model # | Quantity | Energy Star Certificate Uploaded? | Photos Uploaded?
4.0.1.1 |  | [Select] |  |  |  | [Select] | [Select] |  |  | Phius
4.0.1.2 |  | [Select] |  |  |  | [Select] | [Select]
4.0.1.3 |  | [Select] |  |  |  | [Select] | [Select]
4.0.1.4 |  | [Select] |  |  |  | [Select] | [Select]
Verifier Notes

## 5-Appliances & Electrical
Appliances & Electrical Loads Phius Quality Assurance
The Phius Certified Verifier is responsible for verifying all items on this worksheet.
Any additional content needed for clarification of building and its construction shall be added to Verifier Notes in this spreadsheet.
5 | Appliances | [6 empty] | Verifier Confirmed | N/A | Prog Req.
5.0.1 | Refrigerators Freezers Wine Coolers | Manufacturer | Model # |  | Quantity | Energy Star Certificate Uploaded? | Photos Uploaded?
5.0.1.1 | Type 1 |  |  |  |  | [Select] | [Select] |  |  | DOE ZERH
5.0.1.2 | Type 2 |  |  |  |  | [Select] | [Select]
5.0.1.3 | Type 3 |  |  |  |  | [Select] | [Select]
5.0.1.4 | Type 4 |  |  |  |  | [Select] | [Select]
5.0.1.5 | Type 5 |  |  |  |  | [Select] | [Select]
5.0.1.6 | Type 6 |  |  |  |  | [Select] | [Select]
5.0.2 | Dishwashers | Manufacturer | Model # |  | Quantity | Energy Star Certificate Uploaded? | Photos Uploaded?
5.0.2.1 | Type 1 |  |  |  |  | [Select] | [Select] |  |  | DOE ZERH
5.0.2.2 | Type 2 |  |  |  |  | [Select] | [Select]
5.0.3 | Clothes Washers | Manufacturer | Model # |  | Quantity | Energy Star Certificate Uploaded? | Photos Uploaded?
5.0.3.1 | Type 1 |  |  |  |  | [Select] | [Select] |  |  | DOE ZERH
5.0.3.2 | Type 2 |  |  |  |  | [Select] | [Select]
5.0.4 | Clothes Dryers | Manufacturer | Model # | Fuel Type | Quantity |  | Photos Uploaded?
5.0.4.1 | Type 1 |  |  | [Select] |  |  | [Select] |  |  | DOE ZERH
5.0.4.2 | Type 2 |  |  | [Select] |  |  | [Select]
5.0.5 | Range/Oven Combination | Manufacturer | Model # | Fuel Type | Quantity |  | Photos Uploaded?
5.0.5.1 | Type 1 |  |  | [Select] |  |  | [Select] |  |  | Phius
5.0.5.2 | Type 2 |  |  | [Select] |  |  | [Select]
5.0.6 | Wall Oven | Manufacturer | Model # | Fuel Type | Quantity |  | Photos Uploaded?
5.0.6.1 | Type 1 |  |  | [Select] |  |  | [Select] |  |  | Phius
5.0.6.2 | Type 2 |  |  | [Select] |  |  | [Select]
5.0.7 | Cooktop | Manufacturer | Model # | Fuel Type | Quantity |  | Photos Uploaded?
5.0.7.1 | Type 1 |  |  | [Select] |  |  | [Select] |  |  | Phius
5.0.7.2 | Type 2 |  |  | [Select] |  |  | [Select]
5.0.8 | Range Hood | Manufacturer | Model # | Direct Exhaust or Recirc? | Quantity |  | Photos Uploaded?
5.0.8.1 | Type 1 |  |  | [Select] |  |  | [Select] |  |  | Phius
5.0.8.2 | Type 2 |  |  | [Select] |  |  | [Select]
5.0.9 | Dehumidifier | Manufacturer | Model # |  | Quantity | Energy Star Certificate Uploaded? | Photos Uploaded?
5.0.9.1 | Type 1 |  |  |  |  | [Select] | [Select] |  |  | Phius
5.0.9.2 | Type 2 |  |  |  |  | [Select] | [Select]
5.0.10 | Miscellaneous | Manufacturer | Model # | Fuel Type | Quantity | Energy Star Certificate Uploaded? | Photos Uploaded?
5.0.10.1 | Type 1 |  |  |  |  | [Select] | [Select] |  |  | Phius
5.0.10.2 | Type 2 |  |  |  |  | [Select] | [Select]
5.1 | Additional Major Electrical/Other Loads | [6 empty] | Verifier Confirmed | N/A | Prog Req.
5.1.1 | Describe any other additional significant energy uses loads on the property, including items like pools, hot tubs, home automation systems, fire pits, etc.
Phius
Verifier Notes

## 6-Renewables & Electrification
Renewables & Electrification Phius Quality Assurance
The Phius Certified Verifier is responsible for verifying all items on this worksheet.
Any additional content needed for clarification of building and its construction shall be added to Verifier Notes in this spreadsheet.
6 | Renewable Energy Systems | [6 empty] | Verifier Confirmed | N/A | PROG. REQ.
6.0.1 | Solar thermal system installed? |  | [Select] | Area: | Orientation: | Tilt: | System type: |  |  | N/A
6.0.2 | Solar photovoltaic system installed?
| A | Array 1 | [Select] | Area: | Orientation: | Tilt: | Peak production (W): |  |  | N/A
| B | Array 2 | [Select] | Area: | Orientation: | Tilt: | Peak production (W):
| C | Array 3 | [Select] | Area: | Orientation: | Tilt: | Peak production (W):
| D | Array 4 | [Select] | Area: | Orientation: | Tilt: | Peak production (W):
6.0.3 | HERS® Index (ERI Path Only for Dwellings)
| HERS® Index with photovoltaic system: | [8 empty] | Phius
HERS® Index without photovoltaic system:
Verifier Notes:
#REF!
1
#REF!

## Dropdown menus
State | Country | >80% | Radon Zone | ducted h/c | Vent Type | system type | Cooktop filter | supply rooms | exhaust rooms | ERV/HRV Defrost | [Select] | Dwelling Unit Type
[Select] | [Select] | [Select] | [Select] | [Select] | [Select] | [Select] | [Select] | [Select Room Type - Supply] | [Select Room Type - Exhaust] | [Select] | Yes | [Select]
AK Alaska | United States | Yes | Zone 1 | Yes | HRV | Individual | MERV 3+ | Bedroom | Bathroom | n/a | N/A | Studio
AL Alabama | Canada | No | Zone 2 | No | ERV | Shared | Washable Mesh | Living Room | 1/2 Bath | Electric |  | 1 Bdr
AR Arkansas | Mexico |  | Zone 3 |  | Minotair |  |  | Dining Room | Kitchen | Hot Water Loop | Cooktop | 2 Bdr
AS American Samoa | Afghanistan | Indiv Heating, Cooling, HW |  |  | CERV |  |  | Corridor | Laundry | Ground Loop | [Select] | 3 Bdr
AZ Arizona | Albania | [Select] | Functional Agent |  |  |  |  | Multipurpose | Trash | Earth Tube | Electric Induction | 4 Bdr
CA California | Andorra | Yes | [Select] |  |  |  |  | Other | Mechanical |  | Electric Resistance | 5 bdr
CT Connecticut | Angola | No | Credentialed per listing on www.energystar.gov/ftas | [5 empty] | Other |  | Gas | Common Space
DC District of Columbia | Argentina | Heating/Cooling Only | Licensed Professional Mechanical Engineer
DE Delaware | Armenia | Water Heating Only | Representative of the Original Equipment Manufacturer (OEM) | [7 empty] | Exhaust Hood Type | Common Space Type
FL Florida | Australia | [9 empty] | [Select] | [Select]
GA Georgia | Azerbaijan | Project Path | Co-Requisite Eligibility | [7 empty] | Direct Exhaust | Common Space
HI Hawaii | Bahamas, The | [Select] | [Select] | [7 empty] | Recirculation
IA Iowa | Bahrain | Performance | Certification Required
ID Idaho | Bangladesh | Prescriptive | Compliance Required, Certification not Required | [7 empty] | Heating/Cooling System Type
IL Illinois | Barbados |  | No Requirements | [7 empty] | [Select]
IN Indiana | Belgium | Certification Path | [8 empty] | air source heat pump
KS Kansas | Benin | [Select] | Energy Star (Multifamily) | [7 empty] | water source heat pump
KY Kentucky | Bhutan | Phius CORE 2021 | [Select] | [7 empty] | ground source heat pump
LA Louisiana | Bolivia | Phius CORE 2024 | National Program, Version 1.2 | [7 empty] | fan coil
MA Massachusetts | Bosnia & Herzegovina | Phius ZERO 2021 | California Program, Version 1.4 | [7 empty] | furnace
MD Maryland | Botswana | Phius ZERO 2024 | n/a | [7 empty] | hydronic
MI Michigan | Brunei
MN Minnesota | Bulgaria |  | Energy Star (Single Family) | [7 empty] | Heating/Cooling System description (1)
MO Missouri | Burkina Faso |  | [Select] | [7 empty] | [Select]
MS Mississippi | Burma |  | National Program, Version 3.2 | [7 empty] | Ducted
MT Montana | Burundi |  | California Program, Version 3.4 | [7 empty] | Ductless
NC North Carolina | Cambodia |  | n/a
ND North Dakota | Cameroon | [9 empty] | Heating/Cooling System description (2)
NE Nebraska | Cape Verde | [9 empty] | [Select]
NH New Hampshire | Cayman Islands |  | Indoor Air Plus | [7 empty] | Individual
NJ New Jersey | Central African Rep. |  | [Select] | [7 empty] | Shared
NM New Mexico | Chad |  | Indoor airPlus Version 1, Rev.4
NV Nevada | Chile |  | Indoor airPlus Version 2, Certified | [7 empty] | Hot Water System Type
NY New York | China |  | Indoor airPlus Version 2, Gold | [7 empty] | [Select]
OH Ohio | Colombia |  | n/a | [7 empty] | HPWH (inside)
OK Oklahoma | Comoros | [9 empty] | HPWH (outside)
OR Oregon | Congo, Dem. Rep. | [9 empty] | Electric (tanked)
PA Pennsylvania | Congo, Repub. of the |  | ZERH Program Version (SF) | [7 empty] | Electric (tankless)
PR Puerto Rico | Cook Islands |  | [Select] | [7 empty] | Gas (tanked)
RI Rhode Island | Costa Rica |  | Single Family National Program Version 2 | [7 empty] | Gas (tankless)
SC South Carolina | Cote d'Ivoire |  | Single Family for California Program Version 2
SD South Dakota | Croatia |  | n/a | [7 empty] | Clothes Dryer
TN Tennessee | Cuba | [9 empty] | [Select]
TX Texas | Cyprus | [9 empty] | Electric Heat Pump
UT Utah | Czech Republic |  | ZERH Program Version (MF) | [7 empty] | Electric Condensing
VA Virginia | Denmark |  | [Select] | [7 empty] | Electric Exhaust Vented
VT Vermont | Djibouti |  | Multifamily National Program Version 2 | [7 empty] | Gas Exhaust Vented
WA Washington | Dominica |  | Multifamily for California Program Version 2
WI Wisconsin | Dominican Republic |  | n/a | [7 empty] | Range/Oven
WV West Virginia | East Timor | [9 empty] | [Select]
WY Wyoming | Ecuador | [9 empty] | Electric
| Egypt | [9 empty] | Gas
AB Alberta | El Salvador
BC British Columbia | Equatorial Guinea
MB Manitoba | Eritrea
NB New Brunswick | Estonia
NF Newfoundland | Ethiopia
NT Northwest Territories | Faroe Islands
NU Nunavut | Fiji
NS Nova Scotia | Finland
ON Ontario | France
PE Prince Edward Island | French Guiana
QC Quebec | French Polynesia
SK Saskatchewan | Gabon
YT Yukon | Gambia, The
Gaza Strip
Georgia
Germany
Ghana
Gibraltar
Greece
Greenland
Grenada
Guadeloupe
Guam
Guatemala
Guernsey
Guinea
Guinea-Bissau
Guyana
Haiti
Honduras
Hong Kong
Hungary
Iceland
India
Indonesia
Iran
Iraq
Ireland
Isle of Man
Israel
Italy
Jamaica
Japan
Jersey
Jordan
Kazakhstan
Kenya
Kiribati
Korea, North
Korea, South
Kuwait
Kyrgyzstan
Laos
Latvia
Lebanon
Lesotho
Liberia
Libya
Liechtenstein
Lithuania
Luxembourg
Macau
Macedonia
Madagascar
Malawi
Malaysia
Maldives
Mali
Malta
Marshall Islands
Martinique
Mauritania
Mauritius
Mayotte
Micronesia, Fed. St.
Moldova
Monaco
Mongolia
Montserrat
Morocco
Mozambique
Namibia
Nauru
Nepal
Netherlands
Netherlands Antilles
New Caledonia
New Zealand
Nicaragua
Niger
Nigeria
N. Mariana Islands
Norway
Oman
Pakistan
Palau
Panama
Papua New Guinea
Paraguay
Peru
Philippines
Poland
Portugal
Puerto Rico
Qatar
Reunion
Romania
Russia
Rwanda
Saint Helena
Saint Kitts & Nevis
Saint Lucia
St Pierre & Miquelon
Saint Vincent and the Grenadines
Samoa
San Marino
Sao Tome & Principe
Saudi Arabia
Senegal
Serbia
Seychelles
Sierra Leone
Singapore
Slovakia
Slovenia
Solomon Islands
Somalia
South Africa
Spain
Sri Lanka
Sudan
Suriname
Swaziland
Sweden
Switzerland
Syria
Taiwan
Tajikistan
Tanzania
Thailand
Togo
Tonga
Trinidad & Tobago
Tunisia
Turkey
Turkmenistan
Turks & Caicos Is
Tuvalu
Uganda
Ukraine
United Arab Emirates
United Kingdom
Uzbekistan
Vanuatu
Venezuela
Vietnam
Virgin Islands
Wallis and Futuna
West Bank
Western Sahara
Yemen
Zambia
Zimbabwe

## Update Page
Workbook updates:
v1.1 - 2/3/17: Updated kitchen exhaust criteria, spelling updates, added solar/renewable ready criteria.
v2.2 - 2/9/19: Updated for PHIUS+ 2018 Standards, Footnote (2)
v2.3 - 2/20/2020: Updated for EPA Energy Star MFNCP
v2.3 - 7-20-2021: Updates for current RESNET Standards and Energy Star MFNCP
v2.3 - 01-06-2022: Various wording and formatting updates
v2.3 - 09-26-2022: Alignment with Phius 2021. Electrification Readiness, Electric Vehcile Readiness Requirements, Re-organized Building Envelope, Heat+Cool, and Ventilation tabs, DHW temperature rise sampling table added.
v2.3.1 - 01-26-2023: Updates to the 'Ventilation'. Corrections made to 'pass' and 'fail' criteria for ventilation rates on individual rooms.
v2.3.2 - 04-17-2023: Updates to the 'Ventilation'. Corrections made to 'pass' and 'fail' criteria for Bedroom Pressure Difference inputs. Also updated 'pass' and 'fail' criteria for Heat + Cool for ducted systems.
v2.3.3 - 05-16-2023: Updated formulas for the preliminary blower door test on the 'Building Envelope' tab.
3.0.1 (3-4-14)
1) Ventilation - cells AB42, AC42, AB51, AC51 - added formula to sum the individual branch measurments for reference only
2) Ventilation - cell AF2 - added comment describing the "in balance" specification (+/-20% or 5cfm, whichever is greater)
3) DHW+Lights+Appliances - added item #3 for DHW model #, AHRI certificate and photo
4) Renewable Energy Ready - For item #1, updated the PV Watts hyperlink to the new PV Watts site…and added screen shot examples over to the right from PV Watts
5) Heating-Cooling: added note to item 1 "HVAC installer is required to be an accredited installer approved by Energy Star (for example, ACCA) if the heating or cooling system is a split air conditioner, unitary (packaged outside) air conditioner, air-source heat pump, water/ground source ("geothermal") heat pump up to 65,000Btu/hr with a ducted distribution system or a furnace up to 225,000Btu/hr with a ducted distribution system. All other permutations of equipment (e.g. boilers, mini-split / multi-split systems) and distribution systems are exempt."
3.0.2 (3-13-14)
1) Added more footnotes to Building Envelope 6.2 and 6.3
4.0.2 (5/18/17)
1) Totally revamped workbook to reflect newest ENERGY STAR, IAP and ZERH requirements
4.0 (8/10/17)
1) Requirement to supply fresh air to all bedrooms
2) Revised the previous 10' requirement for 'stretched string' distance between exhaust/suppy ports on exterior of building. Now, recommend 10', requirement is a minimum 5' separation but must follow manufacturer's recommendations.
4.1 (1/2019)
1) Updated entire workbook to coincide with PHIUS 2018 Standard; Energy Star V3.1, Rev09; Indoor AirPLUS v1, Rev04 & DOE ZERH Requirements
4.2 (7/2021)
1) Updated to add Electric Vehicle Readiness Checklist items
2) Updated to add Electrification Readiness Checklist items
3) Updated to Phius Certified Rater/Verifier from PHIUS+ Rater/Verifer
4) Updated to align with ENERGY STAR v3.1 (Rev11)
5) Aligned Ventilation tab limits with those outlined in the Guidebook in terms of tolerance and allowed difference in measured vs planned ventilation rates
4.2.1 (5/2023)
1) Revised Intro page layout
2) Revised Building Envelope section for blower door testing inputs
3) Added ability to include multiple ventilation systems and aligned tab limits with those outlined in the guidebook.
24.1.0 (7/2024)
Removed co-requisite requirements, where possible, to streamline the Workbook.
24.1 (8/2024)
1) Updated entire Workbook to coincide with Phius 2024 Standard; Energy Star MFNC v3.2, Indoor AirPLUS v1, REV04 & DOE ZERH Multifamily Version 2 Requirements

## Data entry Instr.
Template for Cover Sheet, row 52:
Data entry cells are in teal. Checkbox cells are in white. Calculation cells are in light gray. Do not change the calculation cells!
| Required input cells. | Select best option. | Calculations (do not change)
[Select]
[Select]