## No Rating
v25.1.0 ¦ 2025.06
Phius: System > Device > Water Storage : DHW
| Input Options |  |  |  | Required input cells. | Notes / Instructions / Units
| Specific total losses | Specific Total Thermal Storage Losses | 1.9624 | Btu/hr.F | Calculated Cells | Inputs for Energy model.
| Total Losses | Average Heat Released from Storage | 141.2931 | Btu/hr
Tank Storage Temperature
|  | Indoor Temperature | 68 | F
|  | Water Storage Temperature | 140 | F
|  | Delta T | 72 | F
Tank Insulation Data
|  | Insulation Performance | 6 | R/in
|  | Insulation Thickness | 2.5 | in
|  | Insulation R-Value | 15 | hr.ft2.F/Btu
|  | Insulation U-Value | 0.066667 | Btu/hr.ft2.F
Tank Size Data
|  | Diameter | 21 | in
|  | Height | 53.75 | in
|  | Surface Area | 4238.7939 | in2
|  | Surface Area | 29.4361 | ft2

## AHRI Rating
v25.1.0 ¦ 2025.06
Phius: System > Device > Water Storage : DHW
| Input Options |  |  |  | Required input cells. | Notes / Instructions / Units
| Specific total losses | Specific Total Thermal Storage Losses | 6.8965 | Btu/hr.F | Calculated Cells | Inputs for Energy model.
| Total Losses | Average Heat Released from Storage | 496.5513 | Btu/hr
Tank Storage Temperature
|  | Indoor Temperature | 68 | F
|  | Water Storage Temperature | 140 | F
|  | Delta T | 72 | F
Tank Data
|  | Storage Capacity | 119 | gal
|  | AHRI - Standby Loss | 0.5 | [F/hr]