## Updated to Match INP Hours
v25.1.1 - 2025.03
Phius - Snow Melt Energy Estimator |  | Required dropdown menu inputs | Constants & Instructions | Output for WUFI Passive or METr
|  | Required inputs | Calculation
Project / System Inputs
Phius Standard: | 2021
Location: | Minneapolis-St. Paul, MN
Area of Snow Melt: | 700 | ft2
Insulation under Snow Melt Area? | TRUE
Heating System: | Natural Gas
Heating System Efficiency Rating: | 1.5
| 95% | Thermal Efficiency (%)
Outputs for WUFI Passive or METr
Name: | Snow Melt Aux Energy
Device Type: | Other
Quantity: | 1
In Conditioned Space: | UNCHECKED
Energy Demand [W]: | 19095.9653
Period of Operation [kh/yr]: | 1
Climate Data Information
Snow-Free Area Ratio [Ar]: | 1 | Ar = 1 Rapid snow melt system that allows no accumulation.
Snow Melting Hours: | 199 | 2019 ASHRAE Handbook HVAC Applications Ch. 52 Table 1
Idling Hours: | 2513
Snow Melting [Btu/sf]: | 11678 | 2019 ASHRAE Handbook HVAC Applications Ch. 52 Table 3
Idling [Btu/sf]: | 127230
Back and edge losses: | 4% | Spitler et al. 2022. Insulated: 1-4% Uninsulated: 10-30%
Calculations
Total Energy at Slab | 97235600 | Btu/hr
Total Energy at Slab + Back and Edge Losses | 106617982.4561 | Btu/hr
| 31247.9433 | kWh

## Snow Melt Data (hidden)
- Select - |  | State | State | City | - Select - | Melting Time/yr | Idling Time / yr | Ar = 1 Melting | Ar = 1 Idling | 2% Min. Snow Temp.
TRUE |  | NY | New York | Albany | Albany, NY | 156 | 1883 | 10132 | 109230 | 9.3
FALSE |  | NM | New Mexico | Albuquerque | Albuquerque, NM | 44 | 954 | 2455 | 38504 | 16.3
|  | TX | Texas | Amarillo | Amarillo, TX | 64 | 1212 | 5276 | 62557 | 6.8
- Select - |  | MD | Maryland | Baltimore | Baltimore, MD | 56 | 957 | 4961 | 69187 | 0.3
2018 | 2.8 | MT | Montana | Billings | Billings, MT | 225 | 1800 | 17299 | 116947 | -10.8
2021 | 1.8 | ND | North Dakota | Bismarck | Bismarck, ND | 158 | 2887 | 16295 | 207888 | -8.8
2024 | 2 | ID | Idaho | Boise | Boise, ID | 85 | 1611 | 3543 | 74724 | 5.3
|  | MA | Massachusetts | Boston | Boston, MA | 112 | 1273 | 7694 | 77992 | 16.3
- Select - |  | NY | New York | Buffalo | Buffalo, NY | 292 | 1779 | 23929 | 105839 | 3.8
Electric Resistance |  | VT | Vermont | Bulington | Bulington, VT | 204 | 2215 | 13182 | 147122 | 4.3
Heat Pump |  | WY | Wyoming | Cheyenne | Cheyenne, WY | 224 | 2152 | 20061 | 126714 | -15.8
Natural Gas |  | IL | Illinois | Chicago | Chicago, IL | 124 | 1854 | 8501 | 116663 | 3.8
|  | OH | Ohio | Cleveland | Cleveland, OH | 188 | 1570 | 11419 | 86539 | 8.8
|  | CO | Colorado | Colorado Springs | Colorado Springs, CO | 159 | 1925 | 11137 | 97060 | -8.8
|  | OH | Ohio | Columbus | Columbus, OH | 92 | 1429 | 4581 | 71037 | 12.8
|  | IA | Iowa | Des Moines | Des Moines, IA | 127 | 1954 | 10884 | 128140 | -1.8
|  | MI | Michigan | Detroit | Detroit, MI | 153 | 1781 | 10199 | 104404 | 11.3
|  | MN | Minnesota | Duluth | Duluth, MN | 238 | 3206 | 20838 | 251218 | 0.3
|  | NV | Nevada | Ely | Ely, NV | 153 | 244 | 74321 | 141288 | 13.3
|  | OR | Oregon | Eugene | Eugene, OR | 18 | 481 | 841 | 17018 | 15.8
|  | AK | Alaska | Fairbanks | Fairbanks, AK | 288 | 4258 | 19803 | 343674 | -15.8
|  | MT | Montana | Great Falls | Great Falls, MT | 233 | 1907 | 3827 | 45132 | 16.3
|  | IN | Indiana | Indianapolis | Indianapolis, IN | 96 | 1473 | 19703 | 123801 | -15.8
|  | KY | Kentucky | Lexington | Lexington, KY | 50 | 1106 | 6558 | 80942 | 10.8
|  | WI | Wisconsin | Madison | Madison, WI | 161 | 2308 | 2696 | 54084 | 13.3
|  | TN | Tennessee | Memphis | Memphis, TN | 13 | 473 | 11404 | 149363 | 5.3
|  | WI | Wisconsin | Milwaukee | Milwaukee, WI | 161 | 1960 | 1010 | 21756 | 12.8
|  | MN | Minnesota | Minneapolis-St. Paul | Minneapolis-St. Paul, MN | 199 | 2513 | 11678 | 127230 | 7.3
|  | NY | New York | New York | New York, NY | 61 | 885 | 16532 | 183980 | 0.3
|  | OK | Oklahoma | Oklahoma City | Oklahoma City, OK | 35 | 686 | 4193 | 50680 | 18.3
|  | NE | Nebraska | Omaha | Omaha, NE | 94 | 1981 | 2955 | 40957 | 6.8
|  | IL | Illinois | Peoria | Peoria, IL | 91 | 1748 | 7425 | 124274 | -2.3
|  | PA | Pennsylvania | Philadelphia | Philadelphia, PA | 56 | 992 | 6544 | 104380 | 2.3
|  | PA | Pennsylvania | Pittsburgh | Pittsburgh, PA | 168 | 1514 | 3758 | 50494 | 18.3
|  | ME | Maine | Portland | Portland, ME | 157 | 1996 | 13318 | 115248 | 9.3
|  | OR | Oregon | Portland | Portland, OR | 15 | 329 | 10029 | 79312 | 7.3
|  | SD | South Dakota | Rapid City | Rapid City, SD | 177 | 2154 | 623 | 13399 | 21.8
|  | NV | Nevada | Reno | Reno, NV | 63 | 1436 | 16889 | 137523 | -4.8
|  | UT | Utah | Salt Lake City | Salt Lake City, UT | 142 | 1578 | 2293 | 54713 | 16.3
|  | MI | Michigan | Sault Ste. Marie | Sault Ste. Marie, MI | 425 | 2731 | 5263 | 70254 | 16.3
|  | WA | Washington | Seattle | Seattle, WA | 27 | 260 | 34249 | 176517 | -0.3
|  | WA | Washington | Spokane | Spokane, WA | 144 | 1832 | 1212 | 10482 | 17.8
|  | MO | Missouri | Springfield | Springfield, MO | 58 | 1108 | 6909 | 81000 | 10.8
|  | MO | Missouri | St. Louis | St. Louis, MO | 62 | 1150 | 4401 | 57165 | 6.8
|  | KS | Kansas | Topeka | Topeka, KS | 61 | 1409 | 4516 | 64668 | 6.8
|  | KS | Kansas | Wichita | Wichita, KS | 60 | 1223 | 4507 | 75598 | -1.8