## Aegis A (250, 350, 500)
v26.1.0 - 2026.03
Phius - Lync by WATTS Aegis A CO2: HPWH COP Estimator
Climate Data | [9 empty] | Required input cells.
Type of Phius Climate Data | Country | State | Phius Climate Location | [6 empty] | Required dropdown menu inputs.
Select | Select | Select | Select
Outputs for Energy Model (WUFI Passive or METr) | [9 empty] | Constants & Instructions
Aegis Model Number: |  | Select | Select water heater model. | [6 empty] | Output for WUFI Passive or METr
Tank Model Number: |  | Select | Select tank model.
Leaving Water Temperature (°F): |  | Select | Round up to the nearest leaving water tempature.
Heat Exchanger Efficiency (%): |  | 85% | If a heat exchanger is used, input the efficiency from the datasheet or use a default of 85%. If no heat exchanger is used, input 100%.
Annual Heating Coefficient of Performance (COP): |  | 0 | Under Systems, input a Heat Pump device and check the box for DHW. Within that Heat Pump device, set the Type to Heat Pump. Input the values calculated to the left into WUFI Passive. Water storage must be modeled as a separate device.
Total System Performance Ratio of Heat Generator: |  | -
Input Options: |  | Total Losses | Under Systems, input a Water Storage device and check the box for DHW. Within that Water Storage device, set the Input options to Total losses. Input the values calculated to the left.
Storage Capacity [gal]: |  | -
Within Thermal Envelope: |  | TRUE
Average Heat Released from storage [Btu/hr]: |  | -
Fill out Climate Data Section Above
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
Ambient Temp (°F) | - | - | - | - | - | - | - | - | - | - | - | -
Weighted COP @140 (°F) | - | - | - | - | - | - | - | - | - | - | - | -
Weighted COP @160 (°F) | - | - | - | - | - | - | - | - | - | - | - | -
Leaving Water Temperature (°F) | V3 | V2 | V1 | Intercept |  | Select |  |  |  | Calculated.
140 | - | - | - | - |  | 140 | 0 |  |  | Calculated from another sheet.
160 | - | - | - | - |  | 160 | 0
250 - Data
Outside Air Temp (°F) | COP @ 140F | COP @ 160F | 40-140 | 60-140 | 40-160 | 60-160
-4 | 1.9 | 1.9 | 2.1 | 1.9 | 2.1 | 1.9
5 | 2.1 | 2 | 2.3 | 2.1 | 2.2 | 2
14 | 2.3 | 2.2 | 2.5 | 2.3 | 2.4 | 2.2
23 | 2.5 | 2.5 | 2.8 | 2.5 | 2.7 | 2.5
32 | 2.8 | 2.7 | 3.1 | 2.8 | 3 | 2.7
41 | 3 | 2.9 | 3.4 | 3 | 3.2 | 2.9
45 | 3.2 | 3 | 3.5 | 3.2 | 3.3 | 3
50 | 3.3 | 3 | 3.6 | 3.3 | 3.6 | 3
59 | 3.6 | 3.2 | 4 | 3.6 | 3.6 | 3.2
68 | 3.8 | 3.3 | 4.3 | 3.8 | 3.8 | 3.3
77 | 4 | 3.4 | 4.5 | 4 | 3.9 | 3.4
95 | 4.1 | 3.5 |  | 4.1 |  | 3.5
350 - Data
Outside Air Temp (°F) | COP @ 140F | COP @ 160F | 40-140 | 60-140 | 40-160 | 60-160
-4 | 1.9 | 1.9 | 2 | 1.9 | 2 | 1.9
5 | 2 | 2 | 2.2 | 2 | 2.1 | 2
14 | 2.2 | 2 | 2.5 | 2.2 | 2 | 2.2
23 | 2.4 | 2.4 | 2.7 | 2.4 | 2.6 | 2.4
32 | 2.7 | 2.6 | 3 | 2.7 | 2.8 | 2.6
41 | 2.9 | 2.7 | 3.2 | 2.9 | 3 | 2.7
45 | 3 | 2.8 | 3.4 | 3 | 3.1 | 2.8
50 | 3.1 | 2.8 | 3.5 | 3.1 | 3.2 | 2.8
59 | 3.4 | 3 | 3.8 | 3.4 | 3.4 | 3
68 | 3.6 | 3.2 | 4.1 | 3.6 | 3.6 | 3.2
77 | 3.8 | 3.2 | 4.3 | 3.8 | 3.7 | 3.2
95 | 4 | 3.4 |  | 4 |  | 3.4
500 - Data
Outside Air Temp (°F) | COP @ 140F | COP @ 160F | 40-140 | 60-140 | 40-160 | 60-160
-4 | 1.9 | 2 | 2.1 | 1.9 | 2.1 | 2
5 | 2.1 | 2 | 2.2 | 2.1 | 2.1 | 2
14 | 2.2 | 2.2 | 2.4 | 2.2 | 2.3 | 2.2
23 | 2.4 | 2.3 | 2.6 | 2.4 | 2.5 | 2.3
32 | 2.6 | 2.5 | 2.8 | 2.6 | 2.7 | 2.5
41 | 2.8 | 2.7 | 3.1 | 2.8 | 2.9 | 2.7
45 | 2.9 | 2.7 | 3.2 | 2.9 | 3 | 2.7
50 | 3 | 2.8 | 3.3 | 3 | 3.1 | 2.8
59 | 3.2 | 2.9 | 3.6 | 3.2 | 3.3 | 2.9
68 | 3.4 | 3 | 3.8 | 3.4 | 3.4 | 3
77 | 3.6 | 3.2 | 4 | 3.6 | 3.8 | 3.2
95 | 3.8 | 3.2 |  | 3.8 |  | 3.2

## Custom Storage Tank (hidden)
Select | Tank Diameter | Tank Height | Tank Capacity | Tank R-Value | Surface Area (sf) | https://www.lyncbywatts.com/dfsmedia/0533dbba17714b1ab581ab07a4cbb521/650040-source/lync-custom-storage-tank-tds
125A-TR | 29.5 | 76 | 125 | 12.5 | 58.4058
150A-TR | 37x37 | 65 | 150 | 12.5 | 85.8194
175A-TR | 37x37 | 73 | 175 | 12.5 | 94.0417
215A-TR | 37x37 | 77 | 215 | 12.5 | 98.1528
250A-TR | 46 | 63 | 250 | 12.5 | 86.3065
300A-TR | 46 | 75 | 300 | 12.5 | 98.3493
400A-TR | 46 | 87 | 400 | 12.5 | 110.3921
500A-TR | 56 | 78 | 500 | 12.5 | 129.5034
600A-TR | 56 | 90 | 600 | 12.5 | 144.1642
750A-TR | 67 | 83 | 750 | 12.5 | 170.2896
900A-TR | 67 | 95 | 900 | 12.5 | 187.8302
1000A-TR | 67 | 107 | 1000 | 12.5 | 205.3707
1250A-TR | 75 | 96 | 1250 | 12.5 | 218.4389
1500A-TR | 75 | 108 | 7500 | 12.5 | 238.0738
1750A-TR | 75 | 132 | 1750 | 12.5 | 277.3437
2000A-TR | 75 | 144 | 2000 | 12.5 | 296.9787
2500A-TR | 75 | 156 | 2500 | 12.5 | 316.6136
3000A-TR | 75 | 180 | 3000 | 12.5 | 355.8835

## Custom Climate Data
Passive House Planning
OFFICIAL CLIMATE DATA SET
METRIC:
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Heating Load |  | Cooling Load
Days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 | Weather 1 | Weather 2 | Radiation
ALGONA IA | Latitude: | 43.083 | Longitude ° East: | -94.267 | Altitude (m): | 372 | 0 |  | Daily temperature variation summer (K) | 10.5 | Radiation Data: | kWh/(m²*month) | Radiation: W/m² |  | W/m²
Ambient Temp (°C) | -8.1 | -6.2 | 6.1 | 9.3 | 13.1 | 20.7 | 24 | 21.8 | 15.5 | 11.6 | 1.7 | -2.9 | -15.8 | -12.3 | 25.9
North | 19 | 32 | 36 | 42 | 51 | 56 | 56 | 46 | 32 | 25 | 19 | 17 | 20 | 20 | 71
East | 27 | 56 | 83 | 106 | 91 | 93 | 98 | 95 | 71 | 57 | 36 | 30 | 32 | 32 | 149
South | 47 | 106 | 123 | 116 | 79 | 73 | 84 | 95 | 99 | 98 | 90 | 72 | 40 | 40 | 148
West | 33 | 62 | 80 | 100 | 94 | 94 | 108 | 100 | 77 | 56 | 43 | 30 | 28 | 28 | 156
Global | 33 | 70 | 115 | 166 | 158 | 165 | 182 | 162 | 117 | 85 | 54 | 35 | 32 | 32 | 285
Dewpoint | -11.4 | -13.3 | -1.3 | -0.5 | 6.8 | 14.2 | 17.8 | 16.2 | 11.1 | 4.4 | -5.7 | -4.9
Sky temperature | -23.1 | -24.3 | -9.5 | -8.4 | 0.9 | 9.1 | 13.4 | 11.4 | 5.7 | -1.5 | -13.5 | -14.3
US CUSTOMARY:
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Heating Load |  | Cooling Load
Days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 | Weather 1 | Weather 2 | Radiation
ALGONA IA | Latitude: | 43.083 | Longitude ° East: | -94.267 | Altitude (ft): | 1220.4724 | 0 |  | Daily temperature variation summer (F) | 18.9 | Radiation Data: | kBTU/(ft².month) | Radiation: BTU/hr.ft² |  | BTU/hr.ft²
Ambient Temp (°F) | 17.42 | 20.84 | 42.98 | 48.74 | 55.58 | 69.26 | 75.2 | 71.24 | 59.9 | 52.88 | 35.06 | 26.78 | 3.56 | 9.86 | 78.62
North | 6.023 | 10.144 | 11.4119 | 13.3139 | 16.1669 | 17.7519 | 17.7519 | 14.5819 | 10.144 | 7.925 | 6.023 | 5.389 | 6.34 | 6.34 | 22.5069
East | 8.559 | 17.7519 | 26.3109 | 33.6018 | 28.8469 | 29.4809 | 31.0659 | 30.1149 | 22.5069 | 18.0689 | 11.4119 | 9.51 | 10.144 | 10.144 | 47.2328
South | 14.8989 | 33.6018 | 38.9908 | 36.7718 | 25.0429 | 23.1409 | 26.6279 | 30.1149 | 31.3829 | 31.0659 | 28.5299 | 22.8239 | 12.6799 | 12.6799 | 46.9158
West | 10.461 | 19.6539 | 25.3599 | 31.6998 | 29.7979 | 29.7979 | 34.2358 | 31.6998 | 24.4089 | 17.7519 | 13.6309 | 9.51 | 8.876 | 8.876 | 49.4518
Global | 10.461 | 22.1899 | 36.4548 | 52.6217 | 50.0858 | 52.3048 | 57.6937 | 51.3538 | 37.0888 | 26.9449 | 17.1179 | 11.0949 | 10.144 | 10.144 | 90.3446
Dewpoint | 11.48 | 8.06 | 29.66 | 31.1 | 44.24 | 57.56 | 64.04 | 61.16 | 51.98 | 39.92 | 21.74 | 23.18
Sky temperature | -9.58 | -11.74 | 14.9 | 16.88 | 33.62 | 48.38 | 56.12 | 52.52 | 42.26 | 29.3 | 7.7 | 6.26
Note on H6: Altitude of Weather Station
Note on I6: Input of building site altitude only required if highly different from weather station altitude. For empty input no temperature correction is applied.
Note on H21: Altitude of Weather Station
Note on I21: Input of building site altitude only required if highly different from weather station altitude. For empty input no temperature correction is applied.

## Update Tracker
Version | Update | Date | Description
v26.1.0 | 1 | 2026-03-24 | Calculation line added to account for heat exchangers which are typically used in tandem with this system.
v26.1.0 | 2 | 2026-03-24 | Note added that if storage tanks are used with the system, they should be modeled and accounted for separately.

## Climate Data (hidden)
|  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
Current Location |  | 2: Temperature (F); 14: Dewpoint (F); 26: Relative Humidity
Select | Select | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
State | City_WUFIp Data Set | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
BC | ABBOTSFORD AP | 38.4 | 41.2 | 44.6 | 49.6 | 55.6 | 60.1 | 65.1 | 65.2 | 60.1 | 51.1 | 43.1 | 37.8 | 32.4 | 32.18 | 35.4 | 38.48 | 44.2 | 49.1 | 53.06 | 53.06 | 49.8 | 43.52 | 37.4 | 31.5
SD | ABERDEEN REGIONAL ARPT | 12.5 | 17.6 | 30 | 44.2 | 56.7 | 66.5 | 71.4 | 69.3 | 60.2 | 46.2 | 30.2 | 17.5 | 6.4 | 6.26 | 25.9 | 32.36 | 49.6 | 57.2 | 59.72 | 60.98 | 52.5 | 41 | 22.6 | 15.3
TX | ABILENE DYESS AFB | 44.7 | 49.3 | 56.8 | 65.2 | 74.3 | 82.2 | 84.4 | 83.6 | 75.6 | 66.2 | 54.5 | 46.6 | 26.6 | 25.16 | 27.5 | 37.76 | 56.3 | 64.22 | 64.4 | 61.16 | 53.8 | 44.24 | 35.1 | 30.9
TX | ABILENE REGIONAL AP [UT] | 45.8 | 49.6 | 57 | 65.3 | 73.3 | 80.4 | 83.3 | 83 | 75.7 | 66.1 | 54.7 | 46.3 | 24.4 | 29.84 | 39 | 45.32 | 58.1 | 60.62 | 61.7 | 62.78 | 57.4 | 47.66 | 38.1 | 27
VA | ABINGDON | 36 | 39.4 | 47.1 | 56.1 | 64.2 | 71.6 | 74.1 | 73.9 | 67.9 | 57.2 | 46.7 | 38.9 | 31.8 | 24.62 | 32.2 | 35.42 | 44.2 | 59.18 | 62.6 | 62.42 | 49.3 | 39.92 | 30.2 | 30.9
AK | ADAK NAS | 32.3 | 33.3 | 33.9 | 36.4 | 40.3 | 45.2 | 49.1 | 51.3 | 47.9 | 42.3 | 37.6 | 33.5 | 25.9 | 29.48 | 30.4 | 25.88 | 32.4 | 36.5 | 42.98 | 41.36 | 34.5 | 33.44 | 30.6 | 27.1
NY | ADIRONDACK RGNL | 13.9 | 15.7 | 25 | 39 | 50.8 | 59.7 | 63.6 | 62 | 55 | 43.7 | 33.1 | 20.8 | 12.7 | 12.92 | 22.5 | 25.88 | 41.2 | 53.06 | 54.68 | 56.48 | 47.5 | 33.98 | 25.7 | 14.5
BC | AGASSIZ CDA | 38 | 41.4 | 44.5 | 50.2 | 56.7 | 60.8 | 65.8 | 65.7 | 61.1 | 51.9 | 42.9 | 38.3 | 28.2 | 31.64 | 36.9 | 41.18 | 47.8 | 53.42 | 57.74 | 57.38 | 53.1 | 45.5 | 37.9 | 28.8
NE | AINSWORTH MUNICIPAL | 25.4 | 28.1 | 36.9 | 46.8 | 57.2 | 66.8 | 74.8 | 72.3 | 63.2 | 49.5 | 37.1 | 26.8 | 17.1 | 16.34 | 28.8 | 32.36 | 45.7 | 55.04 | 58.46 | 57.74 | 43.5 | 40.46 | 27.9 | 19.6
MN | AITKIN NDB(AWOS) | 10 | 14.8 | 27.1 | 40.9 | 52.9 | 62.3 | 67 | 64.5 | 56.3 | 44.4 | 29.7 | 16.5 | 5.2 | 3.02 | 17.1 | 32.9 | 38.7 | 51.62 | 61.52 | 57.92 | 48.9 | 42.08 | 23 | 16
OH | AKRON AKRON-CANTON REG AP | 27.1 | 29.2 | 38 | 49.9 | 59.8 | 68.7 | 72.3 | 70.8 | 63.5 | 52.3 | 41.4 | 31.8 | 15.4 | 18.5 | 27.7 | 38.66 | 50.2 | 57.74 | 61.7 | 60.62 | 54.3 | 39.2 | 32 | 21.9
CO | AKRON WASHINGTON CO AP | 29.3 | 31.5 | 40.2 | 47.3 | 57.5 | 67.9 | 74.3 | 72.4 | 63.7 | 50.6 | 38.2 | 29.2 | 14.7 | 20.12 | 24.6 | 31.28 | 40.1 | 54.32 | 57.2 | 51.8 | 44.1 | 26.78 | 26.1 | 17.1
CO | ALAMOSA SAN LUIS VALLEY RGNL | 16.8 | 23.7 | 34.6 | 42.4 | 51.7 | 60.3 | 64.9 | 62.9 | 55.5 | 43.7 | 29.8 | 17.8 | 5.2 | 10.58 | 16.3 | 18.68 | 28.2 | 34.7 | 44.42 | 43.7 | 37.2 | 21.92 | 16.5 | 10.9
NY | ALBANY COUNTY AP | 24.1 | 26.4 | 35.4 | 47.9 | 58.7 | 67.9 | 72.3 | 70.6 | 62.6 | 50.9 | 40.3 | 29.9 | 12.6 | 15.8 | 23.5 | 32.72 | 45.9 | 54.14 | 60.44 | 59.36 | 52.3 | 42.26 | 31.8 | 19.6
GA | ALBANY DOUGHERTY COUNTY AP | 50.5 | 53.5 | 59.7 | 66.4 | 74.6 | 80.3 | 82.4 | 81.8 | 77.7 | 68.1 | 58.3 | 52.1 | 46 | 46.76 | 43.5 | 55.4 | 59 | 69.08 | 71.6 | 70.16 | 66.2 | 64.04 | 48.7 | 37.8
MN | ALBERT LEA (AWOS) | 15.5 | 19.9 | 32.2 | 46.3 | 57.9 | 68.1 | 72.1 | 69.4 | 61.7 | 49.3 | 34.5 | 21.2 | 18.7 | 16.7 | 26.2 | 36.32 | 43 | 59.9 | 63.32 | 66.02 | 53.8 | 37.76 | 27.9 | 17.6
NM | ALBUQUERQUE INTL ARPT [ISIS] | 37.7 | 42.2 | 49.3 | 57 | 66.6 | 76.3 | 78.8 | 76.7 | 70.2 | 58.5 | 45.9 | 37.1 | 18.5 | 21.74 | 22.1 | 20.48 | 30 | 39.56 | 51.26 | 50.72 | 45.9 | 31.82 | 23.2 | 16
LA | ALEXANDRIA ESLER REGIONAL AP | 49.6 | 52.3 | 59.4 | 66.5 | 74.2 | 80 | 82.5 | 82.4 | 77 | 66.5 | 56.7 | 50.1 | 41.5 | 48.56 | 50.5 | 52.7 | 64.4 | 71.24 | 71.96 | 74.48 | 65.3 | 61.88 | 47.7 | 40.6
MN | ALEXANDRIA MUNICIPAL AP | 10.9 | 15.4 | 27.5 | 42.9 | 55.9 | 65.5 | 70.4 | 68.5 | 59.7 | 46 | 30.1 | 16.5 | 8.1 | 6.8 | 18 | 34.52 | 43.9 | 54.5 | 60.62 | 59.72 | 54.3 | 33.98 | 26.1 | -2.4
IA | ALGONA | 18.2 | 22.5 | 33.9 | 47.6 | 59.7 | 69.8 | 73.2 | 71 | 62.9 | 50.4 | 36.4 | 23.1 | 11.5 | 8.06 | 29.7 | 31.1 | 44.2 | 57.56 | 64.04 | 61.16 | 52 | 39.92 | 21.7 | 23.2
TX | ALICE INTL AP | 58.2 | 61.4 | 67.2 | 73.8 | 79.7 | 84.2 | 85.6 | 86.1 | 81.6 | 74.8 | 65.6 | 59.2 | 50.5 | 46.04 | 52.5 | 66.38 | 72 | 70.88 | 71.96 | 72.86 | 66 | 63.14 | 54.5 | 50.7
PA | ALLENTOWN LEHIGH VALLEY INTL | 29.7 | 31.6 | 40.1 | 51.1 | 60.9 | 70 | 74.4 | 72.5 | 65 | 53.7 | 43.3 | 34.1 | 15.3 | 19.4 | 26.8 | 35.24 | 48.9 | 55.76 | 63.32 | 60.98 | 52.5 | 39.56 | 32.7 | 25.5
NE | ALLIANCE MUNICIPAL | 25.6 | 27.3 | 36.9 | 44.5 | 54.6 | 65.7 | 73.8 | 71.3 | 60.9 | 46.5 | 34.5 | 24.8 | 12.2 | 10.58 | 26.8 | 32 | 40.3 | 49.28 | 54.86 | 54.32 | 47.1 | 33.44 | 21.4 | 13.5
GA | ALMA BACON COUNTY AP | 50.5 | 53 | 59.5 | 66.3 | 73.7 | 79.8 | 81.6 | 81.6 | 77.3 | 68 | 58.3 | 52.4 | 38.5 | 42.8 | 41.7 | 55.4 | 63 | 69.26 | 72.68 | 73.4 | 66.2 | 52.88 | 49.1 | 37.6
MI | ALPENA COUNTY REGIONAL AP | 20 | 20.7 | 29.2 | 41.4 | 52.9 | 63 | 67.4 | 66 | 58.2 | 47 | 36.2 | 26 | 13.5 | 13.1 | 24.4 | 31.82 | 39.2 | 48.74 | 55.76 | 57.38 | 53.2 | 37.22 | 25.7 | 19.4
PA | ALTOONA BLAIR CO ARPT | 28.3 | 30.2 | 38.6 | 50.2 | 59.5 | 67.9 | 71.6 | 69.9 | 62.8 | 52.3 | 42.1 | 32.4 | 19.9 | 20.84 | 33.1 | 37.58 | 46.4 | 55.94 | 63.5 | 59.18 | 55.2 | 44.78 | 34.9 | 21.4
CA | ALTURAS | 31.1 | 33.9 | 38.7 | 43.3 | 51.8 | 59.9 | 68.4 | 65.5 | 58.5 | 47.4 | 37.7 | 30.8 | 26.1 | 25.52 | 30.2 | 30.38 | 32 | 37.04 | 41.18 | 36.5 | 41.5 | 29.48 | 29.5 | 24.1
OK | ALTUS AFB | 40.6 | 45.7 | 53.7 | 61.5 | 71.7 | 80.9 | 84 | 83.2 | 75 | 63.4 | 51 | 41.3 | 27.7 | 33.26 | 37.4 | 34.34 | 58.8 | 60.8 | 64.94 | 59.9 | 54.7 | 44.42 | 34.5 | 28.2
TX | AMARILLO INTERNATIONAL AP [CANYON - UT] | 37.9 | 40.9 | 48.6 | 56.7 | 66.2 | 75.4 | 78.4 | 77.2 | 69.8 | 58.6 | 46.6 | 37.9 | 20.3 | 24.08 | 28 | 36.86 | 45.7 | 59.18 | 59.72 | 60.62 | 52 | 40.82 | 27.5 | 20.7
AK | AMBLER | -3 | 3.1 | 5.4 | 20.9 | 39.2 | 56.3 | 58.2 | 52.2 | 41.1 | 21.9 | 7 | 1.1 | -15.2 | -3.46 | 6.8 | 15.08 | 28 | 35.24 | 43.7 | 36.32 | 29.1 | 25.16 | 2.5 | -0.8
AK | ANAKTUVUK PASS | -8.4 | -6.2 | -4.1 | 10.5 | 31.6 | 50 | 52.7 | 45.6 | 34.2 | 12.7 | -0.7 | -7 | -14.8 | -11.56 | -4.9 | 7.88 | 27.9 | 33.98 | 37.94 | 29.12 | 30 | 15.8 | -0.4 | -7.1
AK | ANCHORAGE INTL AP | 17 | 20.8 | 25.7 | 37.3 | 48 | 55.6 | 59 | 57.1 | 49 | 35.6 | 22.8 | 18.7 | 10.9 | 11.48 | 13.5 | 25.88 | 36 | 43.88 | 48.74 | 47.3 | 42.6 | 26.6 | 16.5 | 15.1
AK | ANCHORAGE MERRILL FIELD | 15.9 | 20.1 | 25.8 | 38.6 | 49.7 | 57.5 | 60.6 | 58.2 | 49.6 | 35.8 | 22.2 | 17.7 | 23 | 15.26 | 20.7 | 26.24 | 32.2 | 41.9 | 48.74 | 50.36 | 35.2 | 30.02 | 30.2 | 20.1
AK | ANCHORAGE/ELMENDORF | 14.6 | 18.8 | 25.3 | 37.6 | 48.9 | 56.8 | 59.9 | 57.6 | 48.8 | 34.5 | 21.1 | 15.9 | 24.1 | 27.86 | 20.3 | 27.68 | 32.4 | 39.56 | 51.26 | 49.1 | 33.4 | 26.06 | 31.3 | 20.5
SC | ANDERSON COUNTY AP | 43.3 | 46.4 | 53.2 | 61.2 | 69.2 | 76.6 | 79.8 | 78.9 | 72.7 | 62 | 51.9 | 45.1 | 26.6 | 30.38 | 32.7 | 42.98 | 52.9 | 64.76 | 69.62 | 70.34 | 60.8 | 46.04 | 45.7 | 30.2
MD | ANDREWS AFB | 35 | 37.6 | 45.4 | 55.6 | 64.3 | 73 | 77.6 | 75.3 | 68.4 | 57.4 | 47.4 | 39 | 24.6 | 24.8 | 27.9 | 36.14 | 49.8 | 60.62 | 66.92 | 63.86 | 55.8 | 43.7 | 33.4 | 31.5
AK | ANIAK AIRPORT | 5 | 13.5 | 13.7 | 30.4 | 44.7 | 53.9 | 56.6 | 53.3 | 45.2 | 30.5 | 15.3 | 7.8 | 0.9 | 20.3 | 13.6 | 18.5 | 28 | 35.96 | 43.16 | 41 | 28.2 | 25.16 | 20.5 | 9.1
MI | ANN ARBOR MUNICIPAL | 23.2 | 24.8 | 35.3 | 48 | 57.8 | 66.9 | 70.6 | 69 | 61.2 | 49.8 | 39.5 | 28.6 | 14.9 | 15.62 | 30.6 | 37.94 | 43 | 58.46 | 62.06 | 62.24 | 52.7 | 42.8 | 37.9 | 26.8
AK | ANNETTE ISLAND AP | 36.9 | 37.4 | 38.6 | 43.7 | 49.8 | 55.2 | 58.1 | 58.8 | 53.8 | 46.9 | 40.3 | 37.2 | 30.7 | 32.9 | 29.1 | 36.32 | 41.5 | 46.4 | 50.54 | 51.62 | 49.8 | 42.62 | 36.7 | 32.7
AL | ANNISTON METROPOLITAN AP | 44.4 | 47.9 | 55 | 62.4 | 70.2 | 77.1 | 80 | 79.7 | 74 | 63.2 | 52.9 | 46.5 | 39.6 | 42.08 | 41.5 | 55.4 | 65.3 | 64.22 | 71.24 | 67.28 | 62.4 | 47.66 | 45.1 | 35.8
AK | ANVIK | 4.2 | 11.1 | 13 | 28.8 | 44.2 | 54.5 | 56.5 | 52.4 | 45 | 29.2 | 12.9 | 5.4 | -0.6 | 12.2 | 9.1 | 21.56 | 27.5 | 30.74 | 37.04 | 33.44 | 26.6 | 27.68 | 16.7 | 10.4
WI | APPLETON/OUTAGAMIE | 19.1 | 24.7 | 32.7 | 46.4 | 56.3 | 66.9 | 71.8 | 69.4 | 62.7 | 49.7 | 37 | 24.9 | 19.4 | 28.04 | 24.6 | 30.38 | 39.7 | 58.28 | 59.72 | 60.26 | 50.5 | 40.1 | 29.3 | 23.9
CA | ARCATA AIRPORT | 47.6 | 48 | 48.4 | 49.4 | 52.3 | 54.9 | 56.7 | 57.2 | 56.1 | 53.6 | 50.1 | 47.1 | 41.2 | 37.76 | 43.9 | 44.24 | 46.4 | 49.46 | 51.8 | 52.7 | 50.5 | 48.56 | 45.7 | 40.6
NC | ASHEVILLE REGIONAL ARPT | 38.1 | 40.9 | 47.3 | 55.9 | 63.5 | 70.5 | 73.7 | 72.8 | 66.7 | 56.5 | 46.9 | 40.3 | 25.7 | 28.76 | 32.9 | 42.8 | 53.6 | 62.96 | 63.68 | 65.84 | 60.1 | 47.12 | 35.6 | 25.7
CO | ASPEN PITKIN CO SAR | 20.4 | 23 | 32.2 | 40.3 | 48.9 | 58.2 | 64.8 | 61.8 | 54.7 | 43.2 | 31.2 | 20.7 | 14.9 | 13.28 | 21.9 | 22.1 | 22.6 | 33.26 | 43.52 | 35.06 | 32.7 | 20.3 | 18.1 | 12.6
OR | ASTORIA REGIONAL AIRPORT | 43.8 | 44.4 | 46.2 | 48.7 | 53.1 | 57.1 | 60.5 | 61.1 | 59 | 52.8 | 47.1 | 43.1 | 37.6 | 39.92 | 41.4 | 42.44 | 46.2 | 49.82 | 54.14 | 55.4 | 52.2 | 47.84 | 42.4 | 39
GA | ATHENS BEN EPPS AP | 44.1 | 47.3 | 54.2 | 61.8 | 69.7 | 76.9 | 80.1 | 79.1 | 73.1 | 62.7 | 52.8 | 45.9 | 26.2 | 35.6 | 38.1 | 47.48 | 56.7 | 65.66 | 67.46 | 69.98 | 63.5 | 50 | 45.1 | 32.9
GA | ATLANTA HARTSFIELD INTL AP | 44.5 | 48 | 54.9 | 62.6 | 70.5 | 77.3 | 80.1 | 79.5 | 73.9 | 63.6 | 53.5 | 46.4 | 26.6 | 29.66 | 38.8 | 47.84 | 56.7 | 61.7 | 67.64 | 69.26 | 62.2 | 51.44 | 39.6 | 32.5
IA | ATLANTIC | 22.8 | 27 | 38.3 | 50.5 | 61.8 | 71.7 | 75.5 | 72.4 | 64.1 | 51.9 | 38.1 | 26.1 | 19 | 12.02 | 27 | 42.26 | 52.9 | 61.34 | 66.2 | 66.74 | 54.1 | 43.7 | 26.8 | 16.3
NJ | ATLANTIC CITY INTL AP | 34.2 | 35.6 | 42.3 | 52 | 61.1 | 70.7 | 76.1 | 74.2 | 67.2 | 56.5 | 46.5 | 38.4 | 19.2 | 24.98 | 30.7 | 41 | 50.9 | 60.26 | 65.84 | 64.76 | 57 | 44.96 | 38.1 | 28.8
ME | AUBURN-LEWISTON | 19.6 | 22.6 | 31.8 | 43.3 | 53.6 | 63.3 | 68.3 | 66.7 | 59.1 | 47.3 | 37.1 | 26.8 | 17.1 | 10.58 | 25.3 | 28.04 | 37.2 | 47.66 | 57.2 | 51.98 | 47.1 | 35.24 | 26.8 | 18.7
AL | AUBURN-OPELIKA APT | 46.3 | 49.3 | 55.8 | 62.8 | 71.1 | 77.3 | 79.7 | 79.3 | 74.1 | 64.5 | 55 | 47.5 | 28.9 | 34.88 | 36.3 | 43.7 | 55 | 68.54 | 69.08 | 67.28 | 62.4 | 46.04 | 43 | 36.1
ME | AUGUSTA AIRPORT | 20.4 | 23.1 | 32.2 | 44.1 | 55 | 64.4 | 69.9 | 68.6 | 60.5 | 49.2 | 38.3 | 27.3 | 0.1 | 4.1 | 25.7 | 32.54 | 43 | 53.96 | 57.92 | 59.9 | 57 | 43.34 | 31.6 | 16.7
GA | AUGUSTA BUSH FIELD | 46.5 | 49.5 | 56.3 | 63.4 | 71.3 | 78.3 | 81.3 | 80.4 | 74.8 | 64.4 | 54.5 | 48 | 35.2 | 33.44 | 42.3 | 49.28 | 58.6 | 66.74 | 68.36 | 69.44 | 65.8 | 51.44 | 48 | 34.9
CO | AURORA BUCKLEY FIELD ANGB | 32.4 | 34.6 | 41.2 | 47.6 | 57.5 | 66.8 | 73.2 | 71.2 | 63.4 | 51.3 | 38.6 | 33 | 23.9 | 21.02 | 22.1 | 28.4 | 35.2 | 41.18 | 43.52 | 43.16 | 34.3 | 27.14 | 26.8 | 14.9
IL | AURORA MUNICIPAL | 22.5 | 25.1 | 37.6 | 49.4 | 60 | 69.3 | 72.7 | 70.4 | 63 | 51.3 | 39.5 | 27 | 16.9 | 20.3 | 32.7 | 42.62 | 48 | 58.82 | 61.16 | 62.6 | 57.4 | 38.66 | 34 | 9.7
OR | AURORA STATE | 41.6 | 43.8 | 47 | 50.9 | 57.1 | 62 | 68.7 | 68.8 | 64.1 | 54.1 | 46.2 | 40.8 | 37 | 35.96 | 43.2 | 41.18 | 43.9 | 50.36 | 53.42 | 56.3 | 47.1 | 47.66 | 44.4 | 37.6
TX | AUSTIN MUELLER MUNICIPAL AP [UT] | 51.2 | 55 | 61.1 | 68.7 | 76.1 | 82.2 | 84.1 | 84.9 | 79.2 | 70.1 | 59.5 | 52.1 | 41 | 42.08 | 50.2 | 61.34 | 64.8 | 69.98 | 70.88 | 70.34 | 62.6 | 64.76 | 52.9 | 42.6
MN | AUSTIN MUNI | 15.3 | 19.5 | 31.9 | 46 | 57.8 | 67.8 | 71.9 | 69.2 | 60.8 | 48.9 | 34.5 | 21.3 | 19.8 | 8.06 | 29.7 | 41.54 | 41 | 54.86 | 62.24 | 67.64 | 53.1 | 35.42 | 23.4 | 7.2
OR | BAKER MUNICIPAL AP | 26.9 | 31.4 | 38.9 | 44.1 | 52 | 58.5 | 66.9 | 65.9 | 57.8 | 45.3 | 34.2 | 26.7 | 24.3 | 21.38 | 25.5 | 29.66 | 32.5 | 44.06 | 47.48 | 45.86 | 41 | 32.72 | 23.4 | 26.1
CA | BAKERSFIELD MEADOWS FIELD | 48.9 | 53.3 | 58.2 | 62.6 | 70.7 | 77.7 | 84.1 | 82.7 | 77.8 | 67.5 | 55.9 | 48.5 | 39.7 | 40.46 | 40.5 | 42.62 | 43.7 | 48.2 | 55.76 | 55.58 | 52.9 | 48.2 | 40.6 | 41.5
BC | BALLENAS ISLAND | 42.3 | 42.6 | 45.2 | 49.1 | 55.3 | 60.2 | 64.8 | 64.9 | 60 | 52.4 | 45.8 | 43 | 34.7 | 33.8 | 36.1 | 39.2 | 44.6 | 49.28 | 53.78 | 53.78 | 50.2 | 44.42 | 38.8 | 34
MD | BALTIMORE BLT-WASHNGTN INT | 34.7 | 36.6 | 44.4 | 54.9 | 64 | 73.3 | 77.9 | 75.8 | 68.6 | 57.2 | 47 | 38.4 | 20.3 | 22.64 | 26.1 | 40.1 | 52.3 | 59.72 | 65.12 | 63.5 | 61.2 | 41.54 | 37 | 20.8
ME | BANGOR INTERNATIONAL AP | 18.5 | 21.1 | 30.9 | 43 | 54.3 | 63.8 | 69.3 | 67.9 | 59.6 | 48.3 | 37.3 | 26 | 10.9 | 8.24 | 21.7 | 29.84 | 38.5 | 50 | 61.16 | 58.64 | 48.2 | 37.04 | 26.4 | 18.9
ME | BAR HARBOR (AWOS) | 21.2 | 23.8 | 31.8 | 41.9 | 51.3 | 60.1 | 66.2 | 65.4 | 58.6 | 48.1 | 38.3 | 28.7 | 18.7 | 15.62 | 21.6 | 26.06 | 25.5 | 47.48 | 52.88 | 54.32 | 46.6 | 37.04 | 29.7 | 27.1
HI | BARBERS POINT NAS | 72.7 | 72.7 | 73.5 | 75 | 76.4 | 78.7 | 79.9 | 80.4 | 79.9 | 78.6 | 76.4 | 74.2 | 59.9 | 58.64 | 63.7 | 59.9 | 62.4 | 62.96 | 63.32 | 68.18 | 69.4 | 69.08 | 66.6 | 63.7
LA | BARKSDALE AFB | 46.9 | 51.4 | 57.7 | 64.7 | 72.8 | 80.2 | 82.7 | 82.7 | 76.5 | 65.7 | 55 | 49 | 34.2 | 37.04 | 36.3 | 48.92 | 67.5 | 70.34 | 71.24 | 69.62 | 60.6 | 51.98 | 44.4 | 41.4
MA | BARNSTABLE MUNI BOA | 30.7 | 32 | 37.6 | 46.1 | 55.5 | 64.7 | 71.5 | 70.2 | 63.4 | 53.3 | 44.5 | 36.2 | 28.2 | 19.4 | 32 | 38.48 | 45.1 | 56.48 | 62.96 | 63.68 | 54 | 50.18 | 37.4 | 27.9
AK | BARROW W POST-W ROGERS ARPT [NSA - ARM] | -13.2 | -13.7 | -11.9 | 3.5 | 22.2 | 35.8 | 41.1 | 39.6 | 33.3 | 19.9 | 3.7 | -7.5 | -15.7 | -20.02 | -15.3 | -6.52 | 17.4 | 30.38 | 35.42 | 35.42 | 27.9 | 13.64 | -9.9 | -13.7
OK | BARTLESVILLE-PHILLIPS FIELD | 36 | 39 | 50 | 59 | 68 | 76 | 81 | 80 | 72 | 60 | 48 | 38 | 26.1 | 25.16 | 33.1 | 51.8 | 60.3 | 66.74 | 63.86 | 60.26 | 52.7 | 46.22 | 32.2 | 22.3
AR | BATESVILLE (AWOS) | 39.4 | 42.8 | 51.1 | 60.7 | 68.9 | 77.1 | 80.7 | 80 | 72.1 | 61.4 | 50.4 | 41.5 | 33.6 | 26.6 | 29.5 | 39.92 | 53.1 | 65.12 | 65.66 | 61.16 | 63 | 46.22 | 35.6 | 32.9
LA | BATON ROUGE RYAN ARPT | 52.1 | 55.3 | 61.3 | 67.8 | 75.2 | 80.8 | 82.3 | 82.4 | 78.2 | 68.8 | 59.1 | 53.4 | 42.4 | 42.26 | 53.6 | 57.56 | 66 | 67.46 | 73.04 | 71.24 | 66.4 | 58.46 | 52.5 | 41.4
MI | BATTLE CREEK KELLOGG AP | 24 | 26 | 36.4 | 48.9 | 59.8 | 68.8 | 72.5 | 70.7 | 63.3 | 51.4 | 40.7 | 29.3 | 18 | 23.18 | 31.1 | 40.46 | 41 | 57.74 | 58.28 | 62.6 | 54.3 | 41.36 | 34.2 | 20.1
MN | BAUDETTE INTERNATIONAL AP | 5.6 | 11.3 | 23.3 | 39.6 | 51.8 | 62.1 | 67.2 | 65 | 56.1 | 42.9 | 26.8 | 11.5 | 9.7 | 10.4 | 18.5 | 30.2 | 43 | 53.96 | 55.4 | 56.84 | 47.8 | 33.26 | 23.4 | 14
CA | BEALE AFB | 47.5 | 51.7 | 55.4 | 60.1 | 66.8 | 73.3 | 78.5 | 77.4 | 74.3 | 64.8 | 54.6 | 46.9 | 36 | 40.1 | 43.5 | 42.98 | 47.8 | 46.94 | 53.78 | 54.86 | 52 | 42.98 | 37.2 | 39
NE | BEATRICE MUNICIPAL | 26 | 30.7 | 41.1 | 52.2 | 63.1 | 72.8 | 78 | 75.7 | 66.5 | 54.4 | 40.7 | 28.8 | 19.6 | 18.5 | 33.8 | 42.26 | 45.1 | 56.12 | 62.42 | 64.4 | 55.2 | 42.44 | 30.4 | 25.7
SC | BEAUFORT MCAS | 50.2 | 53 | 59 | 66.2 | 73.8 | 79.9 | 82.8 | 81.7 | 77.1 | 68.1 | 58.6 | 52.6 | 34.7 | 41 | 42.8 | 53.24 | 57.2 | 69.8 | 73.76 | 71.42 | 66 | 54.32 | 51.6 | 37.6
ON | BEAUSOLEIL | 17.5 | 18.7 | 27.7 | 41 | 53.1 | 63.8 | 68.7 | 67.6 | 60.9 | 48.2 | 37.4 | 26.3 | 12.9 | 13.28 | 20.3 | 31.1 | 42.6 | 54.5 | 58.64 | 58.64 | 52.9 | 41.54 | 32.5 | 19.2
WV | BECKLEY RALEIGH CO MEM AP | 32.3 | 34.8 | 42.2 | 53 | 60.3 | 67.6 | 70.7 | 69.8 | 63.5 | 53.5 | 43.6 | 35.4 | 27.5 | 26.6 | 33.1 | 41.18 | 47.8 | 59.9 | 64.22 | 62.96 | 55.6 | 40.82 | 32.2 | 17.6
IL | BELLEVILLE SCOTT AFB | 31.4 | 37.1 | 45.9 | 56.3 | 65.9 | 74.7 | 78.2 | 77 | 68.7 | 57.7 | 45.4 | 35.2 | 27 | 26.42 | 27 | 37.22 | 45.5 | 65.48 | 66.2 | 65.12 | 53.6 | 41.9 | 33.3 | 26.8
NE | BELLEVUE OFFUTT AFB | 23.9 | 29.7 | 40.5 | 51.9 | 63 | 72.5 | 77 | 75.1 | 66.3 | 54.1 | 39.5 | 27.8 | 14.5 | 30.92 | 31.3 | 36.14 | 46.8 | 64.58 | 63.68 | 63.5 | 52.5 | 39.38 | 27.5 | 24.8
WA | BELLINGHAM INTL AP | 39.7 | 41.4 | 44.6 | 48.9 | 54.4 | 58.9 | 63.1 | 63.2 | 58.3 | 50.5 | 43.7 | 39.1 | 34.9 | 32.72 | 30.7 | 42.08 | 45.7 | 50.72 | 53.78 | 54.32 | 50.5 | 42.44 | 37.4 | 36.9
NJ | BELMAR ASC | 32.6 | 34.1 | 41.3 | 51.1 | 60 | 70.1 | 75.3 | 73 | 66.7 | 55 | 46.4 | 37.3 | 16 | 22.28 | 24.1 | 33.98 | 45.7 | 54.86 | 61.34 | 60.44 | 53.4 | 41.18 | 34 | 24.1
MN | BEMIDJI MUNICIPAL | 7.9 | 12.5 | 25.3 | 39.8 | 52.4 | 62.7 | 67.1 | 65.5 | 56.3 | 43.4 | 27.6 | 13.8 | 1.6 | 10.4 | 3.9 | 30.2 | 42.3 | 48.38 | 56.48 | 55.94 | 46.8 | 32.54 | 22.6 | 5.4
MN | BENSON MUNI | 12.2 | 16.2 | 29.1 | 44.6 | 56.9 | 66.9 | 71.4 | 68.4 | 60.6 | 47.2 | 31.8 | 17.8 | 11.1 | 16.16 | 28.2 | 32.72 | 45.1 | 51.98 | 64.04 | 56.84 | 52.7 | 40.64 | 21 | 8.4
MI | BENTON HARBOR/ROSS | 26.4 | 28.6 | 36.5 | 47.4 | 57.2 | 66.5 | 70.9 | 69.1 | 62.4 | 51.9 | 41.4 | 31.3 | 22.5 | 24.98 | 32.9 | 39.74 | 43.3 | 57.38 | 64.22 | 64.94 | 52.9 | 45.86 | 31.1 | 14.9
AR | BENTONVILLE (AWOS) | 36.3 | 40.2 | 48.4 | 57.2 | 65.7 | 74.3 | 78.4 | 77.9 | 69.3 | 58.8 | 48.1 | 38.8 | 25.9 | 33.98 | 29.3 | 43.7 | 58.8 | 62.06 | 66.92 | 66.2 | 58.6 | 47.12 | 32.5 | 23.9
NH | BERLIN MUNICIPAL | 14.2 | 17.3 | 26.5 | 39.7 | 51.4 | 60.7 | 64.9 | 63.5 | 56.2 | 44.1 | 33.5 | 21.3 | 8.1 | 9.5 | 12.2 | 28.4 | 36.1 | 53.6 | 55.4 | 56.48 | 50.9 | 36.32 | 27.5 | 22.1
AK | BETHEL AIRPORT | 6.1 | 11.5 | 13.4 | 28 | 42.1 | 52.6 | 55.8 | 53.6 | 45.7 | 30.9 | 17.6 | 9.1 | 10.6 | 7.34 | 9.9 | 24.08 | 33.8 | 44.24 | 48.74 | 49.1 | 39.2 | 27.5 | 13.1 | 8.4
AK | BETTLES FIELD | -11.2 | -4.4 | 3.1 | 24.4 | 45 | 58.4 | 59.4 | 52.9 | 41.6 | 21 | -0.2 | -6.6 | -14.3 | -14.8 | -4.2 | 12.92 | 30.4 | 40.28 | 47.48 | 46.04 | 30.9 | 15.98 | -1.3 | -15.9
MA | BEVERLY MUNI | 26.9 | 29.3 | 36.4 | 46.9 | 55.9 | 65.4 | 71.3 | 70.1 | 63 | 51.9 | 42.8 | 33.2 | 4.6 | 5.54 | 29.1 | 35.78 | 45.5 | 55.22 | 58.28 | 62.24 | 50.4 | 39.56 | 33.6 | 24.3
AK | BIG DELTA ALLEN AAF | -0.4 | 6.3 | 14.4 | 33.3 | 47.8 | 58.1 | 60.1 | 55.6 | 44.5 | 26.1 | 7 | 2 | -3.3 | -3.46 | -0.4 | 16.34 | 35.4 | 46.58 | 44.96 | 37.94 | 34.3 | 17.24 | -4.7 | -2.4
AK | BIG RIVER LAKE | 22.5 | 25.6 | 26.5 | 35.8 | 45.2 | 49.7 | 53.9 | 54.1 | 49.2 | 40.1 | 28.7 | 25.4 | 18 | 13.1 | 21.6 | 31.82 | 33.3 | 46.58 | 50.54 | 50.18 | 35.6 | 19.58 | 14.5 | 20.7
MT | BILLINGS LOGAN INT ARPT | 27.1 | 30.2 | 37.9 | 45.7 | 55.1 | 64 | 73.1 | 71.7 | 61.7 | 48.3 | 36.3 | 27.2 | 9.1 | 13.82 | 23.4 | 30.38 | 38.7 | 43.7 | 46.04 | 44.96 | 39.6 | 27.14 | 19.9 | 16.3
NY | BINGHAMTON EDWIN A LINK FIELD | 23.3 | 25 | 33.1 | 45.3 | 56.3 | 65 | 68.9 | 67.5 | 59.9 | 49.2 | 38.6 | 28.5 | 14.9 | 13.28 | 24.1 | 31.82 | 45.3 | 56.3 | 57.56 | 55.94 | 49.6 | 40.46 | 31.5 | 20.3
AK | BIRCHWOOD | 14.5 | 19.7 | 23.9 | 37 | 47.6 | 55.5 | 58.4 | 55.9 | 48.1 | 34.6 | 21.1 | 15.9 | 11.1 | 24.98 | 21.2 | 28.04 | 32.4 | 39.38 | 47.66 | 41 | 34.3 | 23.72 | 27.9 | 19.8
AL | BIRMINGHAM MUNICIPAL AP | 44.6 | 48.3 | 55.4 | 63.1 | 70.9 | 77.8 | 80.8 | 80.6 | 74.8 | 64 | 53.7 | 46.8 | 31.8 | 32.72 | 39.6 | 50 | 57.6 | 67.82 | 71.42 | 68.54 | 63.3 | 50.72 | 46.8 | 33.4
CA | BISHOP AIRPORT | 39.3 | 42.1 | 48.6 | 54.3 | 62.9 | 71.5 | 77.7 | 75.3 | 68.1 | 56.9 | 45.4 | 37.8 | 18.5 | 29.66 | 10.4 | 18.86 | 27.3 | 31.82 | 38.12 | 39.2 | 31.3 | 28.4 | 20.8 | 26.6
ND | BISMARCK MUNICIPAL ARPT [ISIS] | 13.1 | 18.2 | 30 | 43.4 | 55.3 | 64.9 | 71 | 69.9 | 59.8 | 45.2 | 29.7 | 17.4 | 1.2 | 13.82 | 21.7 | 30.2 | 45.3 | 50.54 | 55.4 | 53.24 | 44.4 | 32.54 | 22.6 | 9.9
UT | BLANDING MUNI AP | 30 | 36 | 44 | 50 | 58 | 72 | 74 | 74 | 65 | 53 | 41 | 32 | 28.2 | 21.56 | 26.8 | 24.8 | 29.7 | 31.82 | 31.82 | 30.56 | 30.7 | 29.3 | 26.4 | 20.7
RI | BLOCK ISLAND STATE ARPT | 33.1 | 33.7 | 38.8 | 46.8 | 55.4 | 64.9 | 71.5 | 70.6 | 65.2 | 55.9 | 46.9 | 38.7 | 27.1 | 24.26 | 27.5 | 35.42 | 43.9 | 57.56 | 62.6 | 64.04 | 59.4 | 45.14 | 34 | 28.6
CA | BLUE CANYON AP | 40 | 38.5 | 41.2 | 44.3 | 52.6 | 60.9 | 69.6 | 68.7 | 64.5 | 54.7 | 44.7 | 38.6 | 23.4 | 21.2 | 31.1 | 28.4 | 32.9 | 38.84 | 40.64 | 40.82 | 50.7 | 29.12 | 28 | 19
WV | BLUEFIELD/MERCER CO [NREL] | 34.4 | 36.4 | 44.4 | 55.3 | 62.3 | 69.3 | 72.3 | 71.5 | 65.4 | 55.3 | 45.7 | 37 | 19.4 | 27.86 | 31.1 | 34.7 | 47.7 | 59.9 | 63.14 | 62.78 | 52.5 | 47.66 | 30.7 | 28.2
CA | BLYTHE RIVERSIDE CO ARPT | 55.7 | 59 | 65.4 | 71.9 | 80.8 | 88.8 | 94.7 | 94.1 | 87.9 | 75.3 | 63 | 54.1 | 24.3 | 32.18 | 35.2 | 31.28 | 37.9 | 39.2 | 49.46 | 59.9 | 54.1 | 42.26 | 28.2 | 18
ID | BOISE AIR TERMINAL [UO] | 31.9 | 37.1 | 44.7 | 50.5 | 59.1 | 67.1 | 77 | 75.4 | 66.4 | 52.9 | 40 | 31.8 | 24.1 | 28.04 | 27.1 | 34.34 | 38.5 | 39.02 | 42.62 | 39.38 | 38.5 | 31.28 | 28.6 | 26.1
IA | BOONE MUNI | 21.8 | 26.5 | 36.8 | 49.9 | 60.9 | 70.2 | 74.1 | 72.8 | 63.8 | 52.3 | 38.7 | 26.6 | 19.2 | 28.22 | 20.3 | 43.7 | 48.6 | 62.96 | 63.14 | 63.86 | 52.3 | 41 | 27.7 | 17.2
MA | BOSTON LOGAN INT ARPT | 30.2 | 32 | 38.7 | 48.8 | 58.1 | 68 | 73.8 | 72.4 | 65.3 | 54.9 | 45.1 | 36 | 13.8 | 17.42 | 24.6 | 35.06 | 47.1 | 54.14 | 60.62 | 60.98 | 53.2 | 41.72 | 33.4 | 23
KY | BOWLING GREEN WARREN CO AP | 36.6 | 40.4 | 48.4 | 58 | 66.6 | 74.8 | 78.3 | 77.3 | 70.3 | 58.7 | 47.8 | 39.3 | 23.5 | 32.4 | 30.4 | 46.6 | 58.1 | 66.4 | 66.6 | 67.1 | 64 | 53.4 | 35.2 | 32.2
MT | BOZEMAN GALLATIN FIELD | 21.7 | 24.9 | 34.5 | 42.4 | 51.3 | 58.6 | 67.6 | 65.8 | 56.6 | 43.7 | 30.3 | 20.6 | 16.3 | 12.74 | 26.1 | 30.92 | 37 | 44.42 | 48.02 | 40.46 | 32.2 | 29.84 | 20.8 | 18.3
PA | BRADFORD REGIONAL AP | 23 | 24.5 | 32.4 | 44.4 | 54.5 | 62.1 | 65.6 | 64.2 | 57.6 | 47.2 | 37.6 | 27.8 | 11.7 | 15.62 | 27.1 | 32 | 41 | 50.36 | 58.46 | 56.3 | 49.5 | 35.78 | 28.6 | 16.3
MN | BRAINERD/WIELAND | 11 | 16.4 | 28.2 | 43.2 | 55 | 64.7 | 70 | 67.4 | 59 | 46 | 30.8 | 16.5 | 7.5 | 5.54 | 24.3 | 34.7 | 42.3 | 53.42 | 59.36 | 57.2 | 51.3 | 37.58 | 20.7 | 7.2
WA | BREMERTON NATIONAL | 38.9 | 40.1 | 43.5 | 47.1 | 53.2 | 57.9 | 63.2 | 63.4 | 58.9 | 50 | 42.6 | 38.2 | 34.2 | 35.42 | 37.4 | 37.58 | 41.5 | 48.2 | 50.9 | 52.16 | 43.5 | 41.54 | 38.7 | 37.9
NE | BREWSTER FIELD ARPT | 28.2 | 30.4 | 40.4 | 50.2 | 61.1 | 71 | 76.3 | 73.5 | 65.1 | 52.6 | 40.7 | 29.4 | 16.9 | 20.3 | 28.4 | 39.02 | 47.3 | 54.32 | 63.14 | 61.52 | 54.1 | 36.32 | 24.6 | 20.3
CT | BRIDGEPORT SIKORSKY MEMORIAL | 30.8 | 33.2 | 39.8 | 49.7 | 59.3 | 68.9 | 74.6 | 73.7 | 67 | 55.7 | 45.7 | 36.6 | 15.4 | 22.1 | 24.4 | 37.04 | 46.4 | 56.66 | 62.96 | 61.88 | 58.8 | 44.78 | 36.5 | 23.9
TN | BRISTOL TRI CITY AIRPORT | 36.6 | 39.9 | 47.3 | 56.3 | 64.3 | 72 | 75 | 74.1 | 67.9 | 56.7 | 46.4 | 39.1 | 26.8 | 24.08 | 31.1 | 39.92 | 52.3 | 62.6 | 64.76 | 64.04 | 57.9 | 46.22 | 36.7 | 25.5
NE | BROKEN BOW MUNI | 26.3 | 26.9 | 38.3 | 48.4 | 58.6 | 68.7 | 74.6 | 72 | 62.4 | 49.6 | 37.1 | 26.5 | 12.9 | 18.86 | 17.8 | 36.32 | 44.2 | 56.84 | 60.62 | 64.22 | 53.4 | 36.32 | 23 | 19.6
SD | BROOKINGS (AWOS) | 13.7 | 18.5 | 30 | 43.9 | 56 | 65.7 | 71 | 68.3 | 59.4 | 47 | 32.3 | 18.9 | 12.2 | 17.78 | 21.4 | 33.8 | 45.9 | 51.98 | 60.08 | 53.96 | 47.5 | 37.22 | 17.8 | 7.5
CO | BROOMFIELD/JEFFCO [BOULDER - SURFRAD] | 31.64 | 33.08 | 40.82 | 49.64 | 57.02 | 66.2 | 73.4 | 71.06 | 62.24 | 50.9 | 40.28 | 29.12 | 15.4 | 18.14 | 24.3 | 30.02 | 36.5 | 42.8 | 45.32 | 48.92 | 37.9 | 27.32 | 20.3 | 12.9
TX | BROWNSVILLE S PADRE ISL INTL | 62 | 65 | 69.6 | 75.1 | 80.4 | 84.2 | 84.8 | 85.3 | 81.8 | 76.4 | 69 | 62.9 | 52.7 | 52.34 | 57.7 | 67.82 | 70.7 | 74.84 | 74.48 | 73.22 | 73.4 | 66.02 | 60.3 | 53.2
GA | BRUNSWICK GOLDEN IS | 52.1 | 54.3 | 60.4 | 67.2 | 74.3 | 80.5 | 82.8 | 82.1 | 77.9 | 69.3 | 60 | 54 | 35.4 | 47.66 | 46.6 | 53.24 | 71.4 | 72.68 | 75.92 | 71.78 | 68.9 | 56.12 | 48.2 | 44.2
GA | BRUNSWICK MALCOLM MCKINNON AP | 52.1 | 54.7 | 60.2 | 66.6 | 74.4 | 79.9 | 82.2 | 81.4 | 78 | 69.9 | 60.7 | 54.5 | 46.6 | 52.34 | 54.7 | 64.4 | 67.1 | 69.8 | 73.04 | 73.04 | 71.2 | 64.22 | 54.7 | 51.3
UT | BRYCE CANYON AP | 21 | 24 | 32 | 39 | 47 | 57 | 64 | 61 | 54 | 43 | 32 | 21 | 9.1 | 13.64 | 19 | 20.3 | 28.8 | 25.7 | 34.34 | 40.1 | 28.6 | 28.76 | 16 | 14.4
NY | BUFFALO NIAGARA INTL AP | 25.8 | 26.4 | 34.3 | 46.1 | 57.5 | 67 | 71.2 | 70.1 | 62.8 | 51.7 | 41.1 | 31.2 | 16.3 | 17.42 | 27 | 35.42 | 42.4 | 52.7 | 60.98 | 56.66 | 52.2 | 41 | 33.4 | 22.5
CA | BURBANK-GLENDALE-PASADENA AP | 56.4 | 56.5 | 59.4 | 62.3 | 66.2 | 70.1 | 75.3 | 76.7 | 74.7 | 67.9 | 61 | 55.2 | 36.1 | 35.6 | 49.6 | 46.4 | 50.2 | 58.46 | 58.28 | 57.2 | 57.6 | 51.26 | 43.3 | 35.6
OH | BURKE LAKEFRONT | 29.8 | 31.3 | 38.3 | 50.2 | 61.3 | 70.6 | 74.6 | 73.4 | 66.9 | 55.7 | 46.3 | 34.9 | 15.3 | 23.72 | 27.1 | 40.46 | 44.6 | 61.88 | 64.22 | 61.52 | 55.8 | 43.34 | 40.1 | 17.4
ID | BURLEY MUNICIPAL ARPT | 28.8 | 33 | 41.3 | 47.1 | 55.4 | 63.2 | 72.2 | 70 | 61.3 | 49.6 | 37.8 | 28.9 | 22.5 | 19.94 | 26.2 | 30.2 | 33.4 | 42.62 | 51.08 | 46.76 | 39.6 | 33.62 | 27.9 | 26.2
VT | BURLINGTON INTERNATIONAL AP | 20.1 | 22 | 31.5 | 44.9 | 57 | 66.5 | 70.9 | 69.3 | 61.1 | 49.2 | 38.5 | 27.1 | 12 | 11.66 | 19.8 | 30.02 | 42.1 | 55.22 | 57.74 | 57.02 | 50.2 | 38.12 | 27 | 19.2
IA | BURLINGTON MUNICIPAL AP | 24.8 | 29.5 | 40.9 | 52.9 | 63.2 | 72.5 | 75.9 | 74.3 | 66.4 | 54.7 | 41.6 | 29.7 | 15.1 | 15.98 | 31.8 | 42.8 | 53.2 | 64.4 | 68.72 | 66.56 | 58.3 | 41.18 | 36.9 | 18.9
ON | BURLINGTON PIERS | 26.5 | 27.2 | 34.3 | 44.7 | 55.1 | 65.6 | 70.9 | 70.4 | 63.6 | 52.1 | 41.8 | 32.4 | 15.8 | 17.06 | 23.9 | 32.54 | 42.4 | 53.6 | 57.92 | 58.82 | 54.1 | 42.26 | 34 | 20.3
OR | BURNS MUNICIPAL ARPT [UO] | 26 | 29.3 | 37.6 | 43 | 51.3 | 58.3 | 67.7 | 65.4 | 57.2 | 44.9 | 33.8 | 25.2 | 19.9 | 22.1 | 27.9 | 25.52 | 30.2 | 40.64 | 37.76 | 40.64 | 34.9 | 30.74 | 25.3 | 23.5
PA | BUTLER CO (AWOS) | 27.4 | 28.7 | 37.9 | 49.6 | 58.3 | 67.4 | 70.9 | 69.4 | 62.1 | 51.3 | 41.4 | 32.2 | 21.9 | 23.18 | 25.2 | 33.26 | 43.2 | 57.02 | 62.24 | 58.64 | 48.7 | 38.84 | 28 | 23.5
MT | BUTTE BERT MOONEY ARPT | 20.5 | 22.6 | 31.8 | 38.7 | 47.3 | 54.8 | 63.7 | 61.8 | 53 | 40.9 | 28.4 | 18.8 | 12.7 | 13.82 | 19.9 | 25.34 | 29.7 | 36.86 | 41.18 | 42.8 | 34.3 | 28.22 | 17.8 | 14.5
MI | CADILLAC WEXFORD CO AP | 19.4 | 20.6 | 29.5 | 42.1 | 53.5 | 63.4 | 67.2 | 65.3 | 57.8 | 46.6 | 35.3 | 25 | 12.6 | 26.42 | 15.4 | 28.58 | 39.2 | 54.5 | 55.76 | 54.68 | 53.2 | 36.5 | 33.8 | 20.7
IL | CAHOKIA/ST. LOUIS | 32.5 | 35.8 | 46.1 | 57.2 | 66.6 | 74.5 | 78.3 | 77 | 68.6 | 57.5 | 46.1 | 35.4 | 27.5 | 29.12 | 37.2 | 47.12 | 46.9 | 60.98 | 69.26 | 69.08 | 63.1 | 46.76 | 39.4 | 24.3
AL | CAIRNS FIELD FORT RUCKER | 50.3 | 53.4 | 59.4 | 65.7 | 73.8 | 79.5 | 81.4 | 80.4 | 76.7 | 67.4 | 57.7 | 52.4 | 35.4 | 41.36 | 42.8 | 47.3 | 68.9 | 68.9 | 73.76 | 70.52 | 66.6 | 48.92 | 45.7 | 39.6
ID | CALDWELL (AWOS) | 30.7 | 35.9 | 43.9 | 49.4 | 58.2 | 65.5 | 74.3 | 72 | 63 | 50.6 | 38.5 | 31 | 28.9 | 25.34 | 27.7 | 33.08 | 34.7 | 43.88 | 45.32 | 40.64 | 37.6 | 36.86 | 28.6 | 20.8
NJ | CALDWELL/ESSEX CO. | 29.8 | 32.1 | 40.8 | 51.8 | 61.3 | 70.4 | 75.3 | 73.5 | 66.2 | 54.5 | 44.9 | 34.9 | 16.5 | 20.84 | 28.6 | 37.4 | 45 | 57.02 | 58.64 | 60.8 | 58.1 | 44.24 | 33.6 | 29.5
AB | CALGARY INT AP | 18.9 | 22.3 | 28.4 | 39.5 | 49 | 55.9 | 61.9 | 60.7 | 53.1 | 41.1 | 28 | 20 | 9.1 | 10.76 | 15.4 | 23.36 | 32.4 | 43.16 | 48.56 | 45.14 | 36.9 | 26.42 | 17.6 | 9.7
CA | CAMARILLO (AWOS) | 55.5 | 55.1 | 57 | 58.5 | 61.8 | 64.7 | 67.7 | 68.2 | 67.3 | 63.9 | 59.3 | 54.7 | 38.8 | 38.3 | 38.5 | 44.6 | 53.1 | 53.78 | 56.3 | 58.82 | 55 | 53.24 | 43.7 | 42.4
MN | CAMBRIDGE MUNI | 12.5 | 17.3 | 29.6 | 44.1 | 56.3 | 66 | 71.3 | 68.3 | 59.8 | 47 | 32.2 | 18.3 | -2.9 | 5.9 | 21.4 | 35.78 | 37.9 | 53.96 | 61.88 | 61.16 | 52.2 | 37.4 | 18.7 | 16.7
TX | CAMP MABRY | 52.2 | 55.6 | 61.7 | 69.1 | 76.5 | 82.1 | 84.7 | 85.2 | 79.9 | 70.9 | 60.8 | 52.8 | 37.2 | 42.44 | 44.2 | 57.74 | 65.7 | 69.44 | 71.24 | 67.64 | 65.5 | 56.48 | 48.7 | 37.2
CA | CAMP PENDLETON MCAS | 54.4 | 54.4 | 56.9 | 59.1 | 63.2 | 66.4 | 70.1 | 71.4 | 69.8 | 64.4 | 58.6 | 53.5 | 41.4 | 48.02 | 42.3 | 49.1 | 54.7 | 55.76 | 59.36 | 59.36 | 56.8 | 54.5 | 44.2 | 39.7
MO | CAPE GIRARDEAU MUNICIPAL AP | 34.7 | 39 | 47.8 | 58 | 67.4 | 75.8 | 78.8 | 77.3 | 69.1 | 58.2 | 46.9 | 37.5 | 24.1 | 28.58 | 39.7 | 40.46 | 50.4 | 67.64 | 67.28 | 68.9 | 56.1 | 48.92 | 43.5 | 27.7
NC | CAPE HATTERAS NWS BLDG | 46.2 | 47.4 | 51.9 | 59.7 | 67.3 | 76.2 | 79.2 | 78.9 | 74.9 | 66 | 57.2 | 49.4 | 35.6 | 39.74 | 45.1 | 51.62 | 59.5 | 68.36 | 73.4 | 70.88 | 68.4 | 53.96 | 49.6 | 37
NJ | CAPE MAY CO | 35.2 | 36.6 | 43 | 52 | 60.7 | 70.9 | 76.3 | 74.2 | 68 | 57.6 | 47.7 | 40 | 29.1 | 28.58 | 28.8 | 36.32 | 49.8 | 60.98 | 51.26 | 62.96 | 60.4 | 47.48 | 42.8 | 29.8
ME | CARIBOU MUNICIPAL ARPT | 11.2 | 13.9 | 25 | 38.5 | 51.5 | 61.2 | 66 | 64.2 | 55.7 | 44.1 | 32.2 | 19.6 | 6.4 | 7.7 | 10.9 | 26.24 | 34.9 | 49.1 | 56.3 | 55.76 | 46 | 34.7 | 23 | 9.9
NM | CARLSBAD CAVERN CITY AIR TERM | 44.9 | 49.2 | 56.2 | 64.7 | 73.8 | 81.9 | 82.4 | 81.3 | 74.3 | 64.3 | 52.1 | 44.3 | 26.1 | 35.78 | 20.7 | 39.38 | 39 | 57.56 | 55.76 | 58.1 | 54.9 | 35.24 | 28.4 | 27.1
CA | CARLSBAD/PALOMAR | 56.4 | 55.6 | 57.1 | 58.8 | 62.3 | 64.7 | 68.9 | 69.9 | 68.9 | 65.1 | 60.4 | 55.8 | 46 | 46.76 | 47.8 | 48.74 | 52.2 | 56.12 | 60.8 | 61.88 | 59.9 | 55.4 | 44.1 | 41.7
IA | CARROLL | 21.6 | 24.5 | 36.7 | 50 | 61.5 | 71.1 | 74.2 | 71.9 | 64 | 52.1 | 38.2 | 24.8 | 14 | 13.1 | 32 | 41.36 | 47.8 | 61.16 | 64.76 | 63.32 | 53.6 | 39.74 | 25.5 | 14.2
WY | CASPER NATRONA CO INTL AP | 25.9 | 27.6 | 36.2 | 42.8 | 52.6 | 62.6 | 71.2 | 69.7 | 59.4 | 46.1 | 34.4 | 25.3 | 11.3 | 14 | 21.4 | 23.36 | 33.6 | 39.74 | 44.6 | 39.74 | 32.4 | 27.86 | 19 | 13.6
UT | CEDAR CITY MUNICIPAL AP | 30.3 | 34.3 | 41.7 | 47.6 | 57.1 | 67.1 | 74.3 | 72.3 | 63.6 | 51 | 38.7 | 29.4 | 18.9 | 18.5 | 25.7 | 22.1 | 28.2 | 29.12 | 40.64 | 42.44 | 35.1 | 29.12 | 22.3 | 18.1
IA | CEDAR RAPIDS MUNICIPAL AP | 20.2 | 24.8 | 36.7 | 49.3 | 60.3 | 69.8 | 73 | 71.2 | 63.1 | 51.2 | 37.4 | 24.8 | 13.5 | 22.28 | 30.2 | 41 | 49.1 | 62.6 | 65.66 | 63.14 | 55.4 | 44.6 | 30.4 | 6.6
IL | CENTRAL ILLINOIS RG | 24.6 | 27.2 | 40.5 | 52.6 | 62.5 | 71.9 | 75 | 73.3 | 66.3 | 53.9 | 41.6 | 29.6 | 25.5 | 20.84 | 28.6 | 31.64 | 43.5 | 58.82 | 63.86 | 61.16 | 49.1 | 39.2 | 31.8 | 22.8
NE | CHADRON MUNI AP | 26 | 26 | 38 | 46 | 55 | 67 | 76 | 73 | 63 | 48 | 36 | 25 | 18.9 | 12.02 | 22.6 | 31.46 | 43.2 | 46.94 | 57.02 | 53.78 | 42.4 | 30.56 | 24.6 | 15.8
SD | CHAN GURNEY MUNI | 20.2 | 24.4 | 35.6 | 48 | 59.6 | 69.2 | 74.4 | 72.1 | 63.6 | 50.5 | 36.1 | 24 | 13.1 | 11.84 | 14.2 | 36.86 | 44.6 | 55.58 | 63.14 | 62.24 | 52.2 | 34.52 | 27.9 | 16
KS | CHANUTE MARTIN JOHNSON AP | 33.1 | 37.2 | 47 | 57.3 | 66.3 | 74.8 | 79.8 | 79.3 | 70.1 | 58.2 | 46.7 | 35.2 | 30.6 | 25.88 | 37.9 | 49.28 | 59.4 | 64.04 | 68.36 | 68.9 | 65.3 | 51.44 | 31.8 | 15.4
IA | CHARITON | 25.5 | 28.9 | 39.5 | 52.5 | 62.4 | 71.6 | 76.5 | 74 | 65.7 | 54 | 41.6 | 28.3 | 14 | 16.52 | 36.3 | 44.42 | 54 | 65.12 | 69.44 | 66.92 | 54.3 | 41.18 | 28 | 21.7
IA | CHARLES CITY | 18.6 | 23.2 | 34.1 | 48.2 | 59.5 | 69.2 | 72.3 | 70.2 | 62.4 | 50.5 | 35.7 | 22.6 | 19 | 12.92 | 34 | 42.44 | 46.9 | 55.22 | 64.58 | 69.26 | 59.9 | 43.88 | 28.4 | 21.6
SC | CHARLESTON INTL ARPT | 49.8 | 52.5 | 58.7 | 65.7 | 73.1 | 79.3 | 82.3 | 81.2 | 76.5 | 67.4 | 58.2 | 52 | 37.9 | 36.5 | 47.8 | 51.8 | 63.3 | 69.62 | 72.86 | 72.32 | 67.8 | 56.84 | 49.3 | 40.1
WV | CHARLESTON YEAGER ARPT | 35.2 | 38 | 45.9 | 56.8 | 64 | 71.9 | 75.1 | 74.1 | 67.3 | 56.4 | 46.4 | 38.3 | 19 | 25.16 | 32.4 | 39.02 | 51.8 | 62.24 | 68.18 | 65.48 | 58.3 | 45.14 | 36.5 | 25.9
NC | CHARLOTTE DOUGLAS INTL ARPT | 42.5 | 45.7 | 52.7 | 61.1 | 68.8 | 76.3 | 79.5 | 78.3 | 72.1 | 61.6 | 51.5 | 44.6 | 28.8 | 31.28 | 35.1 | 42.8 | 56.7 | 63.14 | 68.18 | 69.26 | 62.4 | 49.28 | 39.4 | 28.4
VA | CHARLOTTESVILLE FAA | 36.4 | 38.9 | 46.8 | 56.7 | 64.6 | 72.9 | 76.1 | 74.9 | 67.5 | 57 | 47.8 | 39.3 | 18.3 | 32.54 | 31.1 | 41.36 | 56.1 | 62.24 | 64.58 | 64.58 | 59.7 | 43.16 | 34.5 | 29.8
PE | CHARLOTTETOWN | 19.2 | 19.4 | 27.3 | 37.8 | 48.3 | 58.5 | 66.2 | 65.5 | 58.3 | 48 | 37.9 | 27.6 | 13.1 | 12.56 | 20.1 | 29.3 | 39.2 | 50.9 | 58.82 | 58.1 | 51.3 | 41.72 | 33.1 | 21.4
TN | CHATTANOOGA LOVELL FIELD AP | 41.8 | 45.2 | 52.8 | 61.4 | 69.2 | 76.8 | 79.9 | 79.6 | 73.1 | 61.8 | 50.9 | 43.8 | 31.1 | 32.54 | 39.7 | 45.32 | 56.5 | 67.46 | 68.36 | 68.9 | 63.7 | 51.8 | 41.9 | 30.2
NC | CHERRY POINT MCAS | 45.8 | 47.6 | 53.7 | 61.9 | 69.5 | 76.9 | 80.1 | 79 | 74.4 | 64.6 | 55.2 | 48.7 | 32.9 | 34.16 | 36.7 | 44.42 | 54 | 68.18 | 74.3 | 68.9 | 63 | 50.18 | 41.4 | 30
WY | CHEYENNE MUNICIPAL ARPT | 29.1 | 29.3 | 36.5 | 42.6 | 52.1 | 62.3 | 69.4 | 67.7 | 58.9 | 46.4 | 35.8 | 28.3 | 12 | 12.2 | 18.1 | 24.98 | 34 | 40.64 | 44.06 | 45.68 | 37.6 | 22.82 | 14 | 15.4
IL | CHICAGO MIDWAY AP | 25.9 | 29.5 | 39.3 | 50.5 | 61.1 | 71.1 | 75.7 | 74.1 | 66.5 | 54.6 | 41.9 | 30.6 | 12.6 | 19.76 | 29.8 | 42.62 | 44.4 | 57.02 | 60.8 | 62.6 | 58.6 | 43.88 | 33.6 | 21.2
IL | CHICAGO OHARE INTL AP | 24.6 | 28.2 | 38.2 | 49.2 | 59.6 | 69.5 | 74.2 | 72.7 | 64.9 | 53.1 | 40.6 | 29.3 | 15.1 | 17.24 | 29.3 | 39.2 | 45 | 55.4 | 65.66 | 61.88 | 55.2 | 41 | 32.7 | 18.3
IL | CHICAGO/WAUKEGAN | 23.3 | 25.3 | 35.7 | 46.6 | 56.1 | 66.2 | 71.5 | 70.5 | 62.9 | 51.5 | 40.2 | 27.7 | 19.4 | 20.12 | 23.2 | 38.3 | 42.1 | 57.38 | 66.92 | 63.32 | 52.3 | 39.74 | 34.5 | 17.2
MA | CHICOPEE FALLS WESTO | 25.2 | 26.7 | 36.6 | 48.1 | 58.2 | 67 | 72.5 | 69.9 | 61.9 | 51.4 | 40.8 | 31.3 | 23 | 20.48 | 25.3 | 30.2 | 41.2 | 57.56 | 59.36 | 58.46 | 52.7 | 40.46 | 31.8 | 29.3
TX | CHILDRESS MUNICIPAL AP | 41.9 | 45.2 | 53.6 | 62.5 | 71.5 | 79.8 | 83 | 82 | 74.1 | 63.3 | 51.6 | 42.6 | 26.6 | 34.34 | 36.1 | 45.68 | 57 | 59.54 | 62.96 | 64.22 | 56.8 | 42.26 | 41 | 26.8
CA | CHINA LAKE NAF | 46 | 50 | 58 | 64 | 72 | 82 | 88 | 86 | 79 | 66 | 54 | 44 | 18.1 | 25.7 | 28 | 25.34 | 34.2 | 30.2 | 36.5 | 40.28 | 29.5 | 24.44 | 25.5 | 23
CA | CHINO AIRPORT | 54.5 | 54.4 | 57.6 | 60.4 | 66.5 | 70.7 | 76.6 | 77 | 74.4 | 66.7 | 59.3 | 53.4 | 37 | 39.2 | 46.8 | 49.28 | 52.3 | 54.86 | 58.46 | 58.1 | 52.5 | 49.1 | 44.2 | 38.5
MI | CHIPPEWA CO INTL | 16.1 | 17.2 | 26 | 38.7 | 51.6 | 61.1 | 64.9 | 64.2 | 56.5 | 45 | 33.3 | 22.1 | 4.1 | 14.72 | 13.6 | 33.08 | 36.9 | 51.44 | 53.6 | 50.54 | 46.8 | 34.34 | 27.7 | 19.6
CA | CHULA VISTA BROWN FIELD NAAS | 55.9 | 54.9 | 57.2 | 59.2 | 63 | 65.6 | 69.5 | 70.8 | 70.1 | 65.6 | 60.3 | 55.3 | 42.8 | 44.6 | 48.2 | 51.08 | 51.1 | 55.4 | 59.54 | 60.62 | 56.7 | 49.28 | 43.2 | 37.8
OH | CINCINNATI MUNICIPAL AP LUNKI | 32.6 | 35.6 | 44.3 | 54.9 | 64 | 72.4 | 76 | 74.9 | 67.5 | 55.9 | 45 | 36.2 | 24.6 | 22.64 | 31.5 | 45.14 | 52.3 | 59.54 | 66.38 | 65.3 | 57.6 | 47.48 | 40.3 | 27.5
KY | CINCINNATI NORTHERN KY AP | 31.4 | 34.7 | 43.7 | 54.6 | 63.8 | 72.1 | 75.5 | 74.9 | 67.4 | 55.8 | 44.6 | 35.3 | 19.8 | 20.5 | 33.6 | 38.3 | 53.2 | 61.7 | 63.7 | 62.8 | 56.5 | 43.5 | 36.1 | 25.3
IA | CLARINDA | 24.5 | 28.1 | 40.4 | 51.8 | 62.7 | 71.9 | 75.8 | 74.1 | 65.2 | 53.5 | 39.9 | 28.6 | 14.7 | 27.86 | 30.2 | 44.24 | 57.7 | 64.58 | 69.44 | 69.44 | 61.7 | 42.8 | 30.6 | 19
NM | CLAYTON MUNICIPAL AIRPARK | 35.9 | 38.1 | 45.2 | 52.7 | 62.4 | 71.8 | 75.5 | 73.9 | 66.7 | 55.6 | 44.4 | 35.7 | 17.1 | 17.24 | 15.4 | 28.22 | 41 | 50 | 50.9 | 54.14 | 52.2 | 39.02 | 24.8 | 15.1
OH | CLEVELAND HOPKINS INTL AP | 28.2 | 30.1 | 38 | 49.6 | 59.8 | 69.2 | 73 | 71.6 | 64.5 | 53.7 | 43 | 33 | 19 | 18.14 | 28.6 | 37.4 | 45.7 | 59.18 | 61.7 | 61.34 | 55 | 42.44 | 33.4 | 20.5
IA | CLINTON MUNI (AWOS) | 20.9 | 25 | 36.9 | 49.1 | 60.7 | 69.9 | 73.2 | 70.9 | 63.3 | 51.3 | 38.8 | 26.4 | 14.7 | 25.7 | 26.8 | 37.94 | 44.8 | 58.82 | 63.5 | 67.82 | 57.2 | 37.4 | 26.8 | 8.8
OK | CLINTON-SHERMAN | 40 | 42.2 | 50.5 | 59.6 | 70.1 | 79 | 83.7 | 82.9 | 74.5 | 62.2 | 49.8 | 40.1 | 30 | 28.22 | 34.5 | 42.8 | 57.4 | 63.14 | 65.48 | 66.2 | 55.6 | 49.46 | 34.7 | 22.3
MN | CLOQUET (AWOS) | 10.6 | 15.1 | 26.4 | 39.1 | 50.3 | 59.6 | 66 | 64.3 | 55.8 | 43.8 | 29.4 | 16.2 | 9.5 | 13.28 | 25.2 | 32.18 | 36.7 | 55.76 | 61.34 | 60.98 | 50 | 35.42 | 14.4 | 11.7
NM | CLOVIS CANNON AFB | 38.9 | 43.5 | 49.9 | 57.8 | 66.6 | 75.8 | 77.8 | 76.8 | 70.3 | 59.3 | 47.6 | 40 | 22.5 | 27.14 | 28.8 | 34.34 | 36.5 | 39.02 | 51.8 | 57.74 | 40.8 | 40.28 | 30.7 | 25.2
NM | CLOVIS MUNI (AWOS) | 38.3 | 41.1 | 48.4 | 56.1 | 65.6 | 74.6 | 76.6 | 75.4 | 68.6 | 57.7 | 46.4 | 37.9 | 21 | 24.98 | 15.4 | 33.08 | 38.3 | 53.78 | 53.06 | 51.08 | 48.9 | 43.7 | 28 | 17.6
WY | CODY MUNI (AWOS) | 26.2 | 27.3 | 36.3 | 42.9 | 52.4 | 61 | 69.9 | 68.4 | 59.1 | 45.9 | 34.5 | 26.7 | 15.3 | 12.2 | 15.8 | 23.9 | 30.2 | 38.48 | 39.74 | 37.04 | 34.7 | 22.64 | 21.2 | 13.1
ID | COEUR D`ALENE(AWOS) | 29.3 | 31.5 | 38.4 | 45.2 | 53.7 | 59.5 | 68 | 67.3 | 59.3 | 46.6 | 36 | 28.6 | 22.8 | 24.98 | 29.3 | 34.52 | 37.9 | 46.58 | 49.1 | 43.7 | 42.1 | 36.32 | 31.1 | 24.4
AK | COLD BAY ARPT | 28.4 | 29.3 | 29.4 | 34.4 | 40.4 | 46.4 | 50.8 | 52.1 | 48 | 40.7 | 34.7 | 30.9 | 26.6 | 25.52 | 25.7 | 27.86 | 33.8 | 41.72 | 45.5 | 46.4 | 44.1 | 35.42 | 30.4 | 28.4
TX | COLLEGE STATION EASTERWOOD FL | 51.6 | 55.3 | 61.4 | 68.7 | 76.2 | 82.6 | 84.6 | 85.3 | 80.1 | 70.8 | 60.1 | 52.9 | 39.7 | 46.94 | 47.8 | 52.52 | 62.8 | 73.58 | 71.78 | 70.88 | 66 | 61.52 | 48 | 40.5
CO | COLORADO SPRINGS MUNI AP | 31.1 | 32.6 | 40.1 | 46.7 | 56.3 | 66.2 | 71.2 | 69.1 | 61.7 | 50 | 38.7 | 30.7 | 11.48 | 13.82 | 18.5 | 26.06 | 35.24 | 43.88 | 47.66 | 47.3 | 40.64 | 23.36 | 19.76 | 10.04
SC | COLUMBIA METRO ARPT | 46.2 | 49.3 | 56 | 64.2 | 72.1 | 79.1 | 82.2 | 80.9 | 75.1 | 64.4 | 54.2 | 47.7 | 27.7 | 37.04 | 44.6 | 47.48 | 59.9 | 65.66 | 67.28 | 69.62 | 65.7 | 54.5 | 47.3 | 33.3
MO | COLUMBIA REGIONAL AIRPORT | 30.2 | 34.9 | 44.9 | 55.3 | 64.4 | 73.2 | 77.3 | 76.4 | 67.6 | 56.5 | 44.6 | 33.8 | 17.8 | 21.74 | 35.8 | 43.34 | 51.3 | 60.8 | 64.76 | 66.2 | 56.3 | 45.5 | 31.1 | 23
MS | COLUMBUS AFB | 44.3 | 49.2 | 55.5 | 63.2 | 71.6 | 78.8 | 81.4 | 80.7 | 75.1 | 63.6 | 52.4 | 47.1 | 34 | 35.24 | 36.7 | 44.78 | 59.5 | 69.8 | 74.3 | 69.98 | 57.4 | 48.74 | 40.3 | 30.6
GA | COLUMBUS METROPOLITAN ARPT | 48 | 51.6 | 58.1 | 65.2 | 73.2 | 79.6 | 82.3 | 81.7 | 76.7 | 66.5 | 56.6 | 49.8 | 33.3 | 39.02 | 49.3 | 50.9 | 60.4 | 68.72 | 70.88 | 68 | 68.4 | 52.88 | 48.7 | 37.8
NE | COLUMBUS MUNI | 22.3 | 26.6 | 37.8 | 49.4 | 60.4 | 70.3 | 75.4 | 72.6 | 64.3 | 51.7 | 37.2 | 25.4 | 14 | 19.22 | 16.9 | 35.42 | 48.4 | 59.36 | 63.5 | 63.5 | 54.9 | 39.92 | 29.8 | 19.9
OH | COLUMBUS PORT COLUMBUS INTL A | 30 | 32.7 | 41.9 | 53.5 | 63.1 | 72 | 75.3 | 74.1 | 66.8 | 55.1 | 44 | 34.5 | 20.1 | 19.58 | 31.3 | 39.56 | 48.6 | 59.36 | 63.86 | 62.42 | 55.4 | 40.28 | 34.3 | 23.5
BC | COMOX AP | 38.8 | 39.5 | 42.6 | 47.7 | 54.2 | 59.6 | 64.7 | 64.4 | 58.4 | 49 | 42.4 | 38.5 | 35.8 | 34.34 | 36.1 | 38.84 | 44.2 | 49.1 | 53.06 | 53.42 | 49.8 | 44.42 | 39 | 35.2
CA | CONCORD CONCORD-BUCHANAN FIEL | 48.3 | 51.6 | 55.8 | 58.5 | 64.8 | 69.6 | 72.1 | 71.9 | 70.2 | 63.7 | 54.8 | 48.8 | 41.2 | 40.1 | 42.6 | 46.04 | 49.3 | 51.08 | 50.72 | 52.7 | 52.5 | 46.58 | 47.3 | 41.2
NH | CONCORD MUNICIPAL ARPT | 22 | 24.5 | 33.3 | 45.4 | 56 | 65.5 | 70.4 | 69 | 60.5 | 48.9 | 38.5 | 28.1 | 10.9 | 12.92 | 19.9 | 29.84 | 45 | 53.96 | 60.44 | 57.02 | 52.7 | 37.76 | 26.8 | 15.1
KS | CONCORDIA BLOSSER MUNI AP | 29 | 33.1 | 43.3 | 53.1 | 63.5 | 74 | 79 | 76.9 | 68.2 | 55.9 | 42.1 | 31.1 | 16.2 | 17.06 | 29.5 | 43.34 | 57.7 | 61.16 | 62.24 | 63.14 | 54 | 41.36 | 34.7 | 25.2
AB | COP UPPER | 20.5 | 23.1 | 28.7 | 39 | 48.6 | 54.8 | 61.6 | 60.3 | 52.8 | 41.8 | 29.2 | 22.7 | 9 | 10.4 | 15.1 | 22.28 | 30 | 40.64 | 45.5 | 42.8 | 35.4 | 25.34 | 16.5 | 10
AK | CORDOVA | 26 | 28.6 | 30.9 | 38.2 | 45.5 | 51.4 | 54.5 | 54 | 48.3 | 40.2 | 31.2 | 28.6 | 23.5 | 26.78 | 27.1 | 30.38 | 35.4 | 44.42 | 48.56 | 46.04 | 39.6 | 28.58 | 24.1 | 19.8
TX | CORPUS CHRISTI INTL ARPT [UT] | 58.1 | 61.5 | 66.7 | 73 | 78.5 | 82.9 | 84.1 | 85.1 | 81.4 | 74.8 | 65.9 | 59.4 | 45.9 | 48.92 | 56.8 | 63.86 | 68 | 74.84 | 74.3 | 73.94 | 71.1 | 64.4 | 59.2 | 47.1
TX | CORPUS CHRISTI NAS | 58.8 | 62 | 67.1 | 73.1 | 78.8 | 83.8 | 84.7 | 85.3 | 82.2 | 76.1 | 67.3 | 60.4 | 53.8 | 57.74 | 62.8 | 60.62 | 70.9 | 74.3 | 76.82 | 75.2 | 75.4 | 67.82 | 63.5 | 50.4
CO | CORTEZ/MONTEZUMA | 28.1 | 32.3 | 40.1 | 46.7 | 56.3 | 65.6 | 72.9 | 69.9 | 61.7 | 49 | 37.8 | 28.6 | 21.7 | 22.28 | 24.6 | 25.7 | 31.1 | 32 | 47.48 | 53.42 | 44.8 | 31.46 | 22.3 | 18
OR | CORVALLIS MUNI | 41.7 | 43.7 | 47.8 | 51.6 | 58.1 | 62.8 | 69.4 | 69 | 64 | 54.6 | 46.4 | 41.4 | 36.3 | 37.22 | 42.6 | 35.96 | 41.7 | 49.46 | 51.62 | 53.06 | 49.8 | 40.1 | 39.4 | 38.5
TX | COTULLA FAA AP | 55.7 | 59.6 | 66.5 | 74.1 | 80.2 | 85.7 | 85.6 | 87.2 | 81.5 | 74.3 | 64.4 | 56.2 | 48.4 | 51.8 | 57.6 | 50.54 | 66.4 | 69.08 | 72.32 | 69.62 | 67.5 | 58.46 | 48.2 | 36.9
IA | COUNCIL BLUFFS | 25.2 | 29.5 | 40.2 | 52.8 | 63.4 | 72.8 | 76 | 75.1 | 66.6 | 54.6 | 40.1 | 28.3 | 17.4 | 15.44 | 35.2 | 44.24 | 46.9 | 65.3 | 65.48 | 68 | 56.3 | 42.44 | 24.4 | 26.8
TX | COX FLD | 44 | 47.7 | 55.5 | 63.3 | 71.3 | 79.2 | 82.5 | 83.4 | 75.6 | 64.9 | 53.7 | 45.4 | 30.6 | 31.1 | 32.7 | 44.6 | 57.7 | 67.46 | 68.72 | 65.84 | 60.1 | 51.62 | 36.5 | 30.9
CO | CRAIG-MOFFAT | 15.8 | 21.4 | 33.2 | 42.1 | 51.2 | 59.8 | 67.1 | 65.2 | 56.2 | 43.9 | 30.3 | 18 | 3.9 | 15.8 | 15.6 | 29.66 | 26.8 | 37.4 | 40.82 | 48.02 | 40.6 | 24.8 | 18.3 | 14.5
BC | CRANBROOK AP | 21.3 | 26.2 | 35.2 | 43.4 | 52.1 | 58.3 | 66.4 | 65.1 | 55.9 | 42.2 | 29.7 | 20 | 16 | 17.78 | 23 | 27.86 | 35.4 | 42.08 | 44.96 | 43.34 | 39.2 | 30.92 | 23.5 | 14.7
MN | CRANE LAKE (AWOS) | 6.7 | 10.8 | 23.7 | 38 | 50.8 | 61.2 | 65.3 | 63.5 | 55.1 | 42.3 | 27.5 | 12.8 | -5.8 | 11.12 | 7.5 | 28.58 | 32.5 | 47.48 | 56.48 | 51.26 | 49.1 | 38.3 | 25.3 | 1.4
CA | CRESCENT CITY FAA AI | 48 | 48 | 48.5 | 49.5 | 52.6 | 54.5 | 56.4 | 57.4 | 56.2 | 53.7 | 50.7 | 47.9 | 38.7 | 39.74 | 41.2 | 42.26 | 46.2 | 50 | 53.06 | 54.86 | 51.8 | 47.84 | 45.1 | 41.4
IA | CRESTON | 23.9 | 27.3 | 38.5 | 51.2 | 62.1 | 70.6 | 75.3 | 73.4 | 64.3 | 52.5 | 39.6 | 26.2 | 12.2 | 22.28 | 33.3 | 45.32 | 51.6 | 63.32 | 66.02 | 67.82 | 53.4 | 43.34 | 29.7 | 20.1
FL | CRESTVIEW BOB SIKES AP | 50.1 | 52.6 | 58.7 | 65.7 | 73.1 | 79.9 | 80.9 | 80.9 | 76.8 | 67.3 | 57.3 | 51.6 | 44.2 | 47.66 | 44.4 | 54.5 | 61.3 | 69.98 | 72.5 | 69.62 | 71.6 | 65.66 | 54.7 | 44.8
MN | CROOKSTON MUNI FLD | 5.4 | 10.1 | 23.9 | 41.4 | 53.8 | 64.2 | 68.4 | 66.6 | 57.6 | 43.9 | 27.2 | 12.6 | 8.1 | 10.22 | 21.4 | 34.88 | 41 | 50.54 | 57.74 | 56.84 | 49.6 | 27.32 | 21.9 | 15.4
TN | CROSSVILLE MEMORIAL AP | 36.6 | 39.8 | 47.1 | 56.3 | 63.9 | 71 | 74.4 | 73.7 | 67.5 | 57 | 46.9 | 39.4 | 32.5 | 31.28 | 36.9 | 46.04 | 55 | 63.32 | 67.46 | 62.42 | 62.1 | 44.06 | 41.9 | 30.2
MT | CUT BANK MUNI AP | 22.2 | 23.4 | 31 | 40 | 49.4 | 56.8 | 65 | 63.5 | 54.8 | 42.8 | 30.7 | 22.9 | 14.9 | 13.1 | 17.4 | 25.88 | 32.4 | 38.3 | 43.16 | 41.72 | 33.8 | 28.76 | 20.7 | 15.6
CA | DAGGETT BARSTOW-DAGGETT AP | 49.2 | 52.7 | 59.3 | 65.3 | 74.7 | 83.2 | 89.5 | 88.3 | 81.3 | 69.1 | 56.3 | 47.7 | 26.4 | 26.42 | 31.3 | 33.8 | 38.3 | 42.08 | 45.14 | 46.4 | 43.5 | 40.1 | 27.3 | 29.7
TX | DALHART MUNICIPAL AP | 35.7 | 38.9 | 46.5 | 54.7 | 64.5 | 74.3 | 77.5 | 76.1 | 68.6 | 56.5 | 44.5 | 35.5 | 22.1 | 17.24 | 17.8 | 32.9 | 40.1 | 55.58 | 57.38 | 55.76 | 49.8 | 41 | 25.5 | 21.7
TX | DALLAS-FORT WORTH INTL AP | 47 | 51 | 58.1 | 66.1 | 74.4 | 82.2 | 85.8 | 86.1 | 78.7 | 68.1 | 56.8 | 48.2 | 30.7 | 35.6 | 45.9 | 54.32 | 62.4 | 64.76 | 70.7 | 70.34 | 62.8 | 47.48 | 45.3 | 28.6
TX | DALLAS-LOVE FIELD | 48 | 52 | 59 | 67 | 75 | 83 | 87 | 87 | 80 | 69 | 58 | 49 | 34.9 | 34.88 | 41.7 | 45.68 | 63.3 | 68 | 69.26 | 67.82 | 66.7 | 58.64 | 38.7 | 40.3
TX | DALLAS/ADDISON ARPT | 47.9 | 51.8 | 59 | 67 | 75.1 | 82.9 | 86.6 | 86.9 | 79.4 | 68.8 | 57.4 | 48.9 | 29.5 | 31.28 | 32.9 | 45.5 | 56.1 | 68.36 | 68.72 | 67.82 | 55.8 | 53.6 | 40.3 | 30.9
TX | DALLAS/REDBIRD ARPT | 48 | 50.7 | 58.2 | 66.3 | 74.1 | 81.7 | 85.4 | 86.4 | 78.7 | 68.1 | 57.4 | 48.4 | 35.8 | 31.82 | 48.7 | 57.56 | 64.6 | 67.1 | 68.54 | 64.4 | 63 | 55.22 | 38.8 | 35.1
CT | DANBURY MUNICIPAL | 26.8 | 29.4 | 37.6 | 48.9 | 58.1 | 67 | 71.7 | 70.2 | 63.4 | 51.9 | 42.2 | 32.6 | 16 | 15.08 | 31.5 | 35.42 | 43.3 | 59 | 61.52 | 59.9 | 54.7 | 42.98 | 36 | 27.7
VA | DANVILLE FAA AP | 39.6 | 42 | 49.4 | 58.7 | 66.6 | 74.6 | 78 | 77.2 | 70 | 59.3 | 49.1 | 41.7 | 25.2 | 34.34 | 35.4 | 45.32 | 55.2 | 64.58 | 66.92 | 69.08 | 61.2 | 49.28 | 32.9 | 34.7
NC | DARE CO RGNL | 43.9 | 45.5 | 51.2 | 60.2 | 68.1 | 76.6 | 80.6 | 79.7 | 74.6 | 65.5 | 55.7 | 48.4 | 31.5 | 30.38 | 35.2 | 42.8 | 53.2 | 65.48 | 74.48 | 68.72 | 62.2 | 57.2 | 49.6 | 46.2
AZ | DAVIS MONTHAN AFB | 53.1 | 55.2 | 60.8 | 67 | 76.1 | 85.2 | 86.9 | 85.6 | 82.2 | 71.9 | 60.8 | 52.4 | 30.6 | 43.34 | 35.4 | 24.62 | 23.2 | 32.36 | 49.82 | 51.98 | 52.5 | 34.88 | 34.7 | 21.4
VA | DAVISON AAF | 35.8 | 39.1 | 46 | 56.6 | 65 | 73.7 | 78.6 | 76.3 | 69.4 | 57.7 | 47 | 39.2 | 21.9 | 24.98 | 27 | 33.8 | 50.2 | 64.4 | 68.9 | 65.84 | 61.9 | 47.3 | 33.1 | 31.3
OH | DAYTON INTERNATIONAL AIRPORT | 28.3 | 31.5 | 40.9 | 52.4 | 62.3 | 71.2 | 74.4 | 73 | 65.7 | 54.4 | 42.9 | 32.8 | 17.2 | 19.22 | 30.6 | 38.48 | 47.3 | 58.82 | 66.02 | 63.5 | 57 | 40.64 | 32.2 | 24.3
FL | DAYTONA BEACH INTL AP | 59 | 61.1 | 64.7 | 69.7 | 75.5 | 79.9 | 81.5 | 81.6 | 79.8 | 74.1 | 66.5 | 61.4 | 47.3 | 50 | 55.9 | 58.1 | 65.8 | 71.24 | 72.32 | 73.22 | 71.2 | 62.42 | 58.5 | 52.7
AK | DEADHORSE | -15.9 | -16.6 | -14.8 | 3.2 | 23.4 | 40 | 47.3 | 43.8 | 34.5 | 17.8 | 0.1 | -10 | -15.7 | -27.76 | -23.1 | 5.18 | 25.3 | 35.6 | 36.86 | 35.24 | 32 | 21.56 | 5.9 | -7.4
IL | DECATUR | 27.8 | 31.8 | 42.1 | 53.4 | 63.6 | 72.4 | 75.9 | 74 | 66.8 | 55.2 | 42.8 | 32 | 23.7 | 28.76 | 33.8 | 47.12 | 55.4 | 62.96 | 62.24 | 70.88 | 55.4 | 43.34 | 30.6 | 21.6
IA | DECORAH | 19.9 | 23.1 | 35.4 | 48.8 | 59.5 | 69.1 | 72.9 | 69.8 | 62.3 | 50.9 | 37.6 | 23.8 | 13.1 | 22.82 | 33.8 | 40.46 | 50.7 | 59.9 | 63.32 | 66.02 | 55.2 | 37.94 | 27.5 | 18.5
AZ | DEER VALLEY/PHOENIX | 55.1 | 56.8 | 63 | 69.4 | 79.3 | 88.3 | 92.8 | 91.2 | 86.4 | 74.6 | 63 | 53.6 | 36.7 | 36.86 | 35.1 | 32.72 | 30.2 | 42.8 | 57.92 | 50 | 48.9 | 43.52 | 33.4 | 19.8
GA | DEKALB PEACHTREE | 42.9 | 46.4 | 53.6 | 61.9 | 69.9 | 77.2 | 79.7 | 79.5 | 73.2 | 62.6 | 52.6 | 45 | 26.4 | 33.98 | 35.2 | 44.24 | 58.5 | 65.12 | 69.62 | 68.72 | 65.1 | 44.6 | 36.9 | 31.1
TX | DEL RIO [UT] | 53.2 | 57.9 | 65.2 | 72.7 | 79.5 | 85.2 | 86.3 | 86.7 | 80.7 | 72.2 | 60.9 | 53.3 | 42.1 | 47.3 | 34.3 | 51.44 | 64.9 | 66.2 | 68 | 67.28 | 61.7 | 62.24 | 49.3 | 38.5
TX | DEL RIO LAUGHLIN AFB | 54 | 59.5 | 65.7 | 73.1 | 80.1 | 85.9 | 86.9 | 87.4 | 81.2 | 72.6 | 61.5 | 54.5 | 41.7 | 41.72 | 55.2 | 57.2 | 61.9 | 68.36 | 65.84 | 69.08 | 65.1 | 55.58 | 49.1 | 43.2
IN | DELAWARE CO JOHNSON | 27.1 | 29.3 | 41 | 53 | 62.9 | 71.4 | 73.7 | 71.8 | 65.1 | 54 | 43.1 | 31.4 | 20.1 | 23.18 | 26.6 | 40.82 | 48.7 | 56.48 | 63.68 | 65.48 | 56.7 | 45.32 | 36.5 | 27
NM | DEMING MUNI | 42.4 | 45.9 | 53.3 | 60.8 | 69.4 | 79.3 | 80.9 | 78.7 | 72.8 | 62.3 | 50.2 | 42.1 | 24.8 | 23 | 19.8 | 19.76 | 27.7 | 40.46 | 49.1 | 54.68 | 40.8 | 34.52 | 24.6 | 21.4
IA | DENISON | 22.8 | 26.1 | 37.4 | 50.2 | 60.5 | 71 | 75.2 | 72.3 | 64.6 | 51.7 | 38.5 | 25.1 | 17.8 | 14.36 | 27.3 | 38.48 | 49.5 | 58.82 | 67.82 | 62.06 | 59.9 | 43.88 | 27.5 | 19.9
CO | DENVER INTL AP | 31.6 | 32.3 | 41 | 47.3 | 57.1 | 67.5 | 74.9 | 72.8 | 63.8 | 51 | 40.1 | 30.9 | 13.3 | 15.98 | 17.8 | 27.5 | 38.8 | 43.88 | 49.1 | 46.94 | 37.4 | 34.34 | 19.4 | 15.6
CO | DENVER/CENTENNIAL [GOLDEN - NREL] | 31.7 | 32.8 | 40.4 | 46.3 | 56.2 | 66.6 | 72.7 | 70.7 | 62.4 | 50 | 39.5 | 31.2 | 16 | 17.96 | 25 | 29.3 | 32.5 | 46.4 | 47.84 | 46.4 | 39.4 | 32 | 22.8 | 13.8
IA | DES MOINES INTL AP | 22.7 | 27.6 | 39.4 | 51.5 | 62.2 | 71.8 | 76 | 74.2 | 65.8 | 53.6 | 39.5 | 27.3 | 9.7 | 13.82 | 26.2 | 34.52 | 45.1 | 58.46 | 66.02 | 65.3 | 53.8 | 34.52 | 30.2 | 16.7
MI | DETROIT CITY AIRPORT | 26.7 | 28.7 | 37.2 | 49 | 60 | 70.2 | 74.4 | 72.7 | 65 | 53.5 | 42 | 31.8 | 17.6 | 15.44 | 24.8 | 29.84 | 41.5 | 55.58 | 60.44 | 65.48 | 49.5 | 41.36 | 36 | 22.3
MN | DETROIT LAKES(AWOS) | 9.1 | 13.8 | 26.4 | 42.1 | 54.8 | 64.8 | 69.6 | 67.9 | 59.1 | 45.5 | 29.8 | 15.9 | 6.6 | 11.84 | 16.9 | 31.82 | 46.6 | 53.24 | 58.82 | 60.08 | 51.4 | 30.02 | 25.2 | 16
MI | DETROIT METROPOLITAN ARPT | 26 | 28.2 | 37.3 | 49.2 | 60 | 69.9 | 73.6 | 72.1 | 64.5 | 52.9 | 41.4 | 31.1 | 15.8 | 16.34 | 25.5 | 34.16 | 45.5 | 55.76 | 63.14 | 61.16 | 55.2 | 41.54 | 30.7 | 22.6
MI | DETROIT WILLOW RUN AP | 24.8 | 26.7 | 36.2 | 48.3 | 59.4 | 69 | 72.9 | 71 | 63.2 | 51.9 | 40.6 | 30.2 | 17.2 | 23.9 | 19.4 | 36.32 | 49.3 | 61.16 | 63.14 | 59.36 | 55.9 | 43.16 | 32.4 | 18.3
ND | DEVILS LAKE(AWOS) | 6.9 | 10.9 | 23.5 | 39.8 | 52.8 | 63 | 67.8 | 66.7 | 57.7 | 43.3 | 27.2 | 12.3 | -2.7 | 9.14 | 8.1 | 30.74 | 31.1 | 51.26 | 51.44 | 55.04 | 46.2 | 37.4 | 26.6 | 8.4
ND | DICKINSON MUNICIPAL AP | 16.5 | 20.5 | 30 | 41.8 | 52.8 | 61.9 | 69.2 | 68.7 | 58.6 | 44.2 | 30 | 19.3 | 5 | 13.28 | 19.9 | 32 | 41.2 | 42.62 | 58.28 | 53.24 | 41 | 31.28 | 17.1 | 5.7
NH | DILLANT HOPKINS | 21.9 | 24.4 | 33.4 | 44.9 | 55.6 | 65 | 69.4 | 67.8 | 60 | 48.2 | 38.2 | 28.2 | 7.7 | 15.08 | 20.7 | 32.36 | 40.5 | 52.34 | 55.58 | 58.1 | 54 | 38.12 | 31.8 | 16
AK | DILLINGHAM (AMOS) | 14.5 | 19.1 | 21.3 | 32.4 | 43.2 | 50.8 | 54.7 | 53.8 | 47.1 | 34.8 | 22.4 | 17.2 | 16.3 | 28.94 | 23.9 | 26.96 | 29.5 | 39.2 | 45.86 | 47.66 | 32.4 | 19.22 | 18.9 | 14
BC | DISCOVERY ISLAND | 44.1 | 44.6 | 46.1 | 49.5 | 53.5 | 56.9 | 59.3 | 59.7 | 58 | 52.5 | 47.5 | 44.2 | 36.3 | 35.96 | 38.5 | 40.46 | 45.1 | 49.1 | 52.7 | 53.24 | 50.7 | 45.86 | 41 | 36
KS | DODGE CITY REGIONAL AP | 32.5 | 36 | 44.7 | 53.9 | 64.5 | 74.6 | 79.6 | 77.9 | 69.2 | 56.7 | 43.3 | 33.3 | 15.8 | 23 | 30 | 40.1 | 49.1 | 58.64 | 60.44 | 60.62 | 53.8 | 39.2 | 27 | 20.1
AL | DOTHAN MUNICIPAL AP | 50.5 | 53.8 | 59.8 | 66.5 | 74.8 | 80.5 | 82 | 81.4 | 77.3 | 67.9 | 58.1 | 52.3 | 29.7 | 35.24 | 52.3 | 49.46 | 61 | 68.54 | 70.88 | 72.86 | 71.6 | 52.34 | 47.3 | 35.6
AZ | DOUGLAS BISBEE-DOUGLAS INTL A | 46.4 | 49.5 | 55 | 61.6 | 70.2 | 78.9 | 80.1 | 78.1 | 74.6 | 64.8 | 53.8 | 46.1 | 27 | 25.16 | 34.5 | 22.1 | 27.3 | 35.96 | 58.28 | 57.56 | 45.7 | 39.02 | 28.8 | 24.3
DE | DOVER AFB | 34.9 | 37 | 44.2 | 53.9 | 63.2 | 72.4 | 77.2 | 75.3 | 68.6 | 57.8 | 47.5 | 39.4 | 25.7 | 24.62 | 26.4 | 38.3 | 45.5 | 61.34 | 68.54 | 65.12 | 56.5 | 45.5 | 32.5 | 28.9
TX | DRAUGHON MILLER CEN | 48.8 | 52.1 | 58.9 | 67.1 | 74.5 | 81.3 | 83.9 | 84.4 | 78.1 | 68.6 | 57.5 | 49.8 | 34.5 | 34.16 | 35.2 | 45.68 | 66.7 | 69.8 | 69.26 | 67.1 | 58.6 | 48.74 | 45.5 | 38.5
PA | DUBOIS FAA AP | 25.1 | 26.7 | 35.4 | 47.3 | 56.9 | 65 | 68.8 | 67.4 | 60.3 | 49.8 | 39.4 | 29.6 | 20.1 | 16.16 | 28.6 | 30.92 | 42.8 | 54.5 | 53.78 | 60.26 | 48.4 | 39.38 | 30.6 | 22.8
IA | DUBUQUE REGIONAL AP | 19.2 | 23.7 | 35.5 | 47.8 | 58.8 | 68.4 | 71.7 | 70.1 | 62 | 50.1 | 36.7 | 24.1 | 10.9 | 15.26 | 27.5 | 33.8 | 46.4 | 58.28 | 62.6 | 62.24 | 55.8 | 37.4 | 21.6 | 15.3
MN | DULUTH INTERNATIONAL ARPT | 10.9 | 15.6 | 26.4 | 39.2 | 51.2 | 60.5 | 65.9 | 64.9 | 56.3 | 43.7 | 29.4 | 16.3 | 2.3 | 7.88 | 17.4 | 25.88 | 40.5 | 52.16 | 55.22 | 55.94 | 47.8 | 34.16 | 16.9 | 3.2
CO | DURANGO/LA PLATA CO | 24.8 | 29.2 | 38.1 | 45 | 53.8 | 63.5 | 70.4 | 67.7 | 59.9 | 47.8 | 36.5 | 26.4 | 19.4 | 20.3 | 15.6 | 21.38 | 29.1 | 33.62 | 48.56 | 48.92 | 46.8 | 27.14 | 21.6 | 10.8
AK | DUTCH HARBOR | 33.3 | 33.8 | 33.8 | 36.6 | 41.1 | 46.4 | 51.1 | 53 | 49.1 | 43 | 38.2 | 35.1 | 29.7 | 26.78 | 23.9 | 29.66 | 31.5 | 36.5 | 44.42 | 46.58 | 38.5 | 32.18 | 31.1 | 24.6
TN | DYERSBURG MUNICIPAL AP | 38.8 | 42.1 | 50.5 | 60.4 | 69.3 | 77.4 | 79.7 | 79.2 | 71.4 | 61 | 49.4 | 40.9 | 28.2 | 29.84 | 31.6 | 42.08 | 51.4 | 67.64 | 68.9 | 63.68 | 63.9 | 49.64 | 40.3 | 30.7
CO | EAGLE COUNTY AP | 22.8 | 27.1 | 36.1 | 42.9 | 52.6 | 60.3 | 66.7 | 64.8 | 56.5 | 45.4 | 31.1 | 21.4 | 9.9 | 13.82 | 21.6 | 24.62 | 28.4 | 31.82 | 47.12 | 41.18 | 33.1 | 26.06 | 22.1 | 12
WI | EAU CLAIRE COUNTY AP | 15.1 | 19.7 | 31.5 | 45.5 | 57.4 | 67.2 | 71.3 | 69.4 | 60.7 | 47.9 | 33.6 | 20.4 | 3.4 | 8.6 | 21.9 | 30.38 | 41.2 | 53.96 | 61.52 | 58.46 | 51.3 | 36.68 | 25 | 8.1
AB | EDMONTON AP | 9.8 | 14.1 | 22.7 | 38.5 | 49.9 | 57.1 | 61 | 59.2 | 51.1 | 38.4 | 22.4 | 11.7 | 4.5 | 6.62 | 13.5 | 24.62 | 32.5 | 44.42 | 51.44 | 48.74 | 39.4 | 27.68 | 17.8 | 5
AB | EDMONTON MUN AP | 13.3 | 18.3 | 26.5 | 40.8 | 52.3 | 59.7 | 64.3 | 62.5 | 53.9 | 41.1 | 25.4 | 15.1 | 5.5 | 8.6 | 13.6 | 23.54 | 32.7 | 44.96 | 51.8 | 49.1 | 40.3 | 28.04 | 18.1 | 5.4
AB | EDMONTON NAMAO | 12.9 | 15 | 24.7 | 38.8 | 50.4 | 57.7 | 62.1 | 60.3 | 52 | 39.3 | 24.1 | 12.8 | 5 | 7.7 | 13.3 | 23.54 | 32 | 44.78 | 52.16 | 49.46 | 40.5 | 28.4 | 18.3 | 5.5
CA | EDWARDS AFB | 45.1 | 48.3 | 54.5 | 60 | 68 | 76.4 | 83.1 | 82.4 | 75.6 | 63 | 52 | 43.6 | 29.5 | 30.02 | 32 | 31.1 | 34.9 | 38.66 | 41.9 | 37.22 | 33.4 | 32.36 | 30.9 | 28.6
AR | EL DORADO GOODWIN FIELD | 44.8 | 48.1 | 55.8 | 63.7 | 71.5 | 78.8 | 82 | 81.8 | 75 | 64.1 | 53.3 | 46.4 | 37.2 | 31.46 | 50.4 | 52.34 | 66.9 | 69.8 | 72.14 | 68.72 | 69.3 | 49.28 | 50.7 | 35.6
TX | EL PASO INTERNATIONAL AP [UT] | 46.3 | 50.9 | 57.9 | 66 | 75.1 | 83.5 | 83.3 | 81.7 | 76 | 66.1 | 53.7 | 45.7 | 26.6 | 23.72 | 22.1 | 27.14 | 36.7 | 42.62 | 58.28 | 53.6 | 52.2 | 45.14 | 29.3 | 23.4
NC | ELIZABETH CITY COAST GUARD AI [NREL] | 42.3 | 44.6 | 51 | 60.2 | 68.4 | 76.3 | 79.2 | 78.5 | 72.9 | 63.1 | 53.4 | 45.9 | 37.8 | 34.7 | 41.5 | 50.9 | 59 | 67.1 | 73.22 | 67.64 | 65.7 | 53.96 | 45.9 | 40.8
WV | ELKINS ELKINS-RANDOLPH CO ARP | 30.3 | 32.4 | 40.1 | 50.6 | 58.7 | 66.6 | 70.2 | 69.4 | 62.5 | 51.4 | 41.4 | 33.7 | 16.3 | 24.44 | 30.9 | 36.14 | 47.5 | 58.28 | 62.6 | 61.7 | 54.3 | 38.48 | 34.3 | 24.4
NV | ELKO MUNICIPAL ARPT | 25.7 | 30.1 | 38.9 | 44.8 | 53.3 | 61.8 | 70.7 | 68.4 | 59.6 | 46.7 | 34.9 | 26 | 15.4 | 23.36 | 24.6 | 28.94 | 33.6 | 33.08 | 33.26 | 32.54 | 28.8 | 25.7 | 21.4 | 17.2
SD | ELLSWORTH AFB | 25.3 | 28.3 | 35.9 | 44.6 | 54.8 | 64.9 | 72.1 | 72.6 | 62.7 | 48.1 | 35.1 | 25.5 | 13.5 | 24.08 | 23.2 | 28.76 | 36.5 | 48.02 | 50.72 | 49.46 | 37.8 | 29.84 | 27.3 | 17.2
NY | ELMIRA CORNING REGIONAL AP | 24.8 | 26.4 | 34.4 | 46.2 | 56.9 | 66 | 69.9 | 68.5 | 60.9 | 49.7 | 39.1 | 30 | 19.8 | 20.48 | 27.5 | 36.86 | 39.6 | 58.28 | 60.98 | 60.26 | 53.6 | 42.8 | 31.3 | 22.6
MN | ELY MUNI | 6.4 | 11.3 | 23.8 | 37.7 | 50.4 | 60.5 | 64.7 | 63 | 54.7 | 42.2 | 27.5 | 13.2 | -10.8 | 7.7 | 19 | 30.56 | 42.4 | 49.28 | 54.32 | 58.1 | 52.3 | 35.6 | 19 | 14.2
NV | ELY YELLAND FIELD | 26.2 | 29.1 | 36.9 | 42.5 | 50.8 | 60.1 | 68.5 | 66.6 | 57.8 | 46 | 34.5 | 25.9 | 13.3 | 19.22 | 22.3 | 19.58 | 28.4 | 27.32 | 37.58 | 36.14 | 30.4 | 26.96 | 15.6 | 11.1
AK | EMMONAK | 7.6 | 10.3 | 10.2 | 21.7 | 36.3 | 49.6 | 53 | 52.2 | 44.9 | 32 | 19.6 | 9.2 | 4.6 | 8.96 | 18.7 | 24.98 | 33.1 | 40.64 | 44.24 | 43.34 | 34.5 | 29.66 | 22.1 | 14.4
KS | EMPORIA MUNICIPAL AP | 31.5 | 35.3 | 45.2 | 55.9 | 65.5 | 74 | 79.3 | 78.3 | 69.1 | 57.5 | 45.2 | 33.7 | 16.5 | 24.62 | 22.5 | 45.5 | 57.6 | 65.48 | 67.1 | 65.84 | 59.7 | 43.88 | 31.5 | 13.8
LA | ENGLAND AFB | 50.1 | 53.3 | 59.9 | 67.1 | 75.1 | 80.9 | 82.5 | 82.9 | 77.8 | 67.5 | 57.5 | 51 | 43.3 | 38.12 | 54 | 57.56 | 63.3 | 67.28 | 73.4 | 67.28 | 64.8 | 60.98 | 51.1 | 41.4
BC | ENTRANCE ISLAND | 42.1 | 42.8 | 45.1 | 49.3 | 54.9 | 60 | 64.6 | 64.8 | 60 | 51.8 | 45.8 | 42.2 | 34.9 | 33.98 | 36.5 | 39.38 | 44.8 | 49.46 | 53.78 | 53.78 | 50.2 | 44.6 | 38.8 | 34.3
WA | EPHRATA AP FCWOS | 29.5 | 35.1 | 43.1 | 50.2 | 59.5 | 67.1 | 76.5 | 73.9 | 65.3 | 51.3 | 37.4 | 29.7 | 24.1 | 26.6 | 30.4 | 32.9 | 41 | 44.78 | 45.68 | 44.06 | 41 | 33.08 | 30.4 | 28.2
PA | ERIE INTERNATIONAL AP | 28.2 | 28.5 | 35.8 | 47.3 | 58 | 67.7 | 71.9 | 70.7 | 63.9 | 53.5 | 43.1 | 33.4 | 18.3 | 17.78 | 22.5 | 37.22 | 48.6 | 55.58 | 59.54 | 59.54 | 53.8 | 41.54 | 34.2 | 20.3
ON | ERIEAU | 25.9 | 26.4 | 32.7 | 43.4 | 54.3 | 65.4 | 70.6 | 70.5 | 64.3 | 53.3 | 42.3 | 32.2 | 17.1 | 18.86 | 25.9 | 34.52 | 45.1 | 57.2 | 62.06 | 62.6 | 56.3 | 44.24 | 36 | 21.4
MI | ESCANABA (AWOS) | 17.8 | 19 | 27.8 | 39.2 | 50.7 | 60.8 | 65.4 | 64.5 | 57 | 45.7 | 34.7 | 24 | 14.4 | 16.88 | 16.2 | 30.92 | 32.4 | 49.64 | 56.84 | 52.7 | 45.5 | 35.06 | 27.5 | 18.9
BC | ESQUIMALT HARBOUR | 41.6 | 42.3 | 44.4 | 48.1 | 52.9 | 56.9 | 60.3 | 60.1 | 56.6 | 50.3 | 44.9 | 41.4 | 36.5 | 36.14 | 38.8 | 40.82 | 45.5 | 49.46 | 52.7 | 53.42 | 51.1 | 46.4 | 41.4 | 36
IA | ESTHERVILLE MUNI | 15.9 | 20.3 | 32.7 | 47 | 58.7 | 68.1 | 72.3 | 69 | 61.7 | 49 | 34.6 | 20.8 | 7 | 10.22 | 17.2 | 38.3 | 48.4 | 56.84 | 62.24 | 61.34 | 53.1 | 35.42 | 24.3 | 2.7
OR | EUGENE MAHLON SWEET ARPT [UO] | 41.2 | 43.2 | 46.9 | 50.3 | 55.5 | 60.4 | 67.8 | 67.7 | 63.1 | 53.2 | 45.4 | 40.3 | 38.7 | 36.5 | 41 | 42.98 | 47.5 | 50.36 | 51.98 | 53.06 | 48.9 | 44.96 | 39 | 37.8
WY | EVANSTON-UINTA COUNTY AP-BURNS FIELD | 22 | 24 | 32 | 40 | 49 | 59 | 69 | 66 | 57 | 44 | 32 | 22 | 10.6 | 15.98 | 22.6 | 23.18 | 28.9 | 31.1 | 36.32 | 42.8 | 40.1 | 25.16 | 21.7 | 15.1
IN | EVANSVILLE REGIONAL AP | 33.7 | 37.4 | 46.5 | 57 | 66.4 | 75.1 | 78.1 | 77.1 | 69.5 | 58.1 | 46.4 | 37 | 24.6 | 24.44 | 37 | 43.16 | 54.3 | 63.86 | 65.84 | 68 | 56.5 | 45.32 | 39 | 27.5
MN | EVELETH MUNI (AWOS) | 8.7 | 13.5 | 25.7 | 39.4 | 51.4 | 61 | 65.9 | 63.7 | 55.1 | 43 | 28.2 | 14.8 | 2.3 | 12.38 | 13.6 | 28.76 | 32.9 | 53.6 | 58.64 | 55.76 | 47.5 | 36.5 | 20.5 | -1.7
IA | FAIR FIELD | 24.5 | 27.2 | 40.1 | 52.7 | 63 | 72.4 | 76.1 | 74 | 65.3 | 53.6 | 41.6 | 28.2 | 19.6 | 15.08 | 36.7 | 47.3 | 53.4 | 61.7 | 68.72 | 63.86 | 56.5 | 42.98 | 27.5 | 20.5
AK | FAIRBANKS INTL ARPT | -8.5 | -0.8 | 10.6 | 33.5 | 50 | 61 | 62.6 | 56.9 | 45.5 | 25.3 | 3.1 | -5.1 | -3.8 | -2.02 | 1.2 | 16.16 | 29.3 | 43.52 | 49.82 | 45.68 | 35.2 | 19.22 | -4.5 | -7.4
AK | FAIRBANKS/EIELSON A | -8.2 | -1.5 | 12.6 | 33.9 | 49.2 | 59.8 | 62 | 56.3 | 45 | 23 | 2.4 | -6.5 | 5 | 9.32 | 12.4 | 16.34 | 28.8 | 39.74 | 47.12 | 44.06 | 31.3 | 26.24 | 16 | -0.9
WA | FAIRCHILD AFB | 28.5 | 32.2 | 39.4 | 46 | 53.9 | 60.2 | 69.4 | 68.4 | 60.4 | 46.8 | 35.6 | 28.1 | 26.6 | 27.68 | 27.3 | 31.1 | 36.5 | 42.26 | 37.94 | 40.28 | 32.5 | 28.76 | 30.9 | 21.7
MN | FAIRMONT MUNI(AWOS) | 15.5 | 20.1 | 32.1 | 46.3 | 58.6 | 68.5 | 71.6 | 69.2 | 61.7 | 49 | 34.2 | 20.9 | 9.3 | 22.28 | 15.6 | 36.32 | 37.8 | 54.14 | 64.76 | 60.98 | 50.9 | 36.32 | 24.1 | 18.1
NV | FALLON NAAS | 33.7 | 40 | 46.8 | 52.1 | 60.3 | 68.5 | 77.3 | 75 | 67.1 | 54.2 | 41.7 | 32.4 | 21.7 | 19.22 | 22.3 | 26.24 | 25.3 | 37.76 | 39.2 | 41 | 35.6 | 28.94 | 19.2 | 20.3
NE | FALLS CITY/BRENNER | 26.9 | 29.2 | 42.6 | 54.6 | 64.4 | 73.7 | 77.7 | 75.5 | 66.7 | 55 | 42 | 29.6 | 15.1 | 15.62 | 34 | 42.26 | 48.6 | 59.72 | 65.3 | 66.56 | 55.6 | 40.64 | 28 | 24.3
ND | FARGO HECTOR INTERNATIONAL AP | 9.3 | 14.3 | 27.4 | 43.6 | 56.7 | 66.5 | 70.7 | 69.2 | 60.2 | 46.1 | 29.6 | 15.5 | -2.2 | 3.02 | 22.5 | 28.58 | 44.6 | 53.24 | 59.9 | 54.86 | 46 | 31.64 | 19.6 | 3.9
MN | FARIBAULT MUNI AWOS | 14.6 | 19.2 | 31.8 | 46.3 | 58.1 | 68 | 71.8 | 69.2 | 61.3 | 48.3 | 33.8 | 20.5 | 9.1 | 0.68 | 31.5 | 37.4 | 47.1 | 56.48 | 66.02 | 61.34 | 48.7 | 35.96 | 29.8 | 19.8
MO | FARMINGTON | 33.3 | 36.8 | 46 | 55.6 | 64.6 | 73 | 76.7 | 76.1 | 67.2 | 56.7 | 45.2 | 35.4 | 29.5 | 24.44 | 32.5 | 40.28 | 50.7 | 61.7 | 66.02 | 67.82 | 52.3 | 40.64 | 34.2 | 27.3
NM | FARMINGTON FOUR CORNERS REGL | 31 | 36.7 | 44.4 | 51.2 | 61 | 70.8 | 77.1 | 74.4 | 66.3 | 53.2 | 40.9 | 31 | 22.1 | 22.64 | 23.9 | 20.48 | 32.2 | 33.44 | 44.6 | 46.58 | 38.7 | 31.64 | 23.5 | 18.7
VA | FARMVILLE | 38.5 | 40.4 | 48.5 | 58 | 66 | 74.4 | 78.5 | 77.2 | 69.6 | 58.6 | 48.3 | 41.3 | 24.8 | 27.68 | 25.5 | 45.68 | 57 | 61.7 | 63.32 | 62.78 | 60.4 | 53.6 | 43.3 | 32
AR | FAYETTEVILLE DRAKE FIELD | 37.2 | 41 | 48.8 | 57.8 | 65.9 | 74 | 78.3 | 77.7 | 69.3 | 58.5 | 47.9 | 39.1 | 29.8 | 25.7 | 40.1 | 50.72 | 53.1 | 65.48 | 70.16 | 66.92 | 63.5 | 50.36 | 43.5 | 24.4
NC | FAYETTEVILLE POPE AFB | 43.6 | 46.7 | 53.6 | 63.1 | 71 | 78.4 | 81.5 | 79.7 | 73.5 | 63.2 | 52.8 | 46.1 | 28.4 | 31.64 | 32 | 43.7 | 52.7 | 64.4 | 72.32 | 66.38 | 60.3 | 48.74 | 36.7 | 31.5
NC | FAYETTEVILLE RGNL G | 44.6 | 47.3 | 54 | 62.8 | 70.5 | 77.9 | 81.3 | 79.6 | 73.7 | 63.5 | 53.6 | 46.6 | 28.6 | 31.46 | 32.2 | 42.98 | 53.1 | 64.58 | 68.54 | 68.9 | 62.1 | 48.38 | 38.3 | 25.2
WA | FELTS FLD | 31.6 | 34.6 | 41.2 | 47.6 | 55.9 | 62.2 | 70.8 | 69.8 | 61.6 | 48.8 | 38 | 30.7 | 28.9 | 30.38 | 27 | 33.08 | 36.7 | 46.58 | 47.12 | 46.58 | 49.6 | 36.5 | 33.1 | 28.4
MN | FERGUS FALLS AWOS | 11 | 13 | 29 | 44 | 57 | 67 | 72 | 69 | 61 | 47 | 31 | 15 | 10.8 | 14.18 | 23.4 | 34.88 | 42.8 | 53.96 | 61.52 | 59.54 | 52.2 | 41.54 | 26.1 | 18
OH | FINDLAY AIRPORT | 26.6 | 29.2 | 38.5 | 50.2 | 60.9 | 70.1 | 73.2 | 71.3 | 64.4 | 53.3 | 41.7 | 31.4 | 21.7 | 24.08 | 32 | 39.92 | 50.7 | 57.74 | 61.34 | 57.92 | 53.6 | 39.38 | 36.9 | 24.3
AZ | FLAGSTAFF PULLIAM ARPT | 30.3 | 32.3 | 37.8 | 43.4 | 51.8 | 60.8 | 66.5 | 64.4 | 58.1 | 47.3 | 37.4 | 29.7 | 16.7 | 13.46 | 19.9 | 24.8 | 21.4 | 32.54 | 38.66 | 41.36 | 37.4 | 31.82 | 19 | 15.4
MI | FLINT BISHOP INTL ARPT | 23.7 | 25.6 | 34.9 | 47 | 58 | 67.7 | 71.2 | 69.6 | 61.8 | 50.7 | 39.4 | 29 | 16 | 14.36 | 26.8 | 33.44 | 47.1 | 53.78 | 60.44 | 59.9 | 54.1 | 39.38 | 27.1 | 22.5
AR | FLIPPIN (AWOS) | 37.1 | 41.1 | 49.2 | 59.2 | 67 | 75.3 | 79.2 | 79.1 | 70.4 | 60 | 48.9 | 39.6 | 25.7 | 30.74 | 30.7 | 42.62 | 55.9 | 60.26 | 66.74 | 61.7 | 60.8 | 51.08 | 41.4 | 24.6
SC | FLORENCE REGIONAL AP | 46.5 | 49.2 | 55.8 | 63.9 | 71.5 | 78.3 | 81.5 | 80.1 | 74.7 | 64.8 | 55 | 48.4 | 39 | 31.1 | 48.4 | 50.72 | 59.7 | 66.74 | 73.04 | 71.78 | 66.6 | 55.76 | 48.2 | 30.6
MN | FLYING CLOUD | 16.1 | 19.9 | 32.5 | 47.9 | 59.5 | 68.6 | 74.5 | 71.6 | 63.6 | 49.8 | 35.9 | 21.2 | 17.6 | 6.62 | 21 | 35.96 | 43.3 | 57.92 | 62.06 | 61.88 | 54.5 | 33.8 | 28.6 | 0.1
GA | FORT BENNING LAWSON | 46.6 | 50.6 | 56.7 | 63.1 | 71.7 | 78.4 | 80.9 | 80.2 | 75.1 | 64.8 | 54.9 | 48.3 | 31.6 | 36.5 | 38.5 | 46.76 | 63.1 | 66.2 | 68 | 69.26 | 64.4 | 48.38 | 41.4 | 32.7
NC | FORT BRAGG SIMMONS AAF | 44 | 47.6 | 53.9 | 63 | 70.8 | 78.5 | 81.8 | 79.6 | 73.8 | 63.4 | 52.7 | 46.8 | 34.7 | 32.18 | 32.5 | 42.08 | 57.4 | 64.58 | 72.86 | 67.82 | 62.8 | 48.02 | 37 | 31.8
KY | FORT CAMPBELL AAF | 37.1 | 41.6 | 49.7 | 59.3 | 68 | 75.7 | 78.8 | 78 | 71 | 59.9 | 48.7 | 40.2 | 24.6 | 28.8 | 30.7 | 40.1 | 50.4 | 68.2 | 68.9 | 70.9 | 57.2 | 46.9 | 38.7 | 32.5
CO | FORT COLLINS (AWOS) | 29.6 | 31.4 | 40.7 | 47.1 | 57.3 | 66.4 | 72.8 | 70.6 | 62.8 | 49.7 | 37.4 | 29.7 | 14 | 14.72 | 22.6 | 28.22 | 38.3 | 43.34 | 48.92 | 42.08 | 36.5 | 25.16 | 23.4 | 14.2
IA | FORT DODGE (AWOS) | 17.7 | 22.4 | 34.9 | 47.9 | 59.6 | 69.2 | 73.1 | 70.8 | 62.6 | 50.7 | 36.4 | 22.9 | 12.2 | 22.82 | 23.7 | 38.66 | 48.6 | 60.08 | 64.58 | 61.7 | 52.9 | 33.08 | 26.8 | 11.8
NY | FORT DRUM/WHEELER-S | 19 | 20.8 | 30.3 | 43.8 | 55.9 | 65.1 | 69.1 | 67.8 | 60.1 | 48.6 | 37 | 25.8 | 22.1 | 18.68 | 28.6 | 29.66 | 38.3 | 54.14 | 59.54 | 55.4 | 50.5 | 39.38 | 31.3 | 27.5
TX | FORT HOOD | 49.9 | 54.4 | 61.2 | 68.2 | 75.3 | 83.5 | 85.1 | 86.5 | 79.8 | 70.2 | 59.4 | 52 | 34.2 | 39.92 | 38.1 | 47.84 | 61.5 | 69.08 | 68.54 | 67.64 | 58.3 | 50.72 | 42.6 | 33.8
KY | FORT KNOX GODMAN AAF | 33.7 | 38.4 | 46.3 | 56.9 | 65.7 | 73.6 | 76.5 | 75.9 | 68.8 | 57.8 | 46.6 | 37.2 | 29.5 | 27.1 | 27.9 | 37.8 | 56.1 | 63.7 | 66.9 | 63 | 47.5 | 46.9 | 33.6 | 28.8
FL | FORT LAUDERDALE | 67 | 69.5 | 71.7 | 75.4 | 79.1 | 82.1 | 83.4 | 83.9 | 82.4 | 79.1 | 73.1 | 69.8 | 56.3 | 57.2 | 65.1 | 63.32 | 64.4 | 73.04 | 74.3 | 72.32 | 72.3 | 68 | 63.3 | 56.3
FL | FORT LAUDERDALE HOLLYWOOD INT | 68.8 | 70.4 | 72.7 | 76.2 | 80 | 82.7 | 83.9 | 84.2 | 82.8 | 79.9 | 74.4 | 71 | 63 | 63.86 | 59.5 | 64.94 | 71.1 | 74.66 | 74.84 | 74.48 | 72.9 | 69.08 | 61.7 | 57.6
IA | FORT MADISON | 26 | 30 | 42.1 | 53.5 | 64.4 | 72.6 | 76.6 | 75.6 | 67.2 | 55.8 | 42.2 | 31.3 | 19.9 | 24.62 | 36 | 47.3 | 52.3 | 60.62 | 69.08 | 64.76 | 61.7 | 39.74 | 32.2 | 27.1
AB | FORT MCMURRAY AP | 0.6 | 8.1 | 20 | 37 | 49.3 | 58.4 | 62.9 | 59.9 | 50.2 | 36.4 | 17.6 | 4 | -4.4 | -1.12 | 7 | 20.12 | 30.7 | 43.88 | 51.44 | 49.28 | 41.2 | 27.14 | 14.7 | -2.7
FL | FORT MYERS PAGE FIELD | 64.9 | 66.9 | 69.8 | 74.1 | 79 | 82.1 | 82.9 | 83.2 | 82 | 77.6 | 71 | 66.8 | 54.5 | 56.48 | 59.7 | 63.86 | 68 | 73.22 | 73.76 | 74.66 | 73.9 | 70.34 | 66.7 | 56.8
BC | FORT NELSON | -4.6 | 5.2 | 17.5 | 37 | 49.3 | 58.7 | 62.7 | 59.2 | 49 | 33.2 | 9.8 | -2.3 | -10.1 | -1.3 | 4.8 | 21.02 | 31.6 | 44.78 | 51.62 | 48.38 | 39.7 | 26.6 | 8.6 | -6.5
LA | FORT POLK AAF | 50.5 | 54 | 60 | 67 | 74.5 | 80.6 | 82.5 | 82.9 | 77.9 | 67.9 | 57.8 | 51.6 | 39.7 | 43.16 | 41.7 | 55.76 | 68.7 | 71.24 | 72.32 | 70.7 | 64.6 | 55.58 | 48.7 | 34.3
KS | FORT RILEY MARSHALL AAF | 30.8 | 33.9 | 46.2 | 54.6 | 64.8 | 75.7 | 80.2 | 79 | 69.2 | 57.1 | 44 | 32.8 | 20.5 | 21.2 | 35.1 | 42.62 | 52.7 | 64.94 | 65.66 | 66.56 | 57.2 | 45.32 | 31.8 | 26.6
BC | FORT SAINT JOHN | 8.6 | 15 | 22.7 | 38.2 | 49.4 | 57.2 | 61 | 58.9 | 51 | 38 | 20.3 | 10.9 | 1.4 | 5.54 | 8.8 | 21.56 | 30.2 | 41.36 | 47.48 | 45.5 | 38.5 | 27.5 | 16.2 | 4.6
OK | FORT SILL POST FIELD AF | 40.9 | 45.6 | 53.3 | 61.4 | 70.6 | 80.2 | 84 | 82.9 | 74.8 | 63.2 | 51 | 41.9 | 29.5 | 33.08 | 28.6 | 38.3 | 58.3 | 60.62 | 65.48 | 63.14 | 50 | 44.78 | 38.1 | 33.1
AR | FORT SMITH REGIONAL AP | 40.6 | 44.9 | 53.3 | 62.1 | 70.2 | 78.5 | 82.8 | 82.4 | 74.2 | 63.2 | 51.7 | 42.4 | 26.1 | 26.42 | 39.6 | 47.84 | 57.9 | 67.64 | 70.7 | 68.72 | 64.4 | 49.1 | 43.7 | 26.1
IN | FORT WAYNE INTL AP | 25.6 | 28.8 | 38.8 | 50.4 | 61 | 70.5 | 73.5 | 71.5 | 64.2 | 53 | 41.3 | 30.5 | 14.4 | 17.42 | 28.9 | 37.4 | 51.6 | 54.32 | 60.8 | 62.42 | 55.9 | 42.62 | 32.4 | 18
TX | FORT WORTH ALLIANCE | 45.8 | 49.3 | 57.1 | 64.9 | 73.2 | 81.6 | 85.4 | 85.6 | 77.5 | 66.8 | 55.6 | 46.6 | 34.2 | 34.88 | 41.9 | 48.2 | 62.6 | 70.16 | 67.64 | 68.72 | 62.8 | 55.94 | 39.2 | 27.1
TX | FORT WORTH MEACHAM | 46.7 | 50.5 | 57.5 | 65.5 | 73.8 | 81.8 | 85.4 | 85.6 | 78 | 67.5 | 56.4 | 47.8 | 34.2 | 41.9 | 42.8 | 48.92 | 65.1 | 69.08 | 69.08 | 67.64 | 63 | 55.4 | 41.7 | 34.7
TX | FORT WORTH NAS | 47.4 | 51.7 | 58.9 | 66.3 | 75.1 | 82.9 | 86.3 | 86.1 | 79.4 | 68.4 | 57.3 | 48.4 | 33.1 | 43.34 | 47.5 | 53.6 | 61 | 66.02 | 67.1 | 68.36 | 63.3 | 53.42 | 38.3 | 27.9
AK | FORT YUKON | -17.4 | -11 | 1 | 25.5 | 46.1 | 59.7 | 61.8 | 54.8 | 42.3 | 19.7 | -5 | -11 | -12.8 | -18.76 | -6.2 | 10.22 | 29.8 | 39.02 | 42.44 | 37.4 | 30.9 | 14.54 | 6.1 | -24.2
MN | FOSSTON(AWOS) | 6.8 | 11.1 | 24.7 | 41.1 | 53.7 | 63.5 | 67.6 | 66.1 | 57.6 | 44 | 27.2 | 12.9 | 0.9 | 13.28 | 15.8 | 20.66 | 32.2 | 51.98 | 58.1 | 58.82 | 50.4 | 35.96 | 19.9 | -3.1
PA | FRANKLIN | 25.5 | 26.7 | 35.6 | 47.5 | 57.3 | 65.4 | 69.2 | 67.7 | 60.7 | 50 | 39.8 | 29.9 | 27.3 | 17.42 | 31.6 | 31.82 | 35.4 | 55.22 | 56.48 | 54.68 | 47.3 | 38.48 | 29.3 | 21.6
VA | FRANKLIN NAAS | 41.6 | 43.8 | 50.9 | 60.2 | 68.3 | 76.6 | 80.2 | 78.7 | 72.6 | 61.7 | 51.5 | 44.6 | 29.1 | 33.26 | 38.8 | 45.68 | 56.8 | 61.7 | 68.54 | 67.28 | 64.6 | 52.88 | 40.3 | 33.1
NB | FREDERICTON | 16 | 18.4 | 28.7 | 40.8 | 52.4 | 62 | 67.5 | 66.1 | 57.7 | 46.4 | 35.5 | 24 | 7.5 | 9.68 | 18.1 | 28.76 | 39.7 | 51.44 | 58.1 | 57.02 | 50 | 39.2 | 30.2 | 16.5
NE | FREMONT MUNI ARPT | 23.8 | 27.9 | 39 | 51.1 | 61.9 | 71.7 | 76.5 | 73.6 | 65.7 | 53.3 | 39.3 | 26.7 | 18 | 15.44 | 33.1 | 40.28 | 38.3 | 57.56 | 63.68 | 62.06 | 54.3 | 41.54 | 21.7 | 7.5
CA | FRESNO YOSEMITE INTL AP | 47.7 | 52 | 57.3 | 62.1 | 70.1 | 77 | 83.3 | 81.9 | 77 | 66.7 | 55 | 47.3 | 39.9 | 42.44 | 43.7 | 44.06 | 48.7 | 46.4 | 53.96 | 52.16 | 52.7 | 48.74 | 44.4 | 39.7
CA | FULLERTON MUNICIPAL | 57.7 | 57.7 | 60.6 | 62.8 | 67.1 | 70.1 | 74.5 | 75.5 | 74 | 68.4 | 62.2 | 56.6 | 40.8 | 45.32 | 46.4 | 47.3 | 53.4 | 57.56 | 61.34 | 62.96 | 56.1 | 55.22 | 44.6 | 41.5
GA | FULTON CO ARPT BROW | 43.9 | 47.2 | 53.9 | 61.6 | 69.5 | 76.7 | 79.6 | 78.9 | 73 | 62.5 | 52.3 | 45.7 | 31.5 | 38.48 | 45 | 55.94 | 60.8 | 65.84 | 68.72 | 69.08 | 64.9 | 43.88 | 38.1 | 29.3
AL | GADSEN MUNI AWOS | 42 | 47 | 54 | 60 | 69 | 76 | 79 | 79 | 73 | 62 | 50 | 44 | 30.6 | 37.04 | 45.1 | 50.54 | 53.1 | 64.22 | 68.9 | 67.28 | 59.5 | 50.9 | 42.1 | 27.5
OK | GAGE AIRPORT | 35.9 | 39.3 | 48.3 | 57.6 | 67.4 | 76.4 | 80.9 | 79.7 | 71.2 | 59.1 | 46.4 | 36.5 | 20.3 | 24.26 | 28 | 41.54 | 55.4 | 62.96 | 61.16 | 61.88 | 58.5 | 42.8 | 31.6 | 24.3
FL | GAINESVILLE REGIONAL AP | 55.3 | 58.2 | 62.6 | 68.2 | 74.9 | 79.5 | 81.1 | 81 | 78.3 | 71 | 62.3 | 56.9 | 47.1 | 48.56 | 53.8 | 57.2 | 65.7 | 69.62 | 72.68 | 73.94 | 69.1 | 63.32 | 52.7 | 44.2
NM | GALLUP SEN CLARKE FLD | 29.6 | 34 | 40.2 | 46.7 | 55.9 | 65.3 | 71.1 | 69 | 61.7 | 49.3 | 37.6 | 28.9 | 18 | 22.1 | 23.5 | 23.54 | 28 | 26.42 | 46.4 | 50.72 | 39.2 | 27.5 | 23.4 | 15.3
TX | GALVESTON/SCHOLES | 55.6 | 58.1 | 64.1 | 70.5 | 77.2 | 83.3 | 84.6 | 85.3 | 81.7 | 74.3 | 64.6 | 57.3 | 54.7 | 55.22 | 52.7 | 57.38 | 69.3 | 72.5 | 75.2 | 75.74 | 73.2 | 65.48 | 53.4 | 43
AK | GAMBELL | 6.7 | 9 | 8.4 | 18.5 | 30.7 | 39.3 | 46.1 | 46.9 | 41.8 | 33.1 | 25.1 | 11.6 | 7.3 | 7.34 | 11.7 | 2.66 | 29.5 | 34.52 | 32 | 34.16 | 32.5 | 29.12 | 21.9 | 9.7
KS | GARDEN CITY MUNICIPAL AP | 31.7 | 35.4 | 44.2 | 53.1 | 63.9 | 73.7 | 78.5 | 76.8 | 68.5 | 55.9 | 42.2 | 32.3 | 24.4 | 24.98 | 20.3 | 37.58 | 46.2 | 59.54 | 61.88 | 64.58 | 52 | 33.44 | 27.1 | 21.2
TX | GEORGETOWN (AWOS) | 49.6 | 52.4 | 58.5 | 66.6 | 74.5 | 79.8 | 83.2 | 83.7 | 78 | 69.2 | 57.5 | 50.2 | 30.2 | 35.06 | 36.3 | 44.78 | 61.7 | 67.82 | 63.32 | 66.92 | 57.9 | 48.38 | 41.4 | 35.4
WY | GILLETTE/GILLETTE-C | 25.6 | 26.6 | 35.5 | 42.9 | 52.1 | 62.4 | 71.4 | 70.2 | 60.1 | 46.1 | 34.2 | 25.5 | 13.6 | 21.74 | 20.5 | 31.64 | 36.5 | 46.76 | 51.8 | 44.78 | 44.2 | 31.82 | 22.3 | 20.3
MT | GLASGOW INTL ARPT | 14 | 18.9 | 30.8 | 44.1 | 54.4 | 63.3 | 71 | 70.3 | 59.5 | 44.8 | 29.3 | 17.1 | 5.7 | 15.44 | 20.8 | 30.38 | 39.9 | 44.06 | 50.72 | 48.74 | 37 | 31.82 | 22.3 | 11.3
MT | GLENDIVE(AWOS) | 16.6 | 20.5 | 32 | 43.2 | 53.2 | 62.5 | 71 | 69.5 | 59.2 | 45.1 | 31.3 | 20.1 | 11.1 | 15.26 | 11.8 | 33.8 | 41.5 | 45.32 | 48.56 | 46.76 | 41.5 | 26.42 | 22.8 | 9.1
NY | GLENS FALLS AP | 20.3 | 22.7 | 32.3 | 45.5 | 56.7 | 65.6 | 69.8 | 68.1 | 59.8 | 48.3 | 37.8 | 27 | 10 | 4.46 | 26.8 | 36.5 | 41.4 | 57.56 | 64.04 | 60.98 | 55.4 | 40.46 | 33.6 | 23
MN | GLENWOOD (ASOS) | 11.7 | 16.1 | 28 | 44.3 | 56.4 | 66.4 | 71.8 | 69.3 | 60.8 | 47 | 31.4 | 17.2 | 7.2 | 18.32 | 20.1 | 37.58 | 42.4 | 52.88 | 65.3 | 58.1 | 50.5 | 32.9 | 23.9 | 15.8
MS | GOLDEN TRI(AWOS) | 44.5 | 48.2 | 54.8 | 62.7 | 71.1 | 77.5 | 81 | 80.1 | 74.5 | 64 | 53.4 | 45.3 | 29.3 | 33.26 | 35.4 | 44.6 | 64.4 | 66.2 | 68.54 | 68.9 | 64.9 | 48.56 | 36.9 | 32.7
NC | GOLDSBORO SEYMOUR JOHNSON AFB | 44.6 | 47.6 | 54.1 | 62.7 | 70.7 | 78.1 | 81.6 | 79.3 | 73.8 | 63.6 | 53.5 | 47.3 | 29.5 | 32.18 | 33.3 | 41.72 | 50 | 65.84 | 73.4 | 68.54 | 61.7 | 48.74 | 39 | 27.5
KS | GOODLAND RENNER FIELD | 30.1 | 32.4 | 41.1 | 49.3 | 59.7 | 70.4 | 75.8 | 73.8 | 65 | 52.1 | 39.5 | 30.5 | 11.5 | 19.76 | 24.4 | 33.98 | 47.3 | 54.5 | 57.56 | 56.48 | 48.6 | 32.9 | 23.9 | 17.8
AZ | GRAND CANYON NATL P | 29.4 | 31.5 | 37.8 | 42.7 | 51.4 | 60.1 | 67.2 | 65.5 | 58.4 | 46.8 | 37.1 | 29 | 14.2 | 20.12 | 23.2 | 17.96 | 20.5 | 21.74 | 35.42 | 42.8 | 46.9 | 29.3 | 16.2 | 16
ND | GRAND FORKS AF | 7.2 | 12.4 | 25.1 | 41 | 54.5 | 64.8 | 69.2 | 68.1 | 58.3 | 44 | 27.2 | 14.1 | 14.4 | 25.16 | 20.8 | 28.04 | 37.8 | 54.14 | 57.92 | 58.28 | 43.9 | 29.84 | 26.1 | 20.1
ND | GRAND FORKS INTERNATIONAL AP | 7 | 11.8 | 24.8 | 41.6 | 54.6 | 64.9 | 69 | 67.8 | 58.4 | 44 | 27 | 12.9 | 2.5 | -1.48 | 20.8 | 34.16 | 45.3 | 54.14 | 59.36 | 58.82 | 50.2 | 30.02 | 19.4 | -4.2
NE | GRAND ISLAND CENTRAL NE REGIO | 25.4 | 29.6 | 39.8 | 50.4 | 61.3 | 71.5 | 76.1 | 74.1 | 65.5 | 52.7 | 38.7 | 27.8 | 7.7 | 13.28 | 24.1 | 39.2 | 45.9 | 60.26 | 61.88 | 60.08 | 51.3 | 36.5 | 23.5 | 14.5
CO | GRAND JUNCTION WALKER FIELD | 27.8 | 35.3 | 44.9 | 52.1 | 62.4 | 72.9 | 79.3 | 76.1 | 67 | 53.5 | 39.5 | 28.2 | 17.1 | 21.38 | 23.2 | 26.96 | 32.9 | 34.52 | 44.42 | 44.6 | 37 | 28.76 | 24.4 | 18
AB | GRAND PRAIRIE | 7.2 | 13.3 | 22.1 | 38.5 | 50 | 57.5 | 61.3 | 59.5 | 51.2 | 38.4 | 20.5 | 9.7 | 2.5 | 5.9 | 11.3 | 23.18 | 32 | 42.26 | 48.2 | 46.58 | 39.4 | 28.58 | 17.4 | 4.8
MI | GRAND RAPIDS KENT COUNTY INT | 24.5 | 26.3 | 35.4 | 47.4 | 58.5 | 68.3 | 71.9 | 70.3 | 62.4 | 50.9 | 39.6 | 29.7 | 15.8 | 16.34 | 25.3 | 32.18 | 47.3 | 54.5 | 60.26 | 60.8 | 54.9 | 38.48 | 34.5 | 21.4
MN | GRAND RAPIDS(AWOS) | 9.4 | 14.1 | 26.5 | 40 | 52 | 61.9 | 66.4 | 64.5 | 56.1 | 43.8 | 28.3 | 15.1 | 7.5 | 8.42 | 4.5 | 30.74 | 39.9 | 52.7 | 54.68 | 52.88 | 46.8 | 26.06 | 27.3 | 5.9
WA | GRAY AAF | 40 | 41.6 | 44.9 | 48.7 | 54.8 | 59.7 | 65.2 | 65.4 | 60.4 | 51.3 | 43.9 | 38.5 | 34.3 | 34.52 | 35.1 | 35.78 | 42.8 | 47.66 | 51.8 | 51.8 | 52.3 | 41.54 | 34.9 | 34.2
KS | GREAT BEND (AWOS) | 30.6 | 33.9 | 43.6 | 53.2 | 64.4 | 74.7 | 79.6 | 77.9 | 68.9 | 56.5 | 42.8 | 32.5 | 21.2 | 28.04 | 19.2 | 40.82 | 45.7 | 60.26 | 61.34 | 62.06 | 52.9 | 41.36 | 28.6 | 21.9
MT | GREAT FALLS INTL ARPT | 25.8 | 27.8 | 34.6 | 42.9 | 51.7 | 59.2 | 68.3 | 67.1 | 58.1 | 45.7 | 34.1 | 26.2 | 3 | 14.18 | 16.9 | 26.78 | 32.4 | 40.82 | 43.88 | 40.28 | 39.9 | 30.2 | 19.6 | 12
CO | GREELEY/WELD (AWOS) | 25.7 | 29.3 | 39.9 | 47.2 | 57.4 | 67.4 | 73.5 | 70.7 | 61.9 | 48.7 | 35.8 | 26.1 | 19.9 | 12.74 | 22.3 | 23.9 | 35.2 | 43.16 | 46.58 | 48.38 | 43.3 | 26.6 | 22.1 | 16.5
WI | GREEN BAY AUSTIN STRAUBEL INT | 18.1 | 21.3 | 31.9 | 44.6 | 56.1 | 66.1 | 69.9 | 68.3 | 60.2 | 48.4 | 35.9 | 23.8 | 7.2 | 10.94 | 23.9 | 33.08 | 46.8 | 56.3 | 62.42 | 59.36 | 53.1 | 36.5 | 28.6 | 18.5
WY | GREEN RIVER-GREATER GREEN RIVER INTERGALACTIC SPACEPORT | 22 | 25 | 34 | 41 | 51 | 61 | 70 | 67 | 58 | 44 | 32 | 22 | 15.6 | 18.5 | 17.2 | 24.62 | 30.2 | 32 | 38.84 | 36.68 | 30.9 | 24.44 | 21.4 | 12.4
NC | GREENSBORO PIEDMONT TRIAD INT | 39.9 | 42.8 | 50 | 59.1 | 66.9 | 74.9 | 78.3 | 76.8 | 70.2 | 59.7 | 49.7 | 42.3 | 21.7 | 28.58 | 39 | 42.98 | 54 | 65.84 | 67.64 | 67.28 | 59.7 | 47.48 | 37.9 | 27.1
SC | GREENVILLE DOWNTOWN AP | 42.8 | 45.9 | 53.8 | 62.3 | 69.7 | 77.1 | 79.4 | 79.2 | 72.8 | 62.4 | 53 | 45.1 | 24.8 | 28.4 | 31.6 | 39.56 | 46.8 | 64.4 | 69.44 | 68.18 | 61.7 | 46.22 | 42.8 | 27.9
MS | GREENVILLE MUNI AP | 44 | 47 | 56 | 65 | 73 | 80 | 82 | 82 | 77 | 65 | 54 | 47 | 38.7 | 43.52 | 45 | 52.88 | 59.9 | 68.72 | 70.7 | 71.24 | 61.2 | 50.9 | 41.4 | 41.9
TX | GREENVILLE MUNICIPAL AP | 46 | 49 | 58 | 64 | 73 | 81 | 84 | 85 | 78 | 67 | 56 | 48 | 29.3 | 36.68 | 36.7 | 48.92 | 66 | 68.72 | 69.98 | 69.08 | 57.2 | 49.82 | 41.4 | 33.8
NS | GREENWOOD AP | 23.2 | 23.7 | 31.4 | 41.9 | 52.5 | 61.8 | 68.3 | 66.8 | 59.2 | 48.9 | 39.7 | 30.1 | 17.6 | 17.42 | 23.5 | 31.46 | 41 | 51.98 | 58.46 | 57.74 | 51.3 | 41.54 | 34.7 | 24.1
MS | GREENWOOD LEFLORE ARPT | 44.8 | 48.4 | 56 | 64.2 | 72.4 | 79.1 | 81.4 | 81.2 | 75.3 | 64.6 | 54.1 | 46.9 | 36.9 | 41.54 | 37 | 52.52 | 59 | 69.26 | 73.58 | 68.72 | 64.6 | 51.98 | 48.7 | 35.8
SC | GREER GREENV-SPARTANBRG AP | 42.8 | 45.9 | 52.7 | 60.8 | 68.5 | 76 | 79.3 | 78.1 | 71.9 | 61.4 | 51.7 | 44.7 | 28.4 | 31.28 | 39.9 | 45.32 | 56.1 | 62.06 | 67.46 | 67.82 | 62.6 | 46.94 | 38.5 | 30.2
IN | GRISSOM ARB | 25 | 29 | 40.6 | 51.5 | 62.6 | 71.1 | 73.9 | 71.9 | 64.4 | 53.2 | 41.1 | 30.7 | 24.6 | 23 | 30.9 | 35.42 | 44.1 | 58.28 | 63.14 | 62.6 | 48.9 | 42.8 | 32.7 | 32.4
CT | GROTON NEW LONDON AP | 30.1 | 31.9 | 38.5 | 47.7 | 56.4 | 65.5 | 71.4 | 70.9 | 64.6 | 54.1 | 45.1 | 35.6 | 20.1 | 19.76 | 32.5 | 38.3 | 47.8 | 57.92 | 59.54 | 64.58 | 58.8 | 48.2 | 34 | 25.5
MS | GULFPORT BILOXI INT | 51.5 | 54.3 | 60.2 | 67.8 | 75 | 80.9 | 82.4 | 82.4 | 78.6 | 69.5 | 59.6 | 53.4 | 47.8 | 48.02 | 49.1 | 57.92 | 64.9 | 73.4 | 74.12 | 73.04 | 73.2 | 62.06 | 48.6 | 43.5
AK | GULKANA INTERMEDIATE FIELD | -1.3 | 5.7 | 14.7 | 32 | 45.5 | 54.7 | 57.3 | 53.5 | 43.2 | 27.3 | 5.6 | -0.8 | -7.8 | -0.04 | 5.9 | 17.24 | 26.8 | 39.92 | 43.88 | 40.46 | 32 | 23.72 | 3.6 | -4
CO | GUNNISON CO. (AWOS) | 12.1 | 16.4 | 29.5 | 39.3 | 48.6 | 57 | 63.1 | 60.8 | 52.9 | 41.8 | 28.1 | 14.3 | 10.4 | 9.86 | 14.7 | 19.4 | 16.5 | 29.84 | 39.02 | 41 | 23.2 | 22.1 | 12.4 | 2.7
AK | GUSTAVUS | 28.1 | 30.1 | 32.7 | 39.6 | 46.7 | 52.7 | 55.8 | 55.6 | 50.1 | 42.4 | 33.3 | 30.3 | 27.9 | 27.5 | 26.2 | 28.76 | 24.1 | 44.6 | 49.46 | 45.32 | 41 | 35.6 | 19.8 | 18
MD | HAGERSTOWN RGNL RIC | 31.7 | 33.8 | 42.9 | 54.1 | 63.5 | 72.3 | 76.1 | 74.4 | 67.1 | 55.6 | 45.6 | 35.5 | 21.4 | 23.18 | 31.1 | 37.58 | 47.3 | 56.84 | 66.02 | 63.32 | 55.6 | 47.66 | 34.2 | 20.1
NS | HALIFAX | 22.2 | 23 | 30.2 | 40 | 49.9 | 59.5 | 66.4 | 66.1 | 59.1 | 48.7 | 38.9 | 29.3 | 16.5 | 15.98 | 22.1 | 30.56 | 39.6 | 50.18 | 57.74 | 58.1 | 52 | 42.62 | 34 | 23.7
MN | HALLOCK | 5.1 | 8.8 | 22.7 | 41.4 | 53.3 | 63.6 | 67.7 | 66.4 | 57.2 | 43.3 | 26.8 | 12.2 | 1.6 | 1.58 | 21.4 | 36.32 | 34.7 | 56.12 | 61.52 | 58.64 | 43.3 | 37.22 | 15.3 | 10.4
MI | HANCOCK HOUGHTON CO AP | 16.5 | 18 | 25.9 | 38 | 50.5 | 60.2 | 65.1 | 64.6 | 56.3 | 44.4 | 32.2 | 21.8 | 5.9 | 11.12 | 25 | 32 | 34.5 | 51.98 | 57.2 | 57.2 | 52.5 | 32.72 | 27.7 | 18
WA | HANFORD | 33.8 | 38.4 | 46.9 | 55.3 | 63.5 | 71.1 | 76.1 | 76.5 | 67.9 | 55.2 | 42.2 | 32.6 | 25.7 | 23 | 29.5 | 30.56 | 32.7 | 41 | 42.62 | 40.64 | 36 | 31.1 | 31.8 | 24.8
UT | HANKSVILLE AP | 31 | 37 | 47 | 54 | 63 | 76 | 82 | 78 | 69 | 55 | 41 | 30 | 23.4 | 23 | 31.6 | 25.34 | 31.8 | 31.1 | 36.14 | 35.96 | 37.8 | 30.56 | 30.2 | 21.9
TX | HARLINGEN RIO GRANDE VALLEY I | 61.3 | 64.7 | 69.6 | 75.4 | 80.6 | 84.5 | 85.3 | 85.7 | 81.8 | 76.2 | 68 | 62.2 | 55.8 | 52.52 | 58.5 | 63.5 | 70.7 | 73.94 | 72.14 | 73.94 | 71.8 | 69.44 | 56.5 | 58.5
PA | HARRISBURG CAPITAL CITY ARPT | 31.6 | 33.6 | 42.3 | 53.4 | 62.9 | 71.8 | 76 | 74.4 | 66.8 | 55.6 | 45.4 | 35.3 | 16.9 | 19.58 | 23.9 | 41 | 48.2 | 59.72 | 64.76 | 62.96 | 57.9 | 45.32 | 34.3 | 19.2
AR | HARRISON FAA AP | 37.5 | 41.1 | 49 | 58.7 | 66.2 | 74.4 | 78.6 | 78 | 69.7 | 59.5 | 48.7 | 39.4 | 27.9 | 28.04 | 38.5 | 43.34 | 54.9 | 63.86 | 67.1 | 66.2 | 63.1 | 48.92 | 39 | 30.9
WV | HARRISON MARION RGN | 31.7 | 33.8 | 42.9 | 54.8 | 62.3 | 69.9 | 72.9 | 72.1 | 65.5 | 54.3 | 44.8 | 36.2 | 25.9 | 26.06 | 32.4 | 43.52 | 49.3 | 57.92 | 64.58 | 63.5 | 56.5 | 43.7 | 30.2 | 22.3
CT | HARTFORD BRADLEY INTL AP | 27.4 | 29.7 | 38 | 49.8 | 59.7 | 68.9 | 74 | 72.2 | 64.4 | 53 | 42.6 | 32.8 | 12.7 | 17.6 | 24.8 | 31.82 | 44.1 | 57.02 | 62.78 | 60.08 | 52.5 | 41.72 | 28.2 | 19.4
CT | HARTFORD BRAINARD FD | 29.2 | 31.5 | 39.2 | 50.4 | 60.2 | 69.4 | 74.8 | 73.2 | 65.7 | 54.2 | 44.1 | 34.2 | 15.6 | 18.86 | 30.6 | 34.7 | 47.7 | 54.5 | 60.62 | 56.48 | 57.4 | 43.52 | 38.8 | 30.7
NE | HASTINGS MUNICIPAL | 25.8 | 29.7 | 40.1 | 50.9 | 61.7 | 71.9 | 77.2 | 74.5 | 65.7 | 53.2 | 39.8 | 28.1 | 17.6 | 17.24 | 29.8 | 40.28 | 46.8 | 57.38 | 63.68 | 62.78 | 54.1 | 37.04 | 25.3 | 18.5
MS | HATTIESBURG LAUREL | 48.4 | 51.6 | 58.1 | 65.1 | 72.9 | 78.9 | 80.8 | 81 | 76.3 | 66.2 | 55.9 | 50 | 32.4 | 38.3 | 50.9 | 53.24 | 64.6 | 66.74 | 70.34 | 66.2 | 63.7 | 50.36 | 45 | 30.4
MT | HAVRE CITY-COUNTY AP | 17.7 | 22.1 | 32.1 | 44 | 53.5 | 61.5 | 69.6 | 68.4 | 58.1 | 44.7 | 30.7 | 20.7 | 12.2 | 14.72 | 15.3 | 29.12 | 30.9 | 47.3 | 44.42 | 47.84 | 37.2 | 31.1 | 22.1 | 17.8
CO | HAYDEN/YAMPA (AWOS) | 19.5 | 22.8 | 32.4 | 41.5 | 51.1 | 60.2 | 67.8 | 65.7 | 57.3 | 45.1 | 31.9 | 20.6 | 13.6 | 16.88 | 18 | 24.8 | 32 | 38.12 | 37.4 | 35.24 | 32.4 | 23.36 | 20.5 | 12.9
KS | HAYS MUNI (AWOS) | 29.7 | 32.8 | 42.8 | 52.2 | 63.2 | 74 | 79.2 | 77.2 | 68.2 | 55.3 | 41.8 | 31 | 21.7 | 24.98 | 26.2 | 39.02 | 48 | 54.14 | 58.28 | 58.46 | 56.1 | 34.88 | 31.8 | 18.7
CA | HAYWARD AIR TERM | 50.4 | 52.4 | 55.1 | 56.9 | 60.4 | 63.3 | 65.6 | 66 | 66.3 | 62.6 | 55.8 | 50.9 | 40.3 | 43.16 | 47.5 | 47.3 | 52.2 | 53.24 | 55.04 | 55.94 | 55.4 | 51.26 | 45 | 42.1
MT | HELENA REGIONAL AIRPORT | 23.4 | 27.6 | 36.1 | 44.3 | 53.5 | 61.1 | 70.4 | 68.6 | 59.1 | 45.8 | 32.8 | 23.1 | 13.8 | 15.62 | 20.8 | 25.88 | 32.7 | 41.54 | 42.8 | 42.26 | 39.6 | 30.56 | 23.2 | 16.3
KY | HENDERSON CITY | 33.2 | 36.3 | 46.2 | 57.5 | 67 | 74.9 | 77.5 | 76.3 | 68.7 | 57.5 | 46 | 36.5 | 27.1 | 26.6 | 28.2 | 39 | 48 | 58.3 | 62.4 | 56.7 | 54.3 | 41 | 29.7 | 28.9
MN | HIBBING CHISHOLM-HIBBING AP | 7.9 | 12.9 | 25.1 | 39 | 51.1 | 60.6 | 64.9 | 63.4 | 54.3 | 41.9 | 27.1 | 13.4 | -1.3 | -2.38 | 18.7 | 25.52 | 39.4 | 53.6 | 56.66 | 55.4 | 48.7 | 37.4 | 23.2 | 7.3
NC | HICKORY REGIONAL AP | 40.4 | 43.3 | 50.3 | 59.4 | 66.9 | 74.6 | 77.4 | 76.4 | 70.1 | 59.5 | 50.1 | 42.4 | 23.4 | 21.38 | 40.1 | 43.88 | 55.9 | 63.14 | 64.94 | 68 | 60.4 | 45.86 | 40.1 | 30.9
KS | HILL CITY MUNICIPAL AP | 30.6 | 33.1 | 42.9 | 52.4 | 63.4 | 73.9 | 80.2 | 77.3 | 68.1 | 54.9 | 41.7 | 31 | 16.9 | 16.7 | 18.5 | 40.46 | 46 | 57.2 | 66.02 | 55.58 | 54.9 | 37.76 | 26.2 | 22.6
VA | HILLSVILLE | 35.4 | 37.3 | 44.8 | 54.5 | 62.2 | 69.4 | 72.4 | 71.7 | 65.1 | 55.7 | 45.4 | 38.3 | 24.6 | 26.06 | 25.7 | 36.5 | 42.6 | 60.98 | 62.6 | 64.76 | 53.8 | 41 | 29.7 | 27.1
HI | HILO INTERNATIONAL AP | 71.4 | 71.1 | 71.7 | 72.4 | 74 | 75 | 76 | 76.5 | 76.4 | 75.7 | 74 | 72.3 | 62.6 | 64.22 | 63.7 | 65.3 | 67.1 | 67.46 | 69.08 | 68.54 | 68.5 | 68.54 | 67.6 | 64.4
OK | HOBART MUNICIPAL AP | 39.2 | 43.1 | 51 | 59.7 | 69.9 | 79.6 | 83.8 | 82.8 | 74.4 | 62.4 | 49.6 | 40.1 | 24.6 | 30.02 | 44.4 | 49.46 | 57.7 | 63.68 | 65.48 | 59.18 | 59 | 50.72 | 37.6 | 22.6
NM | HOLLOMAN AFB | 41 | 46 | 52.8 | 61.1 | 70.2 | 79.5 | 80.3 | 78.9 | 72.5 | 61.4 | 48.8 | 41.2 | 27.7 | 29.3 | 28.6 | 32.72 | 28.2 | 38.48 | 43.52 | 53.06 | 39.7 | 33.98 | 31.3 | 26.2
AK | HOMER ARPT | 24.7 | 26.6 | 29 | 37.5 | 44.8 | 50.9 | 54.9 | 54.2 | 48.7 | 39.3 | 29.6 | 26.6 | 20.5 | 11.66 | 20.8 | 31.46 | 37.2 | 42.98 | 48.56 | 49.1 | 45 | 34.88 | 17.2 | 17.2
FL | HOMESTEAD AFB | 67.4 | 69.5 | 71.9 | 75.1 | 78.6 | 81.6 | 82.8 | 83.1 | 81.9 | 78.8 | 73.1 | 70 | 50 | 55.22 | 63.5 | 62.24 | 71.2 | 73.76 | 75.2 | 73.76 | 74.8 | 70.7 | 62.6 | 60.4
TX | HONDO MUNICIPAL AP | 51.8 | 56 | 62.3 | 69.6 | 76.6 | 82.4 | 83.4 | 84.4 | 79.1 | 70.8 | 59.8 | 52.5 | 40.3 | 42.8 | 51.4 | 57.56 | 64.6 | 70.34 | 66.74 | 69.08 | 66 | 63.68 | 49.3 | 33.4
HI | HONOLULU INTL ARPT | 73.4 | 73.6 | 74.4 | 76.3 | 77.9 | 80.1 | 81.1 | 81.9 | 81.4 | 80.1 | 77.6 | 75.2 | 60.6 | 64.76 | 62.2 | 61.7 | 64.8 | 65.66 | 67.1 | 67.28 | 68.7 | 67.46 | 65.5 | 63.9
AK | HOONAH | 31 | 30 | 32 | 39 | 47 | 53 | 57 | 57 | 50 | 42 | 34 | 31 | 22.1 | 24.98 | 22.1 | 32.54 | 34.3 | 46.58 | 51.8 | 50.18 | 42.1 | 36.86 | 29.3 | 25.9
AK | HOOPER BAY | 11.6 | 15 | 12.3 | 25.1 | 35 | 45.7 | 50.7 | 51.4 | 45.7 | 33.3 | 23.4 | 13.3 | 4.8 | 6.08 | 20.1 | 21.38 | 32.4 | 35.78 | 44.06 | 43.52 | 36 | 27.32 | 25.3 | 9.1
WA | HOQUIAM AP | 43.1 | 43.8 | 45.8 | 48.6 | 53.2 | 57.3 | 60.3 | 60.9 | 59.1 | 52.7 | 46 | 42.5 | 39.9 | 37.58 | 40.3 | 43.34 | 44.4 | 51.26 | 54.86 | 54.68 | 53.6 | 47.66 | 43 | 40.6
VA | HOT SPRINGS/INGALLS | 28.3 | 30.7 | 38.3 | 48.9 | 57.8 | 65.5 | 69 | 68.1 | 61.1 | 51.4 | 40.3 | 32.3 | 24.3 | 20.48 | 27.7 | 32.72 | 37 | 51.08 | 58.28 | 55.4 | 45.7 | 38.3 | 30.4 | 25.7
MI | HOUGHTON LAKE ROSCOMMON CO AR | 19.5 | 20.7 | 30.1 | 42.8 | 54.7 | 64.1 | 67.5 | 65.7 | 58 | 46.9 | 35.7 | 25.4 | 11.3 | 10.04 | 22.8 | 29.48 | 43 | 51.44 | 59 | 57.56 | 50.9 | 38.12 | 27 | 19.8
ME | HOULTON INTL ARPT | 13 | 15.3 | 26.1 | 38.9 | 51.2 | 60.7 | 66.1 | 64.4 | 55.8 | 44.5 | 33.2 | 21.2 | 1.4 | 9.86 | 15.1 | 29.48 | 46.2 | 48.74 | 58.46 | 53.6 | 51.4 | 41.36 | 25 | 11.7
TX | HOUSTON BUSH INTERCONTINENTAL | 53.6 | 57 | 62.9 | 69.6 | 77 | 82.4 | 84 | 84.4 | 79.7 | 71.1 | 61.3 | 54.8 | 41.5 | 43.52 | 49.1 | 59.54 | 65.8 | 71.78 | 72.86 | 73.22 | 67.6 | 57.38 | 53.8 | 43.7
TX | HOUSTON ELLINGTON AFB [CLEAR LAKE - UT] | 55 | 58.2 | 63 | 69.8 | 77 | 82.5 | 84.4 | 84.4 | 80.7 | 72.4 | 62.4 | 56.2 | 42.3 | 46.04 | 44.2 | 56.48 | 67.3 | 72.14 | 72.5 | 74.48 | 67.5 | 61.34 | 55.2 | 47.3
TX | HOUSTON WILLIAM P HOBBY AP | 55.2 | 58.3 | 63.8 | 70.2 | 77.2 | 82.6 | 84 | 84.5 | 80.5 | 72.3 | 62.7 | 56.4 | 54.7 | 52.52 | 54.9 | 55.04 | 66.6 | 74.12 | 73.4 | 71.78 | 66.4 | 57.2 | 52 | 45.3
TX | HOUSTON/D.W. HOOKS | 53 | 56 | 62.3 | 69.4 | 76.4 | 82 | 83.3 | 84.1 | 79.5 | 70.3 | 60.8 | 53.4 | 44.8 | 50.36 | 53.2 | 64.76 | 66.6 | 71.96 | 73.4 | 70.88 | 68 | 68.54 | 48.2 | 43.9
MI | HOWELL | 24.8 | 26.5 | 35.5 | 47.7 | 58.4 | 68.2 | 71.7 | 69.8 | 63 | 51.4 | 40.6 | 29.5 | 15.4 | 18.14 | 30.7 | 36.5 | 42.6 | 60.62 | 61.52 | 61.52 | 54.3 | 40.46 | 34.9 | 24.1
GA | HUNTER AAF | 51 | 54.6 | 60.4 | 66.7 | 74.4 | 80.1 | 82.8 | 81.7 | 77.6 | 68.7 | 59.6 | 53.5 | 36.1 | 40.82 | 43.3 | 48.56 | 65.1 | 69.08 | 73.76 | 71.06 | 68.5 | 52.7 | 47.1 | 34.3
IN | HUNTINGBURG | 32.7 | 36.3 | 45.4 | 56.2 | 65 | 73.2 | 76.5 | 75.7 | 68 | 57 | 45.9 | 37 | 33.4 | 30.2 | 37 | 36.68 | 55.9 | 62.96 | 66.56 | 68.9 | 55.6 | 47.84 | 35.4 | 28.6
WV | HUNTINGTON TRI-STATE ARPT | 34.8 | 37.9 | 46.1 | 57 | 64.4 | 72.4 | 75.7 | 74.6 | 67.7 | 56.6 | 46.5 | 38.1 | 24.1 | 23.54 | 33.6 | 38.84 | 55 | 61.7 | 66.56 | 65.66 | 58.8 | 41 | 32.9 | 26.1
AL | HUNTSVILLE INTL/JONES FIELD | 41.8 | 45.4 | 53 | 61.8 | 69.9 | 77.2 | 79.7 | 79.3 | 73.3 | 62.3 | 51.5 | 44.2 | 26.6 | 32.54 | 41 | 45.86 | 57.6 | 65.3 | 68 | 68 | 60.8 | 47.48 | 44.8 | 30.7
SD | HURON REGIONAL ARPT | 15.9 | 21.4 | 33 | 46.1 | 58 | 68 | 73.5 | 71.7 | 62.6 | 48.3 | 32.9 | 20.4 | 10.6 | 13.64 | 21 | 31.82 | 43.7 | 56.3 | 59.9 | 57.38 | 46.2 | 34.7 | 20.7 | 8.2
AK | HUSLIA | -3 | 6 | 7.8 | 26 | 45 | 57 | 59 | 53 | 43 | 25 | 7.1 | 1.5 | -14.6 | 4.46 | 5.4 | 16.52 | 27 | 33.98 | 43.34 | 37.58 | 27.7 | 26.6 | 2.7 | 3.6
MN | HUTCHINSON (AWOS) | 13.4 | 17.4 | 29.3 | 45.1 | 56.9 | 67.2 | 71.6 | 68.7 | 61 | 47.9 | 33.2 | 19.9 | 12.9 | 8.42 | 17.2 | 35.24 | 44.4 | 55.94 | 67.1 | 59.54 | 52.3 | 34.7 | 25.5 | 19.4
KS | HUTCHINSON MUNICIPAL AP | 32 | 35.3 | 45.6 | 55.6 | 66 | 75.5 | 80.5 | 79.2 | 69.8 | 57.5 | 44.4 | 33.1 | 23.4 | 29.3 | 35.8 | 41.9 | 55.2 | 63.68 | 64.58 | 64.58 | 55.9 | 47.84 | 34.9 | 20.1
AK | HYDABURG SEAPLANE | 36.5 | 37.4 | 38.4 | 42.6 | 47.5 | 53.1 | 56.6 | 57.3 | 53.3 | 47.7 | 41.1 | 38.3 | 27.7 | 26.96 | 23.4 | 32.36 | 34.3 | 42.26 | 48.74 | 46.58 | 39.2 | 36.68 | 32.9 | 30.2
ID | IDAHO FALLS FANNING FIELD | 20.5 | 25 | 36.5 | 44.9 | 53.1 | 60.5 | 68.9 | 67.1 | 58.3 | 45.8 | 32.6 | 22.4 | 14.9 | 16.88 | 28.4 | 29.48 | 36 | 41.36 | 46.76 | 41.18 | 34.7 | 32.54 | 24.8 | 20.8
AK | ILIAMNA ARPT | 16.8 | 21.7 | 21.9 | 33.6 | 44.1 | 51.6 | 55.7 | 55 | 48.5 | 36.3 | 24.8 | 19.8 | 23.2 | 26.6 | 24.3 | 24.26 | 29.5 | 40.46 | 48.2 | 47.66 | 36.9 | 21.38 | 21 | 19.6
CA | IMPERIAL | 56.3 | 59.4 | 65.4 | 70.8 | 78.9 | 86.8 | 92.9 | 93 | 87.5 | 75.3 | 63.6 | 55.1 | 33.3 | 43.16 | 44.2 | 42.8 | 43.2 | 50.72 | 54.5 | 60.8 | 56.1 | 45.32 | 33.3 | 27.1
NE | IMPERIAL MUNI AP | 30 | 30 | 41 | 50 | 59 | 71 | 77 | 74 | 66 | 52 | 39 | 29 | 19.4 | 21.2 | 20.7 | 33.98 | 39.9 | 55.22 | 59.9 | 57.2 | 47.1 | 37.4 | 24.6 | 20.1
IN | INDIANAPOLIS INTL AP | 28.8 | 32.6 | 42.6 | 53.7 | 63.2 | 72.3 | 75.5 | 74.6 | 67.2 | 55.3 | 43.6 | 33.1 | 18.7 | 18.68 | 31.5 | 39.2 | 49.1 | 62.42 | 65.84 | 62.78 | 55.9 | 40.1 | 32 | 22.3
MN | INTERNATIONAL FALLS INTL AP | 5.6 | 11.1 | 24.1 | 39 | 51.6 | 61.4 | 65.2 | 63.6 | 54.5 | 41.7 | 26.5 | 11.6 | -4 | 1.94 | 12.6 | 23.36 | 38.3 | 52.88 | 58.64 | 56.48 | 46 | 33.98 | 19.6 | -0.6
NU | IQALUIT | -14.9 | -16.4 | -8.3 | 7.9 | 25.9 | 38.8 | 47 | 45.2 | 37.1 | 26.5 | 12.1 | -2.8 | -23.6 | -22.36 | -13.9 | 3.2 | 21.6 | 32.54 | 41 | 40.1 | 32.2 | 22.82 | 7.9 | -7.8
MI | IRON MOUNTAIN/FORD | 15.3 | 18 | 27.9 | 41 | 53.1 | 63.1 | 67.5 | 65.4 | 57.4 | 45 | 32.5 | 20.3 | 5.5 | 16.16 | 24.3 | 33.98 | 37.4 | 56.3 | 58.46 | 59.18 | 53.8 | 35.78 | 27.5 | 5.5
MI | IRONWOOD (AWOS) | 14.1 | 17 | 26.9 | 39.6 | 52 | 61.4 | 65.7 | 63.6 | 56.1 | 44.8 | 31.8 | 19.7 | -0.6 | 14.18 | 11.5 | 27.5 | 37 | 48.2 | 57.56 | 54.86 | 49.3 | 30.56 | 25.9 | 13.1
NY | ISLIP LONG ISL MACARTHUR AP | 32.1 | 33.2 | 39.9 | 49.7 | 59.2 | 68.9 | 74.6 | 73.3 | 66.3 | 55.5 | 45.6 | 37 | 18.7 | 25.52 | 30.4 | 39.74 | 49.1 | 60.26 | 68.36 | 64.94 | 58.1 | 44.78 | 37.9 | 27.3
CA | JACK NORTHROP FLD H | 58.6 | 58.3 | 60.1 | 61.5 | 64.8 | 67 | 70.3 | 70.8 | 70.5 | 67.5 | 63 | 57.8 | 45 | 45.68 | 49.8 | 46.58 | 52.2 | 56.3 | 59.9 | 58.82 | 57.9 | 55.04 | 44.4 | 40.5
WY | JACKSON HOLE | 15.8 | 16.8 | 26.8 | 35.8 | 45.5 | 52.4 | 59.9 | 59 | 50.2 | 39.6 | 25.1 | 15.6 | 16.7 | 8.42 | 20.5 | 23.54 | 26.8 | 36.5 | 35.06 | 40.82 | 36.7 | 25.34 | 18.3 | 13.8
MS | JACKSON INTERNATIONAL AP | 47.1 | 50.5 | 57.4 | 64.8 | 72.7 | 79.4 | 81.6 | 81.5 | 76.2 | 65.5 | 55.1 | 48.7 | 36 | 37.76 | 49.3 | 53.78 | 61.5 | 68.54 | 73.4 | 69.98 | 59.7 | 52.52 | 46 | 37
KY | JACKSON JULIAN CARROLL AP | 35.7 | 39.2 | 47.4 | 57.8 | 64.8 | 72 | 75 | 74.3 | 68.1 | 57.9 | 47.9 | 39 | 27.5 | 28.4 | 31.1 | 43.9 | 54.9 | 63.1 | 68.2 | 64.2 | 55.8 | 46.2 | 32.4 | 32.7
TN | JACKSON MCKELLAR-SIPES REGL A | 39.7 | 43.2 | 51.3 | 60.8 | 69.1 | 76.6 | 79.4 | 78.8 | 71.6 | 60.7 | 49.8 | 42 | 28 | 37.4 | 42.3 | 52.34 | 54.7 | 66.2 | 68.18 | 65.3 | 61.9 | 48.92 | 43.9 | 32.9
MI | JACKSON REYNOLDS FIELD | 24.2 | 26.3 | 35.5 | 47.7 | 58.1 | 67.5 | 70.9 | 69.3 | 61.7 | 50.7 | 39.6 | 29.2 | 21.9 | 12.38 | 30.4 | 37.76 | 50.9 | 57.38 | 62.42 | 62.24 | 53.1 | 44.06 | 33.4 | 18
NC | JACKSONVILLE (AWOS) | 43.8 | 45.8 | 52.4 | 60.8 | 68.8 | 76.1 | 79.8 | 78.1 | 72.5 | 62.5 | 52.5 | 45.9 | 30.2 | 30.92 | 33.8 | 38.12 | 59.4 | 61.52 | 65.84 | 65.66 | 63.1 | 47.3 | 36.9 | 28.2
FL | JACKSONVILLE INTL ARPT | 54 | 56.9 | 61.7 | 67.3 | 74.2 | 79.7 | 82 | 81.5 | 78 | 70.3 | 61.4 | 55.9 | 42.3 | 46.4 | 53.8 | 57.2 | 61.3 | 71.06 | 73.58 | 72.86 | 70.2 | 59.72 | 56.7 | 48.7
FL | JACKSONVILLE NAS | 56.5 | 59.5 | 64.4 | 70.5 | 77.3 | 81.9 | 83.9 | 83.6 | 80.8 | 73.4 | 64.6 | 58.8 | 49.8 | 49.1 | 57.2 | 57.2 | 66.4 | 71.96 | 73.76 | 73.4 | 69.6 | 60.8 | 50.9 | 46.9
FL | JACKSONVILLE/CRAIG | 55 | 57.5 | 62 | 68 | 74.6 | 80 | 82.2 | 81.8 | 78.6 | 71.6 | 62.9 | 57.2 | 49.1 | 52.34 | 53.6 | 55.4 | 65.5 | 71.06 | 75.02 | 71.96 | 69.8 | 63.14 | 60.4 | 47.5
NY | JAMESTOWN (AWOS) | 23 | 24.7 | 32.6 | 44.9 | 55.5 | 63.9 | 67.5 | 65.9 | 59.3 | 49 | 37.8 | 28.4 | 25.7 | 14 | 27 | 29.3 | 39.4 | 53.6 | 57.2 | 55.04 | 45.1 | 39.56 | 28.9 | 26.2
ND | JAMESTOWN MUNICIPAL ARPT | 10.5 | 15.1 | 27.2 | 42.1 | 54.9 | 64.7 | 69.6 | 68.1 | 58.8 | 44.6 | 28.5 | 15.3 | -0.8 | 13.46 | 22.1 | 35.42 | 38.1 | 55.76 | 60.8 | 60.44 | 48.7 | 28.4 | 25 | 3.9
WI | JANESVILLE/ROCK CO. | 22.5 | 25.4 | 36.6 | 49 | 58.1 | 67.4 | 71.7 | 71 | 63.7 | 52 | 40.8 | 25.1 | 24.8 | 26.42 | 24.3 | 27.86 | 40.8 | 52.7 | 57.56 | 58.1 | 50.2 | 36.68 | 29.5 | 28.8
MO | JEFFERSON CITY MEM | 32.3 | 36.2 | 46 | 57.1 | 65.8 | 74.6 | 78.7 | 77.2 | 68.6 | 57.6 | 46.5 | 35.2 | 26.6 | 31.46 | 33.8 | 45.86 | 52.2 | 64.4 | 67.28 | 68.72 | 62.6 | 47.66 | 39 | 26.1
PA | JOHNSTOWN CAMBRIA COUNTY AP | 26.2 | 27.7 | 36.3 | 48.2 | 57.5 | 65.6 | 69.3 | 67.9 | 60.9 | 50.3 | 39.9 | 30.2 | 18.5 | 19.04 | 28.6 | 40.1 | 45 | 55.94 | 61.88 | 60.26 | 53.8 | 38.3 | 32.9 | 13.6
AR | JONESBORO MUNI | 38.7 | 42.3 | 50.7 | 61 | 69.9 | 78.7 | 81 | 80.5 | 73.2 | 61.7 | 49.9 | 40.6 | 24.1 | 31.64 | 40.8 | 52.7 | 57.7 | 64.58 | 69.8 | 66.38 | 64.6 | 49.82 | 37.6 | 21.6
QC | JONQUIERE | 5.4 | 9.5 | 21.6 | 36.9 | 51 | 61.2 | 65.6 | 63.3 | 54.8 | 43.1 | 30.1 | 15.5 | -2 | 1.76 | 12 | 24.44 | 35.4 | 48.92 | 55.58 | 54.5 | 47.5 | 35.78 | 25.9 | 7.9
MO | JOPLIN MUNICIPAL AP | 35.6 | 40 | 48.6 | 58.3 | 66.7 | 75.5 | 80 | 79.5 | 70.5 | 59.6 | 48.3 | 38.2 | 21.7 | 30.74 | 41 | 48.92 | 59.4 | 64.58 | 65.12 | 66.92 | 64.6 | 46.76 | 43.5 | 29.5
ID | JOSLIN FLD MAGIC VA [TWIN FALLS - UO] | 30.4 | 33.7 | 41.8 | 47.2 | 56.4 | 64.9 | 75.4 | 72.9 | 63.9 | 50.8 | 38.5 | 30.1 | 25.3 | 24.98 | 33.1 | 30.02 | 34.9 | 40.46 | 42.26 | 46.58 | 33.1 | 27.32 | 23 | 25.2
AK | JUNEAU INT ARPT | 28.1 | 30.2 | 33 | 40.8 | 48.7 | 54.6 | 56.9 | 56 | 50.2 | 42.2 | 33.5 | 29.7 | 20.5 | 21.02 | 23.4 | 36.5 | 42.4 | 48.02 | 52.16 | 49.46 | 47.7 | 39.38 | 23 | 25.3
HI | KAHULUI AIRPORT | 72 | 71.9 | 72.7 | 74.1 | 75.9 | 77.9 | 78.9 | 79.5 | 79.1 | 78.1 | 75.7 | 73.4 | 64.2 | 64.04 | 62.8 | 65.66 | 64.8 | 65.66 | 67.28 | 67.28 | 69.3 | 66.2 | 66 | 65.5
MO | KAISER MEM (AWOS) | 32.2 | 36.2 | 45.3 | 56.2 | 64.7 | 73.2 | 77.7 | 77.2 | 68.1 | 56.9 | 45.9 | 36.5 | 27.5 | 28.04 | 30.4 | 40.82 | 55.2 | 64.4 | 67.82 | 66.74 | 61.3 | 45.14 | 37 | 23.5
AK | KAKE SEAPLANE BASE | 32.4 | 33.3 | 34.8 | 40.5 | 46.8 | 52.5 | 55.7 | 55.5 | 50.8 | 43.6 | 36.5 | 33.2 | 23.4 | 27.68 | 26.2 | 31.82 | 34.2 | 44.6 | 46.58 | 46.94 | 42.6 | 37.04 | 28.6 | 26.4
MI | KALAMAZOO BATTLE CR | 24.6 | 27 | 36.7 | 49.3 | 59.9 | 69.1 | 72.7 | 70.9 | 63.4 | 51.7 | 41 | 29.7 | 18 | 16.7 | 32.9 | 37.76 | 43.2 | 55.94 | 61.16 | 62.24 | 54.7 | 41 | 38.1 | 20.8
MT | KALISPELL GLACIER PK INT AR | 24.3 | 27.4 | 35.2 | 43.2 | 51.7 | 57.6 | 65.4 | 64.3 | 55.2 | 42.4 | 32.1 | 24 | 18.3 | 23.54 | 22.5 | 32.18 | 39.4 | 45.14 | 46.22 | 48.2 | 41.5 | 30.2 | 26.2 | 20.7
BC | KAMLOOPS AP | 26.9 | 32.1 | 40.9 | 49.7 | 58.3 | 64.6 | 71.4 | 70.1 | 60.9 | 47.5 | 35.9 | 27.9 | 21.2 | 23 | 25.5 | 29.84 | 37.8 | 44.24 | 47.3 | 46.94 | 43.5 | 36.14 | 28.8 | 21.2
HI | KANEOHE BAY MCAS | 73.3 | 73.1 | 73.6 | 74.8 | 76.3 | 77.9 | 78.8 | 79.6 | 79.7 | 78.9 | 76.9 | 74.7 | 62.1 | 63.86 | 63 | 64.4 | 65.7 | 68 | 68.36 | 68.72 | 69.4 | 67.64 | 67.6 | 62.4
MO | KANSAS CITY DOWNTOWN AP | 31.7 | 36.3 | 46.3 | 56.7 | 66.5 | 75.8 | 80.6 | 79.3 | 70.2 | 58.7 | 45.9 | 35 | 23 | 33.08 | 35.1 | 46.94 | 57.6 | 64.22 | 70.7 | 69.08 | 64.9 | 44.42 | 31.5 | 28.8
MO | KANSAS CITY INT ARPT | 29.3 | 34.1 | 44.4 | 54.9 | 64.7 | 73.9 | 78.3 | 77.2 | 68.1 | 56.8 | 44 | 32.8 | 18.3 | 18.32 | 31.1 | 41 | 54.3 | 63.5 | 65.48 | 65.84 | 56.8 | 45.32 | 27.5 | 19
NE | KEARNEY MUNI (AWOS) | 25.7 | 29 | 39.5 | 49.7 | 60.6 | 70.5 | 75.4 | 73.1 | 64.8 | 52 | 38.2 | 27.8 | 14 | 21.56 | 16.3 | 36.32 | 49.5 | 56.84 | 64.76 | 61.88 | 53.1 | 34.34 | 24.8 | 17.6
MS | KEESLER AFB | 52 | 55.6 | 60.8 | 68 | 75.6 | 81.5 | 83 | 83.1 | 79 | 69.9 | 60.2 | 55.2 | 40.8 | 44.96 | 45.5 | 55.76 | 63.9 | 72.32 | 74.84 | 72.68 | 68 | 55.58 | 51.6 | 44.2
BC | KELOWNA AP | 27.3 | 30.4 | 38.7 | 46.3 | 54.6 | 61.1 | 67.8 | 66.4 | 57.3 | 44.8 | 34.6 | 27.3 | 21.4 | 21.38 | 25.3 | 29.66 | 38.5 | 44.6 | 47.48 | 46.58 | 42.6 | 35.78 | 28.6 | 21.9
WA | KELSO WB AP | 40.8 | 42.2 | 46.3 | 49.9 | 55.8 | 60.2 | 65.6 | 65.8 | 61.5 | 52.8 | 45.2 | 40.3 | 35.2 | 36.32 | 41.2 | 41.36 | 44.1 | 49.46 | 52.7 | 54.5 | 51.1 | 45.14 | 41 | 34.9
AK | KENAI MUNICIPAL AP | 15.1 | 19.5 | 23.9 | 36.1 | 45.6 | 52.2 | 55.9 | 54.7 | 47.9 | 35.5 | 22.4 | 17.7 | 24.1 | 27.86 | 20.8 | 28.22 | 31.6 | 43.16 | 48.38 | 44.78 | 36 | 23.54 | 16.9 | 22.6
IA | KEOKUK MUNI | 27.4 | 30.7 | 42.5 | 54.1 | 64.3 | 72.9 | 77.3 | 75.8 | 66.8 | 55.6 | 43.5 | 31.5 | 11.1 | 21.38 | 24.4 | 46.58 | 54.9 | 56.12 | 67.28 | 64.58 | 59 | 44.78 | 33.1 | 24.8
AK | KETCHIKAN INTL AP | 34.9 | 35.9 | 37.5 | 42.9 | 49.2 | 54.7 | 58.1 | 58.5 | 53.2 | 45.7 | 39 | 35.7 | 27 | 24.44 | 21.4 | 32.36 | 39.2 | 47.48 | 51.62 | 57.02 | 47.1 | 39.74 | 27.7 | 20.7
FL | KEY WEST INTL ARPT | 69.9 | 71.5 | 73.5 | 76.9 | 80.5 | 83.5 | 84.8 | 84.9 | 83.5 | 80.5 | 75.6 | 72 | 56.7 | 57.56 | 64.8 | 66.56 | 69.6 | 73.76 | 74.48 | 74.66 | 75.2 | 72.32 | 69.1 | 63.9
FL | KEY WEST NAS | 70.1 | 72 | 73.8 | 77.3 | 80.7 | 83.6 | 84.7 | 84.9 | 83.6 | 80.6 | 75.4 | 72.4 | 59.2 | 61.52 | 63.9 | 65.12 | 73.2 | 73.4 | 74.48 | 76.1 | 75 | 72.68 | 67.3 | 63.9
TX | KILLEEN MUNI AWOS | 50 | 53 | 60 | 68 | 75 | 82 | 85 | 85 | 79 | 69 | 59 | 50 | 31.5 | 32.9 | 34.7 | 43.7 | 65.1 | 66.56 | 66.92 | 67.64 | 57.9 | 47.84 | 42.1 | 34.5
AK | KING SALMON ARPT | 15.8 | 19.8 | 22.1 | 34.8 | 44.5 | 51.5 | 55.4 | 54.8 | 47.8 | 34.7 | 23.3 | 17.4 | 16.5 | 12.56 | 13.3 | 28.22 | 34.7 | 43.16 | 49.28 | 46.94 | 41.5 | 29.84 | 18.9 | 18
AZ | KINGMAN (AMOS) | 44 | 47 | 52.6 | 58.7 | 68.6 | 78 | 83.6 | 82.2 | 75.4 | 63.2 | 51.4 | 42.7 | 18.3 | 26.24 | 30.4 | 23.54 | 27.7 | 28.94 | 45.5 | 47.48 | 41.7 | 34.52 | 33.4 | 28.2
TX | KINGSVILLE | 57.8 | 61.8 | 66.9 | 73.6 | 79.6 | 84.6 | 85.6 | 85.8 | 81.6 | 74.7 | 65.3 | 60 | 51.3 | 42.98 | 57 | 64.4 | 68 | 71.96 | 74.66 | 72.14 | 66 | 63.14 | 61.5 | 51.1
MO | KIRKSVILLE REGIONAL AP | 26.7 | 30.2 | 41.6 | 52.9 | 62.3 | 71.4 | 75.4 | 73.8 | 65.6 | 53.6 | 41.9 | 30 | 15.8 | 21.74 | 31.1 | 41 | 58.3 | 61.34 | 69.26 | 66.38 | 53.8 | 44.42 | 28.8 | 9
OR | KLAMATH FALLS INTL AP [UO] | 31.4 | 34.8 | 39.4 | 43.5 | 51.6 | 58.4 | 67.4 | 65.4 | 59.2 | 47.7 | 37 | 30.3 | 24.1 | 31.46 | 27.7 | 30.92 | 36.5 | 41 | 47.3 | 44.78 | 40.8 | 34.52 | 29.8 | 26.6
IA | KNOXVILLE | 25.2 | 28.3 | 39.9 | 52.9 | 63 | 72 | 76.4 | 74.7 | 66.1 | 53.8 | 42.4 | 29.7 | 17.1 | 14.36 | 25.7 | 43.52 | 52.9 | 64.04 | 62.6 | 63.68 | 63.5 | 41.9 | 30 | 19.9
TN | KNOXVILLE MCGHEE TYSON AP | 39.3 | 43 | 50.5 | 59.6 | 67.6 | 75.1 | 78.2 | 77.6 | 71.3 | 59.9 | 49.1 | 41.6 | 25.3 | 27.86 | 38.1 | 43.16 | 55.6 | 65.48 | 66.56 | 68 | 59.5 | 49.46 | 40.5 | 29.3
AK | KODIAK AIRPORT | 30.4 | 31.1 | 32 | 38.1 | 44.8 | 50.3 | 54.7 | 55.4 | 49.7 | 41 | 34.4 | 30.8 | 25.7 | 26.96 | 24.8 | 30.74 | 35.2 | 44.24 | 48.74 | 49.46 | 43.9 | 35.06 | 25.3 | 25.3
HI | KONA INTL AT KEAHOL | 74.7 | 74.7 | 75.6 | 76.6 | 77.8 | 78.6 | 79.6 | 80.6 | 80.2 | 79.6 | 77.7 | 75.9 | 64.9 | 60.08 | 63.1 | 65.84 | 64.9 | 69.62 | 69.26 | 67.1 | 68.7 | 68.72 | 65.3 | 62.6
AK | KOTZEBUE RALPH WEIN MEMORIAL | -3.3 | -0.8 | 0.8 | 15.1 | 32 | 46.4 | 54.9 | 52.1 | 42.7 | 25.7 | 9.7 | 1.3 | -5.4 | -6.16 | -3.1 | 5.36 | 27 | 39.38 | 48.56 | 47.84 | 38.3 | 19.76 | 4.5 | -1.3
QC | LA BAIE | 4.6 | 9 | 19.9 | 36 | 50.5 | 59.4 | 64 | 62.3 | 54.1 | 42.2 | 29.9 | 14.3 | -0.8 | 2.84 | 13.3 | 25.34 | 36.1 | 48.56 | 55.76 | 54.68 | 47.8 | 36.32 | 26.6 | 9.9
WI | LA CROSSE MUNICIPAL ARPT | 18.4 | 22.9 | 34.8 | 48.4 | 60 | 69.8 | 73.8 | 71.7 | 63.3 | 50.9 | 36.8 | 23.6 | 5.7 | 14.18 | 23.9 | 35.6 | 44.1 | 59.72 | 65.48 | 61.16 | 50.5 | 35.6 | 26.4 | 8.6
OR | LA GRANDE MUNI AP | 32.7 | 35.3 | 41.6 | 46.2 | 53.7 | 60.3 | 69.4 | 67.4 | 59.7 | 48.4 | 38.4 | 32.2 | 24.8 | 27.86 | 27.9 | 33.26 | 38.8 | 42.8 | 40.1 | 42.98 | 44.4 | 34.34 | 27.5 | 24.6
CO | LA JUNTA MUNICIPAL AP | 31.9 | 35.5 | 45 | 53 | 63.3 | 73.7 | 78.5 | 76.5 | 67.9 | 54.6 | 41.5 | 31.7 | 16.7 | 20.84 | 29.3 | 32.9 | 45.5 | 48.02 | 53.42 | 51.62 | 45.5 | 28.22 | 19.8 | 20.5
QC | LACADIE | 15.2 | 17.6 | 28.5 | 43 | 56.5 | 66.1 | 69.5 | 67.3 | 59.8 | 47.8 | 36.3 | 23.4 | 7.3 | 9.5 | 19.4 | 32 | 43.3 | 55.04 | 60.08 | 59.18 | 52.3 | 40.28 | 31.5 | 15.4
AB | LACOMBE | 10.8 | 15.4 | 23.9 | 38.2 | 49.1 | 56.2 | 60.9 | 58.9 | 50.9 | 39.2 | 23.5 | 13.7 | 7 | 9.32 | 16.2 | 26.24 | 34.3 | 45.5 | 52.16 | 49.1 | 40.6 | 29.3 | 19 | 7.3
NH | LACONIA MUNI (AWOS) | 20.8 | 23 | 32.5 | 44.4 | 55.1 | 65.3 | 70 | 68.2 | 60.2 | 48.6 | 38.3 | 28.1 | 18.9 | 12.2 | 25.2 | 25.88 | 37.2 | 53.6 | 53.06 | 55.58 | 48 | 36.32 | 30.7 | 20.5
IN | LAFAYETTE PURDUE UNIV AP | 27.4 | 31.1 | 41.3 | 52.7 | 62.6 | 71.7 | 74.5 | 73.2 | 66.1 | 54.7 | 42.7 | 31.8 | 19 | 19.04 | 35.1 | 45.86 | 50.5 | 60.62 | 64.76 | 65.3 | 55.4 | 42.44 | 39.9 | 14
LA | LAFAYETTE REGIONAL AP | 52.8 | 56 | 61.9 | 68.7 | 76.1 | 81.3 | 82.7 | 83 | 78.8 | 69.8 | 60.3 | 54.4 | 48.4 | 37.76 | 45.3 | 55.4 | 66 | 70.34 | 74.48 | 75.02 | 67.6 | 58.1 | 55.8 | 40.5
ON | LAGOON CITY | 16.5 | 18.2 | 27.4 | 40.7 | 53.9 | 64 | 68.6 | 67.3 | 60 | 48.7 | 36.9 | 25.6 | 11.8 | 13.1 | 20.8 | 32.18 | 45 | 56.84 | 61.52 | 61.52 | 55.8 | 43.7 | 34 | 19.2
LA | LAKE CHARLES REGIONAL ARPT | 52.8 | 55.9 | 61.8 | 68.3 | 75.7 | 81.4 | 82.9 | 83.1 | 79 | 70.2 | 60.5 | 54.3 | 42.1 | 42.62 | 55 | 60.62 | 65.8 | 72.14 | 74.12 | 74.3 | 71.1 | 58.46 | 53.4 | 43
AK | LAKE HOOD SEAPLANE | 17.5 | 22.1 | 25.6 | 37.7 | 49.5 | 57.5 | 60.8 | 58.5 | 50.3 | 37.3 | 23.4 | 19 | 18.9 | 26.06 | 20.3 | 24.98 | 32.9 | 40.28 | 46.22 | 46.58 | 35.8 | 28.04 | 30.9 | 20.8
OR | LAKEVIEW (AWOS) | 28.5 | 30.9 | 37.1 | 41.5 | 50.2 | 57.3 | 66.1 | 63.7 | 56.9 | 45.3 | 34.9 | 27.7 | 22.5 | 22.28 | 25.3 | 31.28 | 33.4 | 37.04 | 39.92 | 37.04 | 31.8 | 26.6 | 28.9 | 24.1
CO | LAMAR MUNICIPAL | 30.1 | 33.7 | 43.4 | 52.4 | 62.9 | 73.4 | 79 | 76.3 | 67.6 | 53.7 | 41 | 30.5 | 23.9 | 26.06 | 15.3 | 28.76 | 45 | 51.98 | 60.62 | 55.94 | 53.1 | 35.6 | 24.4 | 15.6
HI | LANAI AP | 68 | 69 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 74 | 72 | 70 | 61.7 | 62.78 | 61.2 | 62.96 | 62.4 | 65.3 | 65.12 | 66.56 | 67.8 | 65.3 | 63.3 | 59.5
PA | LANCASTER | 29.9 | 31.8 | 41.4 | 51.8 | 61.8 | 70.9 | 74.7 | 73.2 | 66 | 54.3 | 44.4 | 34.5 | 24.4 | 22.28 | 31.1 | 39.56 | 54.5 | 61.34 | 60.08 | 60.62 | 58.3 | 44.24 | 36.5 | 22.8
CA | LANCASTER GEN WM FOX FIELD | 45 | 47.7 | 53.9 | 58.9 | 67.8 | 75.8 | 82.5 | 81.1 | 74.2 | 62.8 | 51.2 | 43.7 | 25.5 | 27.14 | 38.8 | 35.42 | 38.7 | 39.92 | 42.26 | 42.08 | 39.7 | 38.12 | 24.6 | 31.1
WY | LANDER HUNT FIELD | 22.8 | 25.9 | 36.5 | 43.9 | 53.6 | 63.3 | 72.2 | 70.5 | 60.4 | 46.3 | 32.7 | 22.2 | 12.2 | 7.52 | 18.9 | 22.46 | 29.3 | 36.5 | 42.44 | 38.48 | 31.3 | 23.54 | 17.1 | 11.7
VA | LANGLEY AFB | 40.4 | 43 | 49.2 | 58.6 | 66.7 | 75 | 79.3 | 77.4 | 71.9 | 61.4 | 51.5 | 44.3 | 34.5 | 29.66 | 30.9 | 40.64 | 55 | 63.68 | 71.96 | 66.2 | 59.7 | 47.48 | 36.9 | 26.1
MI | LANSING CAPITAL CITY ARPT | 23.5 | 25.5 | 34.8 | 46.8 | 57.6 | 67.4 | 70.8 | 69.2 | 61.5 | 50.2 | 39.1 | 28.7 | 14.9 | 15.8 | 27.7 | 32.9 | 47.5 | 55.58 | 61.88 | 59.9 | 54.3 | 41.9 | 33.1 | 21.7
WY | LARAMIE GENERAL BREES FIELD | 22.4 | 23.7 | 31.9 | 38.1 | 47.7 | 57.7 | 64.5 | 62.6 | 54.1 | 42.4 | 30.2 | 21.6 | 13.6 | 15.98 | 19.8 | 22.46 | 33.3 | 35.06 | 45.86 | 41.36 | 40.3 | 24.08 | 17.4 | 14.2
TX | LAREDO INTL AP [UT] | 58.5 | 62.9 | 69.5 | 76.9 | 83 | 87.8 | 88.2 | 88.6 | 83.1 | 76.3 | 66.4 | 58.9 | 38.3 | 30.02 | 41.2 | 50.36 | 61.9 | 69.44 | 68.54 | 69.08 | 63.7 | 55.76 | 50.2 | 38.1
NM | LAS CRUCES INTL AP | 44 | 48 | 56 | 63 | 70 | 81 | 82 | 80 | 74 | 64 | 52 | 44 | 26.4 | 29.48 | 31.3 | 26.24 | 32.7 | 23 | 49.1 | 45.5 | 43 | 42.08 | 26.2 | 12.4
NV | LAS VEGAS MCCARRAN INTL AP | 48.7 | 52.5 | 60 | 66.9 | 77 | 86.5 | 92.5 | 90.7 | 82.9 | 69.7 | 56.5 | 47.4 | 23.2 | 24.08 | 29.1 | 25.88 | 31.5 | 38.12 | 40.64 | 44.6 | 35.4 | 30.56 | 25.7 | 18.9
NM | LAS VEGAS MUNICIPAL ARPT | 33.2 | 34.1 | 41.6 | 48.9 | 57.2 | 66.7 | 69.2 | 67.4 | 61.1 | 51.5 | 40.8 | 32.8 | 15.3 | 15.62 | 19.4 | 19.22 | 28.8 | 35.24 | 51.8 | 50.36 | 46.9 | 30.2 | 18.3 | 9.7
QC | LASSOMPTION | 13.2 | 16.3 | 27.2 | 42.4 | 55.8 | 65.2 | 69 | 67.1 | 59.2 | 46.8 | 34.8 | 21.2 | 4.1 | 6.62 | 17.2 | 29.3 | 41.7 | 53.78 | 59 | 58.1 | 51.3 | 38.84 | 29.5 | 12.7
MA | LAWRENCE MUNI | 27.5 | 29.6 | 37.3 | 48.4 | 58 | 66.9 | 72.8 | 71.3 | 64 | 52.3 | 42.7 | 32.8 | 12.7 | 15.62 | 30.9 | 35.96 | 48.9 | 53.24 | 61.34 | 61.7 | 55.9 | 40.1 | 35.6 | 22.5
OK | LAWTON MUNICIPAL | 40.8 | 44.5 | 53.7 | 61.9 | 71.4 | 80.1 | 84.4 | 84.3 | 75.5 | 63.6 | 51.5 | 41.4 | 28 | 36.5 | 34.3 | 55.04 | 61.2 | 66.38 | 66.38 | 67.1 | 58.6 | 50.36 | 45.3 | 33.3
IA | LE MARS | 21.1 | 25 | 36.8 | 49.4 | 60.6 | 71.1 | 74.9 | 72.6 | 63.2 | 51.4 | 36.5 | 24.4 | 16.3 | 12.74 | 35.1 | 41.36 | 55.9 | 59 | 61.88 | 65.66 | 55.2 | 47.12 | 35.6 | 20.3
CO | LEADVILLE/LAKE CO. | 17.4 | 17.4 | 24.4 | 31.6 | 41.3 | 50.8 | 56.3 | 53.6 | 47.2 | 37 | 25.8 | 17.4 | 8.4 | 8.06 | 12.9 | 15.44 | 18.3 | 27.68 | 38.84 | 28.76 | 37.2 | 20.48 | 10.2 | 5.7
NH | LEBANON MUNICIPAL | 20.1 | 22.1 | 31.8 | 44.7 | 56 | 64.9 | 69.8 | 68.2 | 60.6 | 48.1 | 37.7 | 26.6 | 8.1 | 14 | 19.6 | 30.2 | 38.1 | 55.4 | 59 | 59.18 | 55.2 | 39.38 | 30 | 19
VA | LEESBURG/GODFREY | 34.8 | 36.9 | 45.5 | 55.7 | 64.7 | 73.9 | 77.9 | 76.8 | 69.1 | 57.4 | 46.5 | 37.9 | 25 | 21.02 | 26.4 | 34.7 | 51.6 | 62.06 | 66.2 | 63.68 | 53.1 | 43.34 | 30.2 | 26.4
CA | LEMOORE REEVES NAS | 47.4 | 52 | 57.4 | 61.8 | 68.8 | 74.7 | 80.6 | 79.3 | 75.2 | 66 | 54.6 | 46.2 | 39.4 | 43.34 | 38.1 | 40.82 | 43.2 | 49.1 | 56.12 | 55.58 | 45.7 | 46.94 | 40.1 | 39
QC | LENNOXVILLE | 15.3 | 18.3 | 28 | 41.8 | 54 | 63.1 | 67.2 | 65.7 | 58.2 | 46.1 | 35.4 | 22.8 | 7 | 8.96 | 18.5 | 30.2 | 42.3 | 51.98 | 56.84 | 58.82 | 51.4 | 39.02 | 30.4 | 14.5
AB | LETHBRIDGE | 20.6 | 24.6 | 30.6 | 41.8 | 50.9 | 57.9 | 64 | 63.9 | 56 | 43.5 | 30.2 | 22.8 | 12.2 | 13.82 | 18.9 | 25.88 | 32.4 | 39.74 | 47.84 | 45.14 | 38.8 | 29.12 | 20.3 | 12.7
WV | LEWISBURG/GREENBRIE | 30.2 | 32.2 | 41 | 51.8 | 59 | 66.5 | 69.6 | 69.4 | 62.7 | 51.9 | 42.4 | 33.3 | 28.4 | 23 | 31.6 | 37.76 | 43 | 58.46 | 63.14 | 60.98 | 52.9 | 40.1 | 27.7 | 28.6
ID | LEWISTON NEZ PERCE CNTY AP | 36.1 | 39.3 | 45.5 | 51.2 | 59.2 | 65.7 | 75.5 | 74.7 | 66.1 | 52.2 | 41.4 | 34.7 | 27.5 | 29.12 | 30.6 | 35.6 | 39.9 | 46.4 | 45.5 | 48.2 | 40.1 | 38.84 | 31.5 | 28.2
MT | LEWISTOWN MUNICIPAL ARPT | 23.4 | 24.4 | 32.4 | 40.4 | 49.5 | 57.1 | 65.9 | 64.9 | 55.9 | 43.9 | 32.2 | 24.2 | 15.1 | 18.14 | 22.1 | 27.5 | 36.7 | 46.22 | 45.68 | 45.5 | 40.3 | 31.28 | 22.1 | 14
KY | LEXINGTON BLUEGRASS AP | 33.6 | 37.1 | 45.5 | 55.8 | 64.6 | 72.8 | 76.1 | 75.3 | 68.3 | 57.1 | 45.9 | 37.1 | 21.6 | 23.7 | 35.4 | 43.3 | 55 | 63.7 | 67.1 | 66.9 | 58.6 | 44.1 | 33.3 | 25.9
KS | LIBERAL MUNI | 33.8 | 36.5 | 45.5 | 54.6 | 65.1 | 75.1 | 80 | 78 | 69.8 | 57 | 43.9 | 34 | 26.1 | 31.46 | 25.5 | 36.14 | 52.5 | 57.38 | 60.08 | 64.22 | 57.9 | 41.54 | 32.9 | 23.2
HI | LIHUE AIRPORT | 71.7 | 71.5 | 72.3 | 73.9 | 75.7 | 77.9 | 78.9 | 79.5 | 79.4 | 78.3 | 75.7 | 73.4 | 61.3 | 64.4 | 65.3 | 65.84 | 67.1 | 67.28 | 71.24 | 70.88 | 71.2 | 68.9 | 67.5 | 63.5
CO | LIMON | 26.9 | 28.7 | 37.6 | 44.9 | 54.9 | 64.9 | 70.9 | 68.7 | 60.2 | 47.7 | 35.4 | 26.4 | 16.2 | 16.34 | 20.1 | 29.12 | 43 | 49.64 | 53.96 | 51.44 | 38.7 | 32.54 | 20.7 | 12.4
NE | LINCOLN MUNICIPAL ARPT | 24.7 | 29.5 | 40.5 | 51.6 | 62.6 | 72.6 | 77.5 | 75.4 | 66.2 | 53.6 | 39.4 | 27.9 | 13.8 | 20.48 | 30.9 | 42.62 | 51.1 | 63.32 | 65.84 | 63.5 | 54.3 | 42.08 | 27.7 | 18.7
MN | LITCHFIELD MUNI | 13 | 17.1 | 29.7 | 44.8 | 57.2 | 67.1 | 71.7 | 69.1 | 61.1 | 47.6 | 32.9 | 18.8 | 6.8 | 6.62 | 28.9 | 36.68 | 50.2 | 55.94 | 59.54 | 55.04 | 51.1 | 43.16 | 23.2 | 12.4
MN | LITTLE FALLS (AWOS) | 11.8 | 16 | 28.6 | 42.8 | 54.9 | 64.9 | 69.7 | 66.9 | 58.3 | 45.7 | 30.8 | 17.2 | 5.5 | 5.72 | 24.6 | 25.52 | 43 | 55.4 | 57.56 | 59.18 | 48.6 | 33.08 | 16.5 | 15.8
AR | LITTLE ROCK ADAMS FIELD | 42.4 | 46.2 | 54 | 63 | 71.1 | 79.3 | 82.6 | 82.2 | 74.9 | 63.8 | 52.6 | 44.1 | 26.6 | 30.02 | 41.5 | 50.36 | 61.9 | 68.72 | 70.88 | 69.44 | 64.8 | 49.28 | 43.5 | 30.2
AR | LITTLE ROCK AFB | 40.8 | 46 | 53.4 | 62.6 | 70.1 | 79.1 | 82.4 | 81.4 | 73.6 | 63 | 49.9 | 42.5 | 31.3 | 34.34 | 33.1 | 43.7 | 66.9 | 70.34 | 70.88 | 70.16 | 57 | 53.78 | 36.9 | 32.5
CA | LIVERMORE MUNICIPAL | 47.7 | 50.2 | 53.9 | 56.8 | 62.4 | 67.9 | 72.1 | 72 | 70.2 | 63.3 | 54.1 | 48.4 | 38.8 | 41.72 | 46.6 | 43.34 | 47.5 | 49.46 | 53.42 | 51.44 | 50.9 | 45.14 | 40.6 | 39.7
MT | LIVINGSTON MISSION FIELD | 29.1 | 27.8 | 36 | 42.3 | 50.5 | 58.8 | 69.6 | 66.9 | 58 | 46 | 35.4 | 27.3 | 12.9 | 11.84 | 21.6 | 29.66 | 34.7 | 43.7 | 42.08 | 44.42 | 32.5 | 30.74 | 22.5 | 17.8
CA | LOMPOC (AWOS) | 52.2 | 53 | 54.5 | 55.5 | 58.1 | 60.1 | 62.2 | 62.8 | 62.4 | 60.2 | 56.6 | 51.8 | 35.8 | 15.08 | 25.5 | 37.04 | 19.9 | 50.54 | 51.8 | 50.9 | 52.5 | 48.38 | 14.4 | 40.5
ON | LONDON AP | 22.7 | 23.6 | 32.3 | 44.7 | 56 | 65.8 | 69.4 | 67.8 | 60.7 | 49.6 | 38.5 | 28.3 | 17.6 | 17.06 | 24.1 | 33.8 | 43.9 | 55.4 | 58.82 | 59 | 53.1 | 41.72 | 33.4 | 21.7
KY | LONDON-CORBIN AP | 36.1 | 39.1 | 47.3 | 57 | 64.7 | 72.4 | 75.4 | 74.9 | 68.3 | 56.9 | 46.5 | 38.7 | 20.1 | 29.8 | 39 | 48.2 | 52.7 | 60.1 | 68 | 66.6 | 52 | 52.5 | 37.4 | 25.5
WI | LONE ROCK FAA AP | 18.9 | 21.5 | 34.9 | 48.1 | 58.7 | 68.6 | 72.3 | 70.3 | 62 | 49.5 | 37.7 | 23.3 | 11.3 | 18.32 | 28.2 | 38.3 | 49.1 | 59.36 | 62.24 | 57.38 | 51.4 | 40.64 | 36.9 | 19.6
CA | LONG BEACH DAUGHERTY FLD | 57.2 | 57.4 | 59.8 | 62.4 | 65.7 | 68.7 | 72.6 | 73.9 | 72.7 | 67.8 | 61.9 | 56.5 | 45.1 | 45.32 | 47.7 | 51.08 | 52.7 | 57.56 | 60.98 | 59.36 | 60.3 | 55.22 | 48 | 41.4
TX | LONGVIEW GREGG COUNTY AP [OVERTON - UT] | 48 | 51.1 | 58.5 | 66.1 | 73.7 | 80.8 | 83.4 | 84.2 | 77.6 | 66.9 | 56.9 | 48.5 | 40.8 | 37.4 | 42.1 | 53.6 | 62.4 | 63.14 | 69.8 | 69.8 | 60.8 | 57.2 | 44.4 | 37
CA | LOS ANGELES INTL ARPT | 57.7 | 57.5 | 58.6 | 60.6 | 63.4 | 66 | 69 | 69.9 | 69.2 | 66.3 | 62 | 57.3 | 46.9 | 48.56 | 45.5 | 50 | 53.6 | 57.74 | 59.9 | 60.08 | 61.3 | 53.96 | 48 | 45.3
KY | LOUISVILLE BOWMAN FIELD | 35.2 | 38.7 | 47.3 | 57.9 | 66.7 | 75 | 78.2 | 77.4 | 70 | 58.5 | 47.6 | 38.5 | 21.7 | 29.3 | 37.9 | 46.9 | 61.2 | 65.8 | 68 | 66 | 59.9 | 48.7 | 43.2 | 30.7
KY | LOUISVILLE STANDIFORD FIELD | 35.4 | 39 | 47.9 | 58.4 | 67.3 | 75.7 | 79 | 78.4 | 70.9 | 59.4 | 48.1 | 38.8 | 22.3 | 23.36 | 35.2 | 40.64 | 52.9 | 62.96 | 68.54 | 65.66 | 60.3 | 49.82 | 36.7 | 25.9
NV | LOVELOCK DERBY FIELD | 31.8 | 37.4 | 44.4 | 50.4 | 59.8 | 68.4 | 77 | 73.8 | 65.2 | 52.2 | 39.2 | 30.6 | 21.9 | 22.64 | 28.9 | 26.24 | 29.3 | 35.42 | 43.52 | 37.4 | 37.6 | 21.92 | 23.9 | 22.3
TX | LUBBOCK INTERNATIONAL AP | 41.2 | 45.1 | 52.6 | 61.2 | 70.4 | 78.7 | 80.7 | 79.5 | 72 | 61.8 | 50.1 | 41.5 | 24.1 | 25.88 | 29.1 | 34.16 | 46.9 | 55.76 | 60.26 | 60.8 | 57.4 | 43.88 | 32.5 | 25.3
TX | LUFKIN ANGELINA CO | 49.8 | 53.7 | 60.1 | 67.1 | 74.8 | 80.8 | 83 | 83.3 | 78 | 68.2 | 57.9 | 51.1 | 41.7 | 38.84 | 48.7 | 57.56 | 65.5 | 70.16 | 72.86 | 70.16 | 66.6 | 55.58 | 54 | 38.1
AZ | LUKE AFB | 53.8 | 57.1 | 63.5 | 70.2 | 79.1 | 88 | 93.4 | 92.5 | 86.4 | 73.4 | 61.6 | 52.7 | 46.4 | 38.84 | 40.6 | 31.28 | 33.1 | 28.76 | 47.48 | 47.12 | 50 | 36.32 | 31.3 | 33.3
VA | LYNCHBURG REGIONAL ARPT | 36.8 | 39.3 | 47 | 56.7 | 64.2 | 72.2 | 76 | 74.6 | 67.7 | 57 | 47 | 39.2 | 18.1 | 25.7 | 34.7 | 40.64 | 51.8 | 62.96 | 67.1 | 64.4 | 60.3 | 44.6 | 34.9 | 26.8
FL | MACDILL AFB | 61.2 | 64 | 67.9 | 72.8 | 78.5 | 82.2 | 82.9 | 83.2 | 81.9 | 76.3 | 68.4 | 64 | 47.5 | 50.72 | 51.3 | 59.36 | 70 | 70.88 | 73.94 | 72.5 | 72 | 65.12 | 54.7 | 50.9
GA | MACON MIDDLE GA REGIONAL AP | 47.2 | 50.5 | 57 | 63.8 | 72 | 78.8 | 81.6 | 80.7 | 75.2 | 64.9 | 55.1 | 48.6 | 33.8 | 35.96 | 45 | 49.46 | 59.2 | 69.26 | 68.9 | 69.62 | 68.5 | 53.06 | 48.2 | 34.7
WI | MADISON DANE CO REGIONAL ARPT [ISIS] | 19.8 | 23.8 | 34.7 | 46.9 | 58.1 | 68.1 | 71.8 | 69.9 | 61.7 | 49.9 | 37 | 24.9 | 8.4 | 11.84 | 26.6 | 33.26 | 50 | 55.94 | 65.48 | 61.88 | 52.2 | 39.74 | 25.5 | 14.9
BC | MALAHAT | 38.1 | 38.8 | 41.8 | 46.2 | 53.1 | 58.2 | 64.4 | 64.6 | 59.1 | 49.2 | 41.4 | 37.6 | 36 | 35.96 | 38.3 | 40.46 | 45.1 | 49.28 | 52.7 | 53.42 | 50.5 | 45.86 | 41 | 35.4
VA | MANASSAS MUNI(AWOS) | 33.3 | 36.2 | 43.4 | 54.4 | 62.2 | 71.8 | 76 | 74.5 | 67.5 | 55.2 | 45.2 | 35.6 | 26.2 | 21.38 | 24.3 | 34.16 | 41.5 | 61.16 | 67.46 | 63.68 | 54.9 | 41.36 | 27.9 | 28.6
NH | MANCHESTER AIRPORT | 25.6 | 28 | 36.3 | 48.1 | 58.6 | 68 | 73.4 | 71.7 | 63.7 | 52 | 41.7 | 31.5 | 10.9 | 16.34 | 28.9 | 34.88 | 39.9 | 56.66 | 58.28 | 57.74 | 56.7 | 38.84 | 30.4 | 26.2
KS | MANHATTAN RGNL | 29.6 | 33.5 | 43.8 | 54.7 | 65 | 74.5 | 79.9 | 77.8 | 68.3 | 56.3 | 43.2 | 31.7 | 20.7 | 22.28 | 33.6 | 45.32 | 54.9 | 65.48 | 70.16 | 68.54 | 55.9 | 42.8 | 31.8 | 20.8
MI | MANISTEE (AWOS) | 23.8 | 24.6 | 31.7 | 43 | 53.7 | 62.8 | 66.8 | 65.8 | 58.5 | 47.9 | 37.4 | 28.7 | 16.2 | 21.38 | 20.7 | 36.14 | 40.8 | 58.64 | 62.42 | 61.7 | 50.4 | 39.38 | 31.5 | 14.9
WI | MANITOWOC MUNI AWOS | 20.2 | 22.7 | 31.9 | 42.8 | 53.2 | 63.3 | 68.6 | 67.4 | 60 | 48.7 | 37 | 25.3 | 10 | 18.68 | 21.9 | 37.04 | 43.7 | 53.96 | 59.36 | 60.26 | 51.4 | 40.82 | 34.7 | 18.7
MN | MANKATO(AWOS) | 14.8 | 19.2 | 31.8 | 46.7 | 58.3 | 68.2 | 71.8 | 69.5 | 61.4 | 49.1 | 34.4 | 20.5 | 8.4 | 18.14 | 16.3 | 39.2 | 46.8 | 52.52 | 60.98 | 63.68 | 50.7 | 31.64 | 28.2 | 11.8
OH | MANSFIELD LAHM MUNICIPAL ARPT | 26.4 | 28.6 | 37.6 | 49.4 | 59.6 | 68.4 | 71.7 | 70.2 | 63.2 | 52.2 | 41.2 | 31.2 | 13.1 | 17.78 | 28.4 | 38.12 | 48 | 57.02 | 64.58 | 61.7 | 54.5 | 41.18 | 34.3 | 20.7
FL | MARATHON AIRPORT | 69.7 | 72.1 | 74.6 | 78 | 81.5 | 84.4 | 85.2 | 85.6 | 84.2 | 81 | 75.1 | 72.1 | 62.1 | 57.38 | 70 | 67.1 | 71.6 | 74.12 | 78.8 | 77.36 | 74.3 | 74.3 | 69.6 | 63.5
CA | MARCH AFB | 53.1 | 53.3 | 56.5 | 60.2 | 65.9 | 71.4 | 77.4 | 78.9 | 75.6 | 66.7 | 58.2 | 51.9 | 31.6 | 26.96 | 35.1 | 38.84 | 50.9 | 48.38 | 53.06 | 49.28 | 50.5 | 35.78 | 31.5 | 25.9
TX | MARFA AP | 41.9 | 45.7 | 51.5 | 58.8 | 67.1 | 74.1 | 73.4 | 72.6 | 67.8 | 59.7 | 49.3 | 42.5 | 28.8 | 32.72 | 29.5 | 30.74 | 31.8 | 43.34 | 46.4 | 49.46 | 40.8 | 34.16 | 30.4 | 20.7
GA | MARIETTA DOBBINS AFB | 42.6 | 46.4 | 53.1 | 62.1 | 69.5 | 77 | 79.7 | 78.4 | 73 | 61.6 | 51.9 | 45.5 | 26.8 | 32 | 33.3 | 41.18 | 50.5 | 66.56 | 71.06 | 68.18 | 61.5 | 45.14 | 36.3 | 30.2
VA | MARION / WYTHEVILLE | 33.3 | 36.1 | 44.9 | 53.8 | 62.1 | 69.8 | 73.1 | 72.2 | 65.4 | 54.7 | 43.7 | 37 | 18 | 29.48 | 34 | 32.36 | 45.1 | 57.74 | 60.98 | 62.96 | 52.2 | 48.02 | 36.1 | 21
IL | MARION REGIONAL | 34.2 | 36.3 | 48.5 | 58.6 | 67.2 | 75.2 | 77.8 | 77.8 | 70.3 | 58.7 | 49.1 | 37.9 | 30 | 28.22 | 30.6 | 39.38 | 49.8 | 67.46 | 67.64 | 64.76 | 55.9 | 45.32 | 40.8 | 26.8
MN | MARSHALL MUNI-RYAN FIELD AWOS | 15 | 19 | 32 | 45 | 58 | 68 | 72 | 69 | 62 | 49 | 34 | 20 | 10.6 | 20.3 | 14.7 | 35.42 | 41.5 | 51.62 | 59.72 | 63.86 | 50 | 35.78 | 26.1 | 11.3
WI | MARSHFIELD MUNI | 14.4 | 18.9 | 30.6 | 44.3 | 55.8 | 65.3 | 69.7 | 67.8 | 59.5 | 47.1 | 33.4 | 21.1 | 17.1 | 17.78 | 25.5 | 34.88 | 40.1 | 55.58 | 59.36 | 58.82 | 54 | 38.48 | 26.8 | 10.6
MA | MARTHAS VINEYARD | 31.4 | 32.1 | 37.6 | 46.1 | 55.5 | 63.9 | 70.1 | 69 | 62.7 | 53.2 | 45.1 | 36.9 | 28.6 | 21.02 | 31.1 | 37.76 | 43.5 | 57.02 | 64.04 | 61.88 | 57 | 48.74 | 40.1 | 25.5
WV | MARTINSBURG EASTERN WV REG AP | 33.1 | 35.3 | 43.3 | 54 | 62.5 | 71.3 | 75.7 | 73.8 | 66.5 | 55.3 | 45.3 | 36.2 | 22.3 | 30.56 | 30.6 | 40.82 | 50.2 | 59.36 | 64.04 | 63.86 | 59.2 | 46.4 | 34.2 | 28.4
VA | MARTINSVILLE | 38.5 | 41.3 | 48.4 | 58.1 | 65.6 | 73.7 | 77.1 | 76 | 68.8 | 57.9 | 47.5 | 40.4 | 31.6 | 25.52 | 26.8 | 39.02 | 45.9 | 62.78 | 65.84 | 66.74 | 57.6 | 44.24 | 31.3 | 28.8
IA | MASON CITY MUNICIPAL ARPT | 16.2 | 21 | 33.1 | 46.5 | 58.4 | 68.4 | 71.6 | 69.4 | 61.2 | 48.9 | 34.3 | 21.2 | 6.6 | 12.38 | 25.9 | 35.42 | 49.1 | 56.84 | 62.96 | 61.7 | 53.1 | 36.86 | 27.5 | 10.2
NY | MASSENA AP | 16.2 | 18.5 | 29.1 | 43.9 | 56.2 | 65.4 | 69.7 | 67.8 | 59.6 | 48 | 36.5 | 23.9 | 10.2 | 10.58 | 18.9 | 30.2 | 41.9 | 56.3 | 60.26 | 59.18 | 49.5 | 37.94 | 27.9 | 17.8
AL | MAXWELL AFB | 48.3 | 52.6 | 58.8 | 65.8 | 74.1 | 81 | 82.8 | 82.7 | 77.8 | 67.1 | 56 | 51.5 | 32.4 | 36.5 | 39.7 | 47.84 | 61.3 | 69.98 | 73.58 | 69.8 | 64.9 | 51.44 | 42.3 | 36.1
FL | MAYPORT NS | 56 | 58.4 | 62.9 | 68.9 | 75.8 | 80.8 | 82.7 | 82.5 | 79.8 | 73.3 | 63.7 | 58.4 | 42.3 | 46.94 | 58.5 | 56.3 | 67.1 | 70.52 | 72.68 | 71.96 | 70.5 | 60.98 | 56.3 | 44.8
TX | MC GREGOR (AWOS) | 48.1 | 51.4 | 57.8 | 66.5 | 74.5 | 81.6 | 84.7 | 85.2 | 78.2 | 67.8 | 57.4 | 49.1 | 34 | 35.42 | 34.2 | 44.42 | 62.6 | 69.08 | 64.58 | 65.66 | 59.2 | 46.22 | 43.2 | 37.8
QC | MC TAVISH | 17.6 | 20.1 | 30.5 | 44.4 | 57.4 | 66.9 | 71.3 | 69.7 | 61.7 | 49.3 | 37.5 | 24.7 | 7.3 | 9.32 | 18.3 | 28.76 | 41.2 | 53.78 | 58.46 | 57.92 | 51.4 | 39.38 | 30 | 14.5
OK | MCALESTER MUNICIPAL AP | 41.4 | 45.6 | 53.7 | 61.8 | 69.8 | 78.1 | 82.4 | 82 | 73.9 | 63.2 | 52.1 | 43.3 | 26.8 | 36.68 | 43 | 49.82 | 61.5 | 70.34 | 70.7 | 68 | 63.1 | 50.54 | 42.1 | 24.8
TX | MCALLEN MILLER INTL AP [EDINBURG - UT] | 61.9 | 65.6 | 71.1 | 76.9 | 82 | 86.1 | 86.9 | 87.4 | 83.2 | 77.3 | 69 | 62.6 | 50.5 | 56.12 | 55.8 | 62.06 | 68.7 | 71.78 | 71.42 | 74.66 | 72.3 | 63.68 | 57.6 | 47.3
MS | MCCOMB PIKE COUNTY AP | 49.6 | 52.9 | 59.1 | 65.7 | 73.3 | 79.4 | 81 | 81.3 | 76.8 | 67.1 | 57 | 51.2 | 40.1 | 43.52 | 45.9 | 58.64 | 62.2 | 69.44 | 71.42 | 73.22 | 72 | 56.84 | 46 | 38.7
KS | MCCONNELL AFB | 33.9 | 38.7 | 47.8 | 56.7 | 66.9 | 76.4 | 80.8 | 80.1 | 71.6 | 59.6 | 46.4 | 36.4 | 27.9 | 29.66 | 32.7 | 39.74 | 56.1 | 63.14 | 60.08 | 61.16 | 48.6 | 40.28 | 32.9 | 28.4
NE | MCCOOK MUNICIPAL | 29.5 | 31.7 | 41.9 | 51.1 | 61.9 | 72.4 | 78.7 | 76 | 66.8 | 52.9 | 40.3 | 29.4 | 22.5 | 19.04 | 27.3 | 33.8 | 47.5 | 55.94 | 60.26 | 60.26 | 55.8 | 35.6 | 26.1 | 15.8
AK | MCGRATH ARPT | -6.5 | 2.7 | 11 | 31.3 | 47.3 | 57.8 | 59.8 | 55 | 45 | 26.9 | 6.5 | -3.9 | -5.6 | -5.8 | 0.3 | 16.34 | 32.4 | 42.08 | 48.74 | 48.74 | 34 | 20.84 | -1.7 | -9.8
NJ | MCGUIRE AFB | 32.9 | 35 | 42.4 | 52.7 | 62.1 | 71.2 | 76.3 | 74.4 | 67.3 | 56.4 | 46.3 | 37.5 | 22.3 | 22.1 | 35.2 | 35.6 | 47.3 | 59 | 64.4 | 63.5 | 57.6 | 46.94 | 31.6 | 29.8
OR | MEDFORD ROGUE VALLEY INTL AP [ASHLAND - UO] | 40.1 | 44.2 | 48.2 | 52.5 | 59.8 | 66.1 | 75 | 73.9 | 68 | 55.9 | 44.9 | 38.9 | 32.4 | 34.88 | 37.6 | 39.56 | 42.3 | 46.4 | 48.74 | 50.36 | 46.2 | 40.64 | 36.9 | 33.6
AB | MEDICINE AP | 16.5 | 21.6 | 31.5 | 43.3 | 53.3 | 60.9 | 67.6 | 66.7 | 57.3 | 44.1 | 29.7 | 18.9 | 10.4 | 11.66 | 18.1 | 26.24 | 35.2 | 46.04 | 50 | 46.94 | 40.3 | 30.02 | 20.5 | 10.2
AK | MEKORYUK | 10.9 | 15.2 | 14.8 | 24.5 | 34.7 | 43.2 | 48.5 | 50.2 | 45.4 | 34.3 | 25.6 | 16.3 | 10.2 | 22.64 | 22.6 | 24.26 | 30.7 | 35.96 | 42.8 | 42.44 | 36.7 | 23.72 | 25.5 | 21.9
FL | MELBOURNE REGIONAL AP | 62.3 | 64.4 | 67.6 | 71.8 | 77.1 | 80.6 | 81.9 | 82 | 80.9 | 76.2 | 69.2 | 64.6 | 57.4 | 53.24 | 60.8 | 65.3 | 65.7 | 72.32 | 73.22 | 74.12 | 71.8 | 66.56 | 57.7 | 56.5
VA | MELFA/ACCOMACK ARPT | 40 | 41.2 | 47.6 | 56.9 | 65.9 | 74.7 | 79.2 | 77.1 | 70.7 | 61.4 | 50.8 | 43.2 | 27.9 | 28.04 | 29.7 | 46.76 | 57 | 64.22 | 68 | 70.7 | 59.2 | 51.8 | 42.8 | 37.2
TN | MEMPHIS INTERNATIONAL AP | 42.3 | 46.1 | 54.1 | 63.3 | 71.8 | 79.7 | 82.4 | 82.1 | 75.4 | 64.2 | 52.8 | 44.5 | 30.7 | 29.48 | 42.1 | 47.12 | 60.8 | 66.2 | 69.08 | 66.92 | 65.5 | 48.38 | 42.3 | 30
MI | MENOMINEE (AWOS) | 17.9 | 21 | 29.8 | 41.3 | 53.3 | 63.6 | 68.2 | 66.7 | 58.8 | 47.6 | 35.5 | 23.9 | 8.1 | 12.92 | 17.8 | 35.96 | 36.9 | 51.8 | 56.12 | 52.34 | 51.4 | 37.22 | 27.7 | 16.9
CA | MERCED/MACREADY FLD | 45.7 | 49.8 | 54.9 | 59.2 | 67.8 | 74.2 | 79.2 | 77.4 | 73.4 | 63.9 | 53.3 | 46.3 | 37.9 | 46.4 | 48.4 | 41.18 | 44.1 | 52.52 | 53.78 | 54.68 | 48.9 | 45.14 | 43.2 | 41.9
NV | MERCURY DESERT ROCK AP [SURFRAD] | 45.2 | 47.9 | 54.5 | 60.4 | 70 | 79.3 | 86.1 | 84.3 | 76.8 | 64.4 | 52 | 43.7 | 27.3 | 24.08 | 22.8 | 24.62 | 33.4 | 35.78 | 41.72 | 39.2 | 32.4 | 33.98 | 25.5 | 20.5
MS | MERIDIAN KEY FIELD | 46.6 | 50.1 | 57 | 64.1 | 71.9 | 78.5 | 80.9 | 80.7 | 75.5 | 64.7 | 54.5 | 48.4 | 34.3 | 36.5 | 45.7 | 51.8 | 61.3 | 67.1 | 72.5 | 69.8 | 63.3 | 52.88 | 44.8 | 35.6
MS | MERIDIAN NAAS | 46.4 | 50.2 | 57.5 | 63.9 | 72.3 | 79.4 | 81.4 | 80.8 | 75.8 | 64.7 | 53.8 | 49.3 | 34.2 | 40.46 | 47.5 | 55.4 | 64.6 | 67.46 | 71.96 | 71.42 | 64.6 | 52.7 | 49.1 | 38.3
FL | MIAMI INTL AP | 68.8 | 70.5 | 72.7 | 76.2 | 80.1 | 82.5 | 83.9 | 84.1 | 82.8 | 79.7 | 74.4 | 70.8 | 56.5 | 57.02 | 59.2 | 63.32 | 69.3 | 72.86 | 73.04 | 73.4 | 72.7 | 69.98 | 65.3 | 60.3
FL | MIAMI/KENDALL-TAMIA | 67.1 | 69 | 71.1 | 74.8 | 78.7 | 81.7 | 82.8 | 83.1 | 81.8 | 78.7 | 72.8 | 69.1 | 56.7 | 60.8 | 58.1 | 62.96 | 67.5 | 72.68 | 73.76 | 73.58 | 73 | 66.56 | 63.5 | 58.1
FL | MIAMI/OPA LOCKA | 66.9 | 69.7 | 72 | 75.5 | 79.2 | 82.2 | 83.2 | 83.9 | 82.4 | 79.4 | 73.1 | 70 | 56.8 | 58.1 | 60.4 | 60.44 | 67.8 | 73.04 | 77.36 | 73.58 | 75 | 68.72 | 63.7 | 57.9
AK | MIDDLETON ISLAND AUT | 35.5 | 35.3 | 35.8 | 40.6 | 44.8 | 50.4 | 54.6 | 55.3 | 51.6 | 44.8 | 38.8 | 36.8 | 28.9 | 30.92 | 24.8 | 24.44 | 30.9 | 44.06 | 28.76 | 37.76 | 34.9 | 33.44 | 27.9 | 24.6
PA | MIDDLETOWN HARRISBURG INTL AP | 31.2 | 33.4 | 42.1 | 53.2 | 63.1 | 72.4 | 76.8 | 74.8 | 67.3 | 55.5 | 44.9 | 35.6 | 14 | 21.02 | 25.3 | 40.64 | 48.7 | 63.68 | 62.78 | 63.86 | 57 | 44.06 | 35.6 | 21.4
TX | MIDLAND INTERNATIONAL AP | 44.9 | 49.1 | 56.5 | 65.1 | 74.1 | 81.6 | 82.5 | 81.6 | 74.7 | 65.3 | 53.2 | 45.3 | 25.7 | 29.12 | 28 | 40.64 | 48.2 | 57.02 | 59 | 58.46 | 57.2 | 47.12 | 40.6 | 29.5
MT | MILES CITY MUNICIPAL ARPT | 20.2 | 25.2 | 35.4 | 46.2 | 56.1 | 65.8 | 74.6 | 73.4 | 62.1 | 47.5 | 33 | 22.6 | 7.7 | 8.78 | 21 | 29.48 | 37.4 | 47.12 | 50.36 | 48.38 | 36.1 | 31.64 | 19 | 12.4
ME | MILLINOCKET MUNICIPAL AP | 15.9 | 19.1 | 28.6 | 41.1 | 53.5 | 62.9 | 68.6 | 66.5 | 58.8 | 46.6 | 35.1 | 23.3 | 13.1 | 7.88 | 21.9 | 28.58 | 42.4 | 51.44 | 55.4 | 55.58 | 53.4 | 37.22 | 25.5 | 18.3
NJ | MILLVILLE MUNICIPAL AP | 33.8 | 35 | 42.4 | 52.5 | 61.7 | 71.2 | 76.2 | 74.3 | 67.3 | 56 | 46 | 37.6 | 21.6 | 27.32 | 26.6 | 42.8 | 57.7 | 60.8 | 68.18 | 66.02 | 57.9 | 48.74 | 38.7 | 30.2
WI | MILWAUKEE MITCHELL INTL AP | 23.4 | 26.6 | 35.7 | 45.8 | 56.2 | 66.8 | 72.2 | 71.4 | 63.7 | 52.2 | 39.6 | 28.3 | 13.3 | 13.82 | 27.5 | 33.08 | 46.4 | 53.96 | 59.9 | 61.7 | 55 | 42.08 | 27.9 | 17.1
AK | MINCHUMINA | -4 | 3.5 | 11 | 31 | 48 | 58 | 60 | 55 | 45 | 26 | 6.8 | -1 | -16.6 | 5.18 | 9.3 | 24.26 | 28.9 | 39.02 | 43.7 | 41.72 | 28 | 26.24 | 5.2 | -24.2
TX | MINERAL WELLS MUNICIPAL AP | 45.4 | 47.9 | 57.5 | 65.9 | 72.9 | 80.7 | 83.8 | 84.4 | 76.5 | 65.9 | 55.8 | 46 | 33.8 | 37.58 | 29.7 | 41.9 | 59.5 | 67.82 | 67.46 | 66.74 | 60.6 | 57.92 | 38.7 | 34.5
MN | MINNEAPOLIS-ST PAUL INT ARP | 16 | 20.9 | 32.9 | 47.1 | 59 | 69.1 | 73.7 | 71.5 | 62.9 | 49.6 | 34.5 | 21.2 | 2.5 | 12.2 | 22.8 | 33.44 | 45.9 | 52.52 | 62.06 | 58.82 | 49.3 | 37.04 | 23.7 | 10.4
MN | MINNEAPOLIS/CRYSTAL | 15.8 | 20.2 | 32 | 46.8 | 58.2 | 67.7 | 73.7 | 70.9 | 62.5 | 48.8 | 34.8 | 20.9 | 7 | 6.26 | 19.9 | 30.56 | 42.1 | 54.68 | 60.8 | 55.22 | 53.8 | 33.62 | 27.3 | -0.4
WI | MINOCQUA/WOODRUFF | 14.7 | 16.7 | 27.7 | 41.1 | 53.4 | 62.7 | 66.9 | 65.1 | 57.3 | 45 | 32.7 | 19.1 | 6.4 | 12.38 | 19.4 | 32.54 | 35.8 | 51.8 | 55.76 | 56.12 | 49.1 | 38.66 | 27.1 | 5.5
ND | MINOT AFB | 8.6 | 15.1 | 26.4 | 40.3 | 54.1 | 63.3 | 67.8 | 67.8 | 57.6 | 42.9 | 26.1 | 12.8 | 14.7 | 16.52 | 19.8 | 29.3 | 37.8 | 50.72 | 56.66 | 52.16 | 43.7 | 33.08 | 28.2 | 19.2
ND | MINOT FAA AP | 12.3 | 16.8 | 27.6 | 42.3 | 54.3 | 63.7 | 69.4 | 68.7 | 59.1 | 44.7 | 28.5 | 16 | 2.7 | 11.12 | 18.7 | 29.48 | 42.6 | 49.28 | 50.18 | 52.34 | 41 | 30.92 | 21.7 | 8.4
MT | MISSOULA INTERNATIONAL AP | 25.7 | 29.4 | 38 | 44.7 | 53 | 59.8 | 69.1 | 67.6 | 58.4 | 44.9 | 32.8 | 24.7 | 21.4 | 24.62 | 24.1 | 29.12 | 37.6 | 44.06 | 47.12 | 45.14 | 39.2 | 33.26 | 28 | 20.8
SD | MITCHELL (AWOS) | 18.1 | 22.7 | 33.7 | 47.1 | 59 | 68.9 | 74.6 | 71.8 | 63.3 | 50.1 | 34.7 | 22.1 | 12.6 | 13.46 | 15.8 | 38.12 | 45.3 | 56.48 | 64.22 | 63.32 | 51.6 | 34.34 | 18.9 | 18.7
UT | MOAB/CANYONLANDS [UO] | 26.7 | 35 | 45.6 | 53.3 | 63.7 | 74.6 | 81.9 | 77.8 | 68.8 | 54.6 | 40.1 | 27.8 | 18.3 | 19.04 | 29.3 | 23.18 | 26.6 | 35.78 | 36.32 | 40.82 | 45.3 | 31.28 | 21.4 | 19.8
AL | MOBILE DOWNTOWN AP | 51 | 53.9 | 60.3 | 67.1 | 74.4 | 80.4 | 82 | 82.4 | 78.8 | 69.5 | 59.6 | 53 | 48.2 | 47.48 | 47.3 | 56.48 | 67.8 | 66.56 | 74.12 | 72.32 | 67.5 | 55.04 | 50.2 | 40.3
AL | MOBILE REGIONAL AP | 51.3 | 54.5 | 60.3 | 66.7 | 74.2 | 79.9 | 81.6 | 81.7 | 77.7 | 68.3 | 58.8 | 53 | 38.5 | 44.06 | 51.3 | 53.6 | 65.1 | 71.24 | 72.32 | 71.6 | 66.2 | 57.92 | 50.4 | 42.3
SD | MOBRIDGE | 16 | 20.3 | 31.1 | 44.9 | 55.8 | 65.9 | 73.6 | 72 | 62.2 | 47.3 | 32.4 | 19.5 | 10.2 | 18.68 | 22.3 | 32.36 | 42.3 | 52.7 | 62.6 | 58.28 | 47.5 | 29.48 | 19.2 | 7.2
CA | MODESTO CITY-COUNTY AP | 47 | 51.4 | 56.4 | 60.6 | 68.6 | 74.5 | 79.1 | 77.7 | 73.9 | 64.5 | 54.2 | 47.4 | 41.4 | 39.92 | 46.6 | 42.62 | 42.8 | 50.72 | 51.44 | 52.16 | 50.2 | 47.12 | 44.2 | 42.1
IL | MOLINE QUAD CITY INTL AP | 23.5 | 27.9 | 39.5 | 51.4 | 62 | 71.4 | 75 | 73.3 | 65.2 | 53.3 | 40.3 | 28 | 9.9 | 14.9 | 27.3 | 37.94 | 46.9 | 57.02 | 63.68 | 64.58 | 55.4 | 40.82 | 28.6 | 17.4
HI | MOLOKAI (AMOS) | 71.2 | 71 | 71.6 | 73 | 74.8 | 76.9 | 77.8 | 78.7 | 78.4 | 77.4 | 75.1 | 72.8 | 62.6 | 60.8 | 60.3 | 38.48 | 49.6 | 64.76 | 66.02 | 69.98 | 70 | 67.46 | 66.4 | 62.4
NB | MONCTON AP | 17.2 | 18.8 | 27.5 | 38.7 | 50 | 59.8 | 66.4 | 65.4 | 57.5 | 46.6 | 36 | 24.9 | 10.2 | 11.84 | 19.8 | 29.66 | 39.7 | 50.72 | 58.1 | 57.2 | 50 | 40.28 | 31.5 | 18.5
IN | MONROE CO | 30.1 | 33 | 43.8 | 55.2 | 63.8 | 72 | 74.5 | 73.7 | 66.3 | 55.1 | 44.5 | 33.8 | 21.4 | 24.44 | 34 | 45.86 | 54 | 62.42 | 66.92 | 69.08 | 57.7 | 45.86 | 40.3 | 22.8
LA | MONROE REGIONAL AP | 47.4 | 50.9 | 58 | 65.9 | 73.9 | 80.5 | 82.7 | 82.6 | 76.9 | 66.2 | 55.7 | 48.8 | 36.7 | 44.96 | 45.3 | 51.08 | 62.1 | 69.08 | 73.4 | 73.22 | 60.4 | 57.74 | 49.1 | 37.6
QC | MONT JOLI AB | 11.8 | 13.9 | 23.6 | 36.2 | 48.1 | 58.5 | 64.1 | 62.7 | 54.7 | 43.3 | 32.6 | 20.5 | 4.8 | 7.34 | 16 | 26.96 | 37.4 | 48.38 | 55.22 | 53.96 | 47.1 | 36.32 | 27 | 14.2
QC | MONT-ORFORD | 10.3 | 12.8 | 21.7 | 34.3 | 47.7 | 58.7 | 61.7 | 60.6 | 52.7 | 39.7 | 29.1 | 17.4 | 1.6 | 2.84 | 11.7 | 23.72 | 35.8 | 47.3 | 51.98 | 51.98 | 45 | 32.72 | 23.9 | 9.9
CA | MONTAGUE SISKIYOU COUNTY AP | 36.1 | 39.3 | 43.5 | 48.3 | 55.9 | 63.4 | 73.3 | 71.2 | 64.3 | 52.2 | 41 | 35.1 | 30.9 | 28.04 | 26.1 | 35.96 | 39.9 | 39.74 | 45.14 | 43.7 | 37 | 34.16 | 32.9 | 26.4
CA | MONTEREY NAF | 51.6 | 52.2 | 53.3 | 54.2 | 56.7 | 59.2 | 60.3 | 61 | 61.1 | 59 | 55 | 51.4 | 40.5 | 42.26 | 48 | 43.16 | 48 | 50.9 | 54.14 | 53.24 | 52.9 | 47.3 | 44.1 | 43.2
AL | MONTGOMERY DANNELLY FIELD | 47.7 | 51.6 | 58.2 | 65 | 72.8 | 79.5 | 82 | 81.8 | 76.8 | 66.2 | 55.9 | 49.5 | 34.5 | 38.12 | 48 | 55.22 | 61 | 68.36 | 71.96 | 70.7 | 64 | 50 | 45.5 | 35.2
IA | MONTICELLO MUNI | 20.5 | 23.9 | 37.3 | 48.6 | 60.4 | 69.9 | 73 | 71.2 | 62.3 | 50.5 | 38 | 24.8 | 11.8 | 16.52 | 30.9 | 42.62 | 48.6 | 57.92 | 62.42 | 64.4 | 55.4 | 45.14 | 28 | 16.2
NY | MONTICELLO(AWOS) | 22.9 | 25 | 34.1 | 45.7 | 55.9 | 64.5 | 68.6 | 67.3 | 59.3 | 48.6 | 37.7 | 28.1 | 19.2 | 15.08 | 18.1 | 37.04 | 42.1 | 54.14 | 59.9 | 57.56 | 53.2 | 38.66 | 29.3 | 16.7
VT | MONTPELIER AP | 17.7 | 19.8 | 29.1 | 42.1 | 53.8 | 63 | 67 | 65.5 | 57.7 | 46.3 | 35.4 | 24 | 19.9 | 6.8 | 22.8 | 32.54 | 37.9 | 54.32 | 54.32 | 58.46 | 52.5 | 41.36 | 30.6 | 15.3
QC | MONTREAL | 15.9 | 18.5 | 29 | 43.6 | 56.8 | 66.4 | 70.6 | 69 | 60.7 | 48.3 | 36.5 | 23.6 | 8.1 | 9.5 | 17.6 | 29.48 | 42.1 | 53.96 | 59.18 | 58.64 | 52.2 | 40.1 | 30.2 | 16.7
QC | MONTREAL-MIRABEL | 12.6 | 15.5 | 26.5 | 41.9 | 55 | 64.3 | 68.2 | 66.6 | 58.1 | 46 | 34 | 20.5 | 4.8 | 6.62 | 16.2 | 28.94 | 41.2 | 53.42 | 58.46 | 57.38 | 50.5 | 38.12 | 28.2 | 13.8
CO | MONTROSE CO. ARPT | 27.7 | 33.3 | 42.1 | 49 | 58.7 | 68.6 | 74.3 | 71.3 | 62.8 | 50.6 | 38.3 | 27.5 | 15.8 | 20.66 | 25.9 | 24.8 | 29.7 | 32.9 | 51.08 | 46.58 | 42.8 | 37.58 | 17.6 | 16.7
GA | MOODY AFB/VALDOSTA | 52.6 | 56.1 | 61.3 | 67.4 | 75.3 | 80.8 | 82.5 | 81.9 | 78 | 69.2 | 59.5 | 55 | 33.4 | 42.44 | 44.1 | 50.54 | 59.4 | 69.44 | 72.86 | 69.44 | 66 | 52.34 | 46 | 38.1
SK | MOOSE JAW AP | 10.9 | 12.9 | 24.1 | 40.3 | 51.2 | 59.8 | 66.1 | 64.5 | 55.6 | 41.1 | 26.4 | 13.2 | 2.1 | 3.74 | 16.3 | 27.5 | 34.5 | 46.94 | 54.32 | 51.08 | 42.1 | 29.48 | 18.5 | 4.1
MN | MORA MUNI (AWOS) | 12.1 | 16.5 | 28.6 | 42.7 | 54.3 | 63.9 | 68.6 | 66.4 | 57.7 | 45.5 | 32.6 | 18.4 | 9.3 | 0.32 | 25.3 | 30.74 | 39 | 49.64 | 58.64 | 60.44 | 55.4 | 38.48 | 26.4 | -1.1
WV | MORGANTOWN HART FIELD | 32.5 | 34.6 | 42.6 | 53.8 | 62 | 70 | 73.6 | 72.5 | 65.6 | 54.9 | 45 | 36.4 | 19.2 | 26.6 | 32.7 | 42.26 | 50.2 | 59.9 | 64.04 | 62.42 | 56.7 | 48.02 | 32.5 | 30.2
MN | MORRIS MUNI (AWOS) | 10.6 | 14.7 | 27.8 | 43.6 | 55.9 | 66 | 70 | 67.4 | 59.5 | 46.5 | 30.5 | 16.5 | 8.8 | 17.78 | 22.1 | 30.74 | 38.8 | 56.48 | 63.14 | 59.54 | 49.5 | 34.34 | 25.5 | 15.1
WA | MOSES LAKE GRANT COUNTY AP | 30.2 | 36 | 43.6 | 50.1 | 58.7 | 65.9 | 74.1 | 72.5 | 63.6 | 50.3 | 37.8 | 29.7 | 26.8 | 31.28 | 34.3 | 35.6 | 39.2 | 45.68 | 48.92 | 50.54 | 41.2 | 36.5 | 33.4 | 29.5
WI | MOSINEE/CENTRAL WI | 14.8 | 20.6 | 29.2 | 42.7 | 53.5 | 63.8 | 68.4 | 66.5 | 59.1 | 46.4 | 32 | 20.6 | 3 | 16.88 | 19.9 | 29.84 | 40.3 | 55.04 | 57.74 | 58.46 | 48.2 | 35.78 | 24.1 | 3.9
MI | MOUNT CLEMENS SELFRIDGE FLD | 25.1 | 28.1 | 35 | 46.9 | 57.8 | 68 | 72 | 70.5 | 63.1 | 51.9 | 40.5 | 30.7 | 30.2 | 30.56 | 31.5 | 31.64 | 42.6 | 54.86 | 56.84 | 58.82 | 49.6 | 39.92 | 33.3 | 29.7
IL | MOUNT VERNON (AWOS) | 31.3 | 35.1 | 44.6 | 55.6 | 64.7 | 73.7 | 77 | 75.8 | 67.5 | 55.8 | 44.4 | 34.8 | 25.9 | 24.26 | 26.1 | 36.14 | 60.4 | 61.52 | 60.26 | 65.48 | 62.6 | 47.12 | 37.9 | 26.4
NH | MOUNT WASHINGTON | 7.1 | 7 | 13.8 | 24.2 | 35.9 | 45.5 | 49.2 | 48.2 | 42.1 | 31.3 | 21.3 | 12.1 | 8.4 | 3.38 | 14.7 | 21.02 | 28.6 | 36.86 | 42.26 | 40.46 | 35.2 | 27.68 | 18.5 | 9.1
ID | MOUNTAIN HOME AFB | 30.5 | 35.6 | 43.2 | 49.1 | 58.1 | 65.9 | 75.9 | 74.6 | 65.2 | 51 | 38.4 | 29.5 | 28 | 24.44 | 29.8 | 30.38 | 32.7 | 33.44 | 32.72 | 35.42 | 33.4 | 29.3 | 28.2 | 25
CA | MOUNTAIN VIEW MOFFETT FLD NAS | 51 | 53.2 | 56 | 58.9 | 62.5 | 65.9 | 68 | 68.3 | 67.8 | 63.8 | 56.7 | 50.7 | 43.7 | 41.72 | 47.8 | 41.54 | 45.5 | 50.72 | 55.4 | 56.66 | 55.2 | 48.92 | 43.7 | 42.6
IA | MUSCATINE | 24.4 | 28.3 | 39.4 | 52.2 | 62.7 | 72.3 | 76.6 | 74 | 66 | 53.6 | 40.5 | 28.6 | 10.8 | 15.8 | 29.8 | 35.96 | 53.6 | 59.72 | 60.62 | 67.46 | 60.1 | 40.46 | 30.2 | 23.5
AL | MUSCLE SHOALS REGIONAL AP | 42.5 | 45.8 | 53.2 | 62.3 | 70.1 | 77.3 | 80.3 | 79.7 | 73.7 | 62.4 | 51.7 | 44.1 | 39.2 | 32.36 | 41.5 | 49.64 | 60.4 | 64.76 | 73.04 | 66.38 | 61 | 58.64 | 47.1 | 39.9
MI | MUSKEGON COUNTY ARPT | 25.8 | 26.9 | 34.9 | 46.1 | 56.8 | 66.3 | 70.6 | 69.5 | 61.9 | 50.8 | 40 | 30.7 | 18 | 15.26 | 25 | 31.28 | 44.4 | 54.68 | 61.52 | 62.24 | 53.2 | 41.72 | 30.2 | 22.6
SC | MYRTLE BEACH AFB | 46.8 | 49.7 | 55.4 | 62.4 | 70.2 | 76.7 | 80.6 | 78.7 | 74.6 | 65.3 | 56.4 | 48.8 | 29.5 | 37.76 | 49.3 | 50.9 | 60.1 | 66.2 | 73.22 | 70.88 | 65.1 | 48.74 | 49.8 | 34.3
TX | NACOGDOCHES (AWOS) | 48.1 | 51.8 | 58.1 | 65.5 | 73.5 | 79.7 | 82.3 | 82.3 | 76.7 | 66.3 | 56.1 | 49 | 34.7 | 38.3 | 36.9 | 48.92 | 61.5 | 70.52 | 69.26 | 69.08 | 60.8 | 55.76 | 47.8 | 39.9
MA | NANTUCKET MEMORIAL AP | 32.8 | 33.4 | 38.1 | 45.6 | 53.8 | 62 | 69 | 68.7 | 63.9 | 55.1 | 46.5 | 38.3 | 23 | 31.1 | 32.5 | 40.46 | 43.9 | 55.4 | 63.68 | 64.4 | 58.8 | 47.48 | 37.9 | 34.9
CA | NAPA CO. AIRPORT | 46.8 | 49.4 | 52.5 | 54.7 | 59.7 | 64.2 | 65.7 | 65.9 | 65 | 59.7 | 52.4 | 47 | 38.1 | 44.06 | 47.3 | 44.96 | 49.5 | 51.44 | 55.04 | 55.76 | 52.2 | 48.02 | 46.4 | 43.5
FL | NAPLES MUNICIPAL | 64.5 | 66.4 | 69.6 | 73.5 | 78.1 | 81.3 | 82.2 | 82.6 | 81.7 | 78 | 71.1 | 66.7 | 52 | 51.08 | 61 | 57.92 | 64.4 | 71.42 | 73.94 | 74.84 | 71.4 | 65.48 | 59.9 | 55.6
FL | NASA SHUTTLE FCLTY | 61.4 | 63.5 | 66.2 | 70.3 | 75.9 | 79.7 | 81.3 | 81.2 | 79.9 | 75.1 | 68.7 | 63.3 | 44.8 | 50.72 | 55.4 | 59.9 | 66.2 | 73.04 | 74.3 | 72.32 | 71.6 | 64.22 | 63.5 | 56.1
TN | NASHVILLE INTERNATIONAL AP | 39.2 | 42.8 | 50.7 | 60.2 | 68.4 | 76.3 | 79.8 | 79.2 | 72.2 | 60.8 | 49.8 | 41.8 | 27.3 | 26.24 | 40.3 | 42.98 | 56.3 | 64.76 | 68.72 | 68.72 | 60.3 | 50.18 | 35.4 | 31.1
MS | NATCHEZ/HARDY(AWOS) | 47.9 | 51.5 | 57.7 | 64.8 | 72.9 | 78.8 | 80.8 | 80.5 | 75.3 | 65.7 | 56.2 | 49.8 | 38.7 | 45.14 | 51.8 | 59.72 | 59.2 | 67.82 | 73.04 | 70.16 | 62.1 | 53.06 | 45.3 | 38.5
CA | NEEDLES AIRPORT | 55.2 | 58.1 | 65.7 | 72.6 | 83 | 92.4 | 98 | 95.7 | 89.1 | 75.9 | 63.6 | 53.6 | 32 | 32.54 | 26.2 | 35.42 | 33.3 | 38.3 | 51.08 | 54.32 | 45.1 | 41.72 | 33.3 | 28.6
NV | NELLIS AFB | 47.7 | 52 | 59.7 | 66.7 | 76.6 | 86 | 92 | 90.4 | 82.6 | 68.9 | 55.4 | 46.3 | 31.8 | 27.32 | 34 | 25.88 | 31.8 | 35.42 | 42.08 | 39.92 | 36.5 | 30.74 | 33.6 | 28.4
AK | NENANA MUNICIPAL AP | -4.7 | 1.7 | 9.9 | 31.6 | 48.2 | 59 | 60.6 | 55.6 | 44.7 | 25.2 | 4.2 | -2.9 | 5.9 | 3.02 | 9.3 | 13.64 | 29.5 | 30.02 | 34.88 | 31.1 | 23.4 | 15.8 | 13.8 | -15.7
MA | NEW BEDFORD RGNL | 30 | 32.1 | 38.2 | 47.7 | 56.9 | 65.9 | 72.1 | 70.5 | 63.4 | 52.8 | 43.4 | 35.4 | 16.3 | 17.06 | 30.4 | 35.06 | 47.1 | 57.2 | 61.88 | 60.8 | 55.9 | 44.42 | 37 | 30.6
NC | NEW BERN CRAVEN CO REGL AP | 45.1 | 47.2 | 53.5 | 62.1 | 69.6 | 77.3 | 80.5 | 79.1 | 74 | 64.2 | 54.8 | 47.9 | 40.1 | 37.76 | 49.5 | 51.8 | 58.5 | 67.46 | 71.24 | 71.06 | 65.8 | 60.08 | 40.3 | 44.4
CT | NEW HAVEN TWEED AIRPORT | 30.5 | 32 | 39 | 49.4 | 58.6 | 68.2 | 74.4 | 72.8 | 66.4 | 55.1 | 45.2 | 36.3 | 19.4 | 18.32 | 28.4 | 34.34 | 48 | 57.56 | 63.32 | 63.5 | 57.6 | 45.14 | 41 | 22.6
LA | NEW IBERIA NAAS | 53.1 | 55.9 | 62.5 | 69.4 | 76.2 | 81.3 | 82.4 | 83 | 79.1 | 70.2 | 60.9 | 54.2 | 38.8 | 51.44 | 45 | 57.92 | 66.7 | 72.32 | 74.48 | 74.12 | 68.5 | 56.66 | 54.5 | 45
LA | NEW ORLEANS ALVIN CALLENDER F | 53.4 | 56.4 | 61.9 | 67.9 | 75.2 | 80.5 | 81.9 | 82.2 | 78.7 | 69.9 | 59.9 | 55.9 | 44.1 | 49.82 | 48.4 | 60.98 | 70 | 72.86 | 74.48 | 70.88 | 69.1 | 56.66 | 56.5 | 46.9
LA | NEW ORLEANS INTL ARPT | 54.1 | 57.1 | 62.7 | 69.3 | 76.6 | 81.7 | 83.1 | 83.2 | 79.9 | 71.4 | 61.7 | 55.9 | 41 | 47.3 | 53.8 | 60.44 | 66 | 72.14 | 74.3 | 74.48 | 66.9 | 59.9 | 57 | 45.3
LA | NEW ORLEANS LAKEFRONT AP | 54.8 | 58.4 | 64.1 | 71 | 78.2 | 83.3 | 84.8 | 85.3 | 81.7 | 73.1 | 63.2 | 57.2 | 48.7 | 49.64 | 50.4 | 55.22 | 69.6 | 73.76 | 73.94 | 73.4 | 70.3 | 62.24 | 50.7 | 47.1
NC | NEW RIVER MCAF | 45.8 | 48 | 54.3 | 62.6 | 70.1 | 77.1 | 80.5 | 79 | 74 | 64.3 | 54.8 | 48.3 | 31.5 | 31.82 | 34.9 | 50 | 61.2 | 67.28 | 69.08 | 71.78 | 68 | 57.92 | 49.3 | 31.1
MN | NEW ULM MUNI (AWOS) | 14.4 | 18.9 | 31.4 | 46.2 | 58.1 | 68.2 | 71.9 | 69.4 | 61.5 | 48.9 | 33.5 | 19.9 | 13.5 | 10.22 | 16.9 | 37.04 | 43.7 | 55.4 | 63.32 | 64.04 | 53.6 | 39.38 | 27 | 21.6
NY | NEW YORK CENTRAL PRK OBS BELV | 33.5 | 35.6 | 42.7 | 53.4 | 62.3 | 71.3 | 76.5 | 75.1 | 68.4 | 57.3 | 47.5 | 38.5 | 15.8 | 21.74 | 28.4 | 39.38 | 52.2 | 57.92 | 65.48 | 62.96 | 56.7 | 43.16 | 34.9 | 23.4
NY | NEW YORK J F KENNEDY INT AR | 33.4 | 34.9 | 41.6 | 51.2 | 60.6 | 70.3 | 76.1 | 74.9 | 68.4 | 57.6 | 47.4 | 38.5 | 24.3 | 18.68 | 32.5 | 40.46 | 48.4 | 60.44 | 68.54 | 62.78 | 55.8 | 46.22 | 35.8 | 27
NY | NEW YORK LAGUARDIA ARPT | 34.2 | 35.9 | 42.6 | 53.2 | 62.8 | 72.7 | 78.1 | 76.8 | 69.8 | 59 | 48.6 | 39.5 | 22.1 | 17.42 | 30.6 | 38.48 | 45.5 | 57.56 | 67.82 | 64.04 | 56.3 | 43.52 | 36.1 | 25.9
NJ | NEWARK INTERNATIONAL ARPT | 33.3 | 35.3 | 42.9 | 53.6 | 63.3 | 73 | 78.1 | 76.3 | 69 | 57.7 | 47.4 | 38.2 | 17.4 | 22.64 | 30.2 | 37.76 | 48 | 57.92 | 63.68 | 62.78 | 55.4 | 45.14 | 32.4 | 24.4
VA | NEWPORT NEWS | 40.8 | 42.6 | 49.4 | 59 | 66.9 | 75.3 | 79.9 | 77.9 | 71.8 | 61.5 | 51.5 | 44.1 | 31.8 | 29.66 | 40.1 | 44.24 | 57.4 | 64.76 | 71.6 | 64.94 | 65.5 | 51.26 | 35.4 | 37.6
KS | NEWTON (AWOS) | 30.6 | 35.1 | 44.3 | 54.1 | 64.4 | 74.2 | 79.1 | 77.9 | 68.4 | 57.3 | 43.9 | 33.2 | 23.2 | 24.62 | 22.3 | 45.14 | 54.3 | 57.74 | 64.58 | 60.8 | 60.3 | 39.02 | 25.5 | 25.9
IA | NEWTON MUNI | 22.8 | 25.7 | 37.9 | 50.7 | 61.3 | 70.7 | 75.1 | 72.6 | 64.2 | 52.6 | 38.9 | 26.4 | 20.8 | 17.42 | 37.8 | 43.88 | 50.2 | 62.42 | 64.22 | 60.8 | 52.7 | 47.12 | 26.8 | 18.1
NY | NIAGARA FALLS AF | 25 | 25.8 | 33.7 | 45.8 | 57.1 | 67.2 | 71.5 | 70 | 62.3 | 51.2 | 40.3 | 30.8 | 25.7 | 17.96 | 19.2 | 39.02 | 38.5 | 59.72 | 60.08 | 59.54 | 55.9 | 42.8 | 37.8 | 24.4
QC | NICOLET | 12.5 | 15.2 | 26.3 | 41.3 | 55 | 64.2 | 68.4 | 66.3 | 58.5 | 46.8 | 34.9 | 21.4 | 4.1 | 6.98 | 16.7 | 29.3 | 42.1 | 53.96 | 59.36 | 58.46 | 51.3 | 39.2 | 29.3 | 12.9
AK | NOME MUNICIPAL ARPT | 4.9 | 7.4 | 9.3 | 22 | 36.5 | 47.6 | 51.9 | 50.5 | 43.1 | 29.6 | 17.4 | 8.2 | 8.2 | -0.22 | 0.3 | 10.22 | 31.8 | 40.28 | 45.68 | 46.58 | 36.7 | 20.48 | 10.8 | 0.9
VA | NORFOLK INTERNATIONAL AP | 42.1 | 43.7 | 50.2 | 59.4 | 67.3 | 75.8 | 80.2 | 78.4 | 72.9 | 62.8 | 52.9 | 45.6 | 26.1 | 26.96 | 34.7 | 46.22 | 54.9 | 63.68 | 68.9 | 69.44 | 61.5 | 51.8 | 43.5 | 36.7
NE | NORFOLK KARL STEFAN MEM ARPT | 23 | 27.4 | 38.1 | 49.6 | 60.8 | 70.5 | 75.1 | 73.1 | 64.6 | 51.7 | 37.1 | 25.6 | 8.4 | 16.34 | 24.4 | 35.6 | 45.3 | 55.4 | 60.8 | 62.42 | 53.4 | 37.58 | 23.4 | 11.3
VA | NORFOLK NAS | 42.9 | 44.5 | 51 | 60.5 | 68.5 | 76.8 | 81.2 | 79.3 | 74 | 64 | 53.9 | 46.7 | 31.8 | 31.46 | 43.3 | 50.9 | 55.4 | 64.4 | 68.72 | 69.98 | 61.3 | 51.44 | 38.7 | 38.5
MA | NORTH ADAMS | 23.1 | 26.4 | 34.1 | 46.2 | 56.7 | 65.3 | 69.1 | 67.6 | 60.8 | 49.5 | 39.7 | 29.8 | 17.1 | 20.3 | 27.7 | 33.98 | 43 | 55.22 | 57.38 | 58.64 | 55.2 | 42.26 | 33.1 | 19.8
ON | NORTH BAY AP | 10.4 | 13.6 | 24.5 | 38.8 | 52.6 | 62.1 | 65.9 | 64.3 | 55.8 | 43.7 | 31.2 | 18.1 | 4.8 | 6.08 | 13.6 | 25.52 | 38.7 | 51.62 | 55.94 | 55.58 | 49.8 | 37.4 | 27.3 | 13.3
OR | NORTH BEND MUNI AIRPORT | 46.7 | 47.1 | 47.9 | 49.7 | 53.5 | 56.8 | 59.2 | 59.7 | 58.2 | 54.1 | 49.6 | 45.9 | 40.1 | 42.08 | 41.9 | 42.98 | 47.7 | 50.18 | 51.26 | 53.42 | 50.5 | 48.74 | 45 | 40.3
SC | NORTH MYRTLE BEACH-GRAND STRAND FIELD | 46 | 50 | 55 | 62 | 71 | 77 | 80 | 79 | 75 | 66 | 56 | 49 | 30.9 | 42.98 | 48.6 | 53.42 | 60.1 | 68.54 | 72.68 | 69.26 | 64.8 | 52.34 | 49.1 | 36.9
NE | NORTH PLATTE REGIONAL AP | 26 | 29.4 | 38.8 | 47.7 | 58.3 | 68.7 | 74.8 | 72.8 | 63.3 | 49.7 | 36.3 | 26.8 | 13.8 | 17.42 | 24.6 | 32.54 | 43.9 | 54.14 | 58.82 | 60.26 | 47.5 | 33.8 | 25.2 | 17.4
BC | NORTH VANCOUVER | 41.1 | 42.3 | 45.2 | 50.1 | 56.1 | 60.9 | 65.7 | 65.5 | 60.2 | 51.7 | 45 | 41 | 32.2 | 33.26 | 36.7 | 39.56 | 45.3 | 50.36 | 54.5 | 54.68 | 51.4 | 44.96 | 38.8 | 31.5
ME | NORTHERN AROOSTOOK | 9.9 | 13.9 | 23.7 | 36.8 | 50.5 | 59.4 | 64.7 | 62.9 | 54.7 | 42.9 | 30.7 | 17.9 | 5.5 | 4.82 | 18.7 | 26.24 | 36.1 | 45.14 | 57.2 | 53.6 | 50.7 | 31.28 | 23.4 | 8.8
AK | NORTHWAY AIRPORT | -14.5 | -4.6 | 6.9 | 29.6 | 46.1 | 56.4 | 58.8 | 54.2 | 42.3 | 22 | -2 | -11.8 | -16.4 | -8.32 | 2.1 | 8.42 | 29.1 | 37.04 | 46.94 | 39.92 | 29.3 | 22.64 | -8.5 | -13.9
MA | NORWOOD MEMORIAL | 27.2 | 29.5 | 37.1 | 47.9 | 57.4 | 66.6 | 71.9 | 70.1 | 62.5 | 51.3 | 42.4 | 33 | 13.3 | 14.72 | 28.9 | 36.86 | 44.6 | 59 | 60.98 | 64.22 | 59.4 | 37.94 | 33.8 | 27.9
MI | OAKLAND CO INTL | 24.1 | 25.9 | 34.7 | 47.3 | 58.1 | 68.1 | 72 | 70.3 | 62.5 | 51.1 | 39.2 | 28.8 | 20.5 | 12.92 | 30.6 | 39.38 | 45.9 | 61.34 | 61.7 | 60.44 | 55.2 | 43.88 | 37.2 | 24.8
CA | OAKLAND METROPOLITAN ARPT | 49.9 | 52.4 | 55.1 | 57.1 | 59.8 | 62.2 | 63.6 | 64.4 | 64.6 | 61.9 | 55.4 | 50.2 | 41.5 | 43.34 | 48 | 47.3 | 51.3 | 51.8 | 54.14 | 54.5 | 54.5 | 51.62 | 46.4 | 43.9
FL | OCALA MUNI (AWOS) | 56.7 | 58.4 | 63.1 | 68.2 | 75.2 | 79.7 | 81 | 80.7 | 79 | 71.9 | 63.7 | 58.1 | 47.7 | 45.68 | 59.5 | 54.68 | 61.2 | 69.26 | 71.24 | 71.06 | 68 | 62.06 | 50.7 | 38.3
VA | OCEANA NAS | 42 | 43.5 | 49.8 | 58.6 | 66.4 | 74.8 | 79.3 | 77.5 | 72 | 62.4 | 52.4 | 45.4 | 29.1 | 36.86 | 43.3 | 47.66 | 56.7 | 67.46 | 69.62 | 70.88 | 64 | 53.96 | 43.5 | 31.6
IA | OELWEN | 19.5 | 22.7 | 35.8 | 49.1 | 60.3 | 69.7 | 72.1 | 70.4 | 63.8 | 49.8 | 36.5 | 24.7 | 18.3 | 24.08 | 32.4 | 39.2 | 49.1 | 60.26 | 60.26 | 63.5 | 50.9 | 44.6 | 31.1 | 19.4
UT | OGDEN HILL AFB | 28.5 | 32.8 | 42.2 | 48.3 | 58 | 67.3 | 76.7 | 75.1 | 65.1 | 51.5 | 38.7 | 29.3 | 23.7 | 22.64 | 26.1 | 28.22 | 32 | 33.98 | 34.7 | 35.78 | 33.4 | 28.22 | 28.4 | 24.1
UT | OGDEN HINKLEY AIRPORT | 28 | 32.7 | 42.7 | 49.2 | 58.4 | 68.2 | 78.9 | 75.7 | 65.8 | 52.3 | 40.1 | 29.8 | 19.2 | 23.18 | 21.6 | 31.28 | 32 | 38.48 | 40.46 | 49.28 | 35.2 | 36.32 | 27.7 | 24.1
OH | OHIO STATE UNIVERSI | 28.8 | 31.2 | 40.7 | 52.8 | 62.7 | 70.9 | 74.1 | 72.9 | 65.8 | 53.8 | 43.2 | 33.1 | 23 | 23 | 33.1 | 40.64 | 46 | 60.26 | 66.02 | 69.44 | 56.8 | 44.96 | 35.8 | 26.2
OK | OKLAHOMA CITY TINKER AFB | 39.3 | 43.8 | 51.9 | 60.5 | 69 | 77.5 | 82.2 | 81.7 | 73.5 | 62.3 | 50.4 | 41 | 32.4 | 30.92 | 28.9 | 37.04 | 57.9 | 66.56 | 66.56 | 64.58 | 60.3 | 44.24 | 38.1 | 30.6
OK | OKLAHOMA CITY WILL ROGERS WOR | 39.3 | 43.5 | 51.8 | 60.3 | 69.3 | 77.8 | 82.4 | 81.8 | 73.5 | 62.1 | 50.2 | 40.7 | 18.3 | 32.36 | 38.3 | 48.56 | 56.7 | 64.76 | 65.48 | 64.22 | 59.7 | 49.28 | 40.1 | 28.2
OK | OKLAHOMA CITY/WILEY | 39.1 | 43.2 | 51.6 | 60.3 | 69.6 | 78.3 | 83.2 | 82.5 | 73.7 | 62.1 | 50.1 | 40.4 | 29.8 | 28.76 | 36 | 36.68 | 57.9 | 63.14 | 65.66 | 62.6 | 59.7 | 43.7 | 36.9 | 30.2
KS | OLATHE-JOHNSON COUNTY INDUSTRIAL AP | 31 | 34 | 45 | 55 | 65 | 75 | 79 | 78 | 70 | 57 | 45 | 34 | 21.6 | 24.62 | 36.7 | 47.12 | 57 | 65.3 | 67.64 | 64.04 | 60.3 | 44.6 | 34.5 | 19.2
KS | OLATHE/JOHNSON CO. | 30.6 | 34.7 | 45.1 | 55.6 | 65 | 73.8 | 79 | 77.8 | 68.8 | 57.2 | 44.9 | 33.5 | 22.6 | 23.72 | 31.1 | 46.58 | 52.5 | 62.06 | 66.2 | 66.38 | 64.2 | 45.14 | 36.9 | 23.2
WA | OLYMPIA AIRPORT | 39.6 | 40.8 | 44.3 | 48.2 | 54 | 58.8 | 64.1 | 64.2 | 59.4 | 50.5 | 43.4 | 38.8 | 37.9 | 34.34 | 37.9 | 40.82 | 45 | 49.46 | 52.16 | 51.44 | 51.8 | 47.12 | 42.3 | 36.9
NE | OMAHA EPPLEY AIRFIELD | 23.7 | 28.7 | 40 | 51.9 | 62.8 | 72.6 | 77 | 75 | 66.3 | 53.9 | 39.5 | 27.5 | 17.6 | 16.16 | 25.3 | 42.62 | 52.5 | 64.76 | 65.3 | 68.9 | 57.4 | 42.44 | 32.9 | 20.5
NE | OMAHA WSFO | 27.3 | 28.5 | 41 | 52.2 | 63.8 | 73 | 75.7 | 73.3 | 65.6 | 52.4 | 37.5 | 27.5 | 11.3 | 16.16 | 27.9 | 43.16 | 43.9 | 60.44 | 65.3 | 64.58 | 52 | 39.56 | 22.6 | 15.6
NE | ONEILL-BAKER FIELD | 24 | 27 | 37 | 48 | 58 | 69 | 75 | 72 | 64 | 50 | 37 | 26 | 7 | 17.6 | 25 | 37.04 | 45.7 | 54.14 | 61.34 | 57.38 | 48.6 | 35.24 | 20.3 | 7.9
IA | ORANGE CITY | 19.7 | 24.1 | 35.7 | 49.6 | 60.7 | 70.5 | 74.7 | 72.4 | 64.3 | 51 | 36.5 | 22.5 | 12.6 | 18.14 | 37.2 | 37.58 | 44.4 | 59 | 64.94 | 67.64 | 52.3 | 34.88 | 25.3 | 21.7
NE | ORD-SHARP FIELD | 25 | 26 | 39 | 49 | 59 | 70 | 75 | 73 | 64 | 50 | 37 | 26 | 16.7 | 17.42 | 26.2 | 38.84 | 50.5 | 57.2 | 61.7 | 58.1 | 46.9 | 37.94 | 24.8 | 21.9
FL | ORLANDO EXECUTIVE AP | 61.4 | 63.9 | 67.4 | 72.2 | 77.9 | 81.5 | 83.1 | 83.1 | 81.3 | 75.9 | 68.3 | 63.4 | 42.8 | 52.34 | 58.5 | 62.96 | 66.9 | 70.52 | 72.5 | 72.68 | 70.9 | 69.08 | 55 | 48.9
FL | ORLANDO INTL ARPT | 61 | 63.5 | 67.1 | 71.8 | 77.4 | 81 | 82.5 | 82.6 | 80.8 | 75.2 | 67.9 | 63.1 | 51.1 | 50.9 | 53.4 | 59.36 | 66 | 72.5 | 73.58 | 74.12 | 71.4 | 66.38 | 61.2 | 53.8
FL | ORLANDO SANFORD AIRPORT | 60 | 62.4 | 66.2 | 71.5 | 77.2 | 81.2 | 82.8 | 82.8 | 80.6 | 74.8 | 67.4 | 62.2 | 51.1 | 52.7 | 47.7 | 55.4 | 63.1 | 68.72 | 73.04 | 72.68 | 69.1 | 64.94 | 54.9 | 50
MN | ORR | 6.5 | 11.7 | 24.3 | 38.7 | 51.2 | 60.7 | 65.5 | 63.6 | 55.3 | 42.7 | 26.8 | 12.7 | -8.5 | 9.86 | 1.8 | 23 | 38.1 | 52.88 | 53.6 | 54.68 | 50.7 | 29.48 | 18.7 | 3
MI | OSCODA WURTSMITH AFB | 21.9 | 23.1 | 31 | 42.4 | 53.5 | 63.8 | 68.4 | 67.2 | 59.8 | 48.4 | 37.7 | 26.9 | 22.6 | 14 | 26.1 | 35.42 | 39.4 | 54.14 | 60.62 | 55.76 | 51.4 | 41.54 | 30 | 18.5
MA | OTIS ANGB | 30.6 | 31.8 | 37.3 | 45.9 | 55.3 | 64.8 | 70.4 | 69.8 | 62.8 | 52.9 | 44.7 | 35.8 | 28 | 25.88 | 30.6 | 31.64 | 43.3 | 55.94 | 62.24 | 68.18 | 51.6 | 46.4 | 29.8 | 27.9
ON | OTTAWA | 14.5 | 17.6 | 28.3 | 43.2 | 56.3 | 65.8 | 69.7 | 68 | 59.4 | 47.2 | 35.2 | 22 | 7 | 8.6 | 17.1 | 29.12 | 41.9 | 54.32 | 58.46 | 57.74 | 51.6 | 39.38 | 29.5 | 16
IA | OTTUMWA INDUSTRIAL AP | 23.4 | 27.9 | 39.5 | 51.3 | 61.9 | 71.4 | 75.1 | 73.3 | 64.8 | 53.2 | 39.8 | 27.7 | 17.2 | 15.8 | 30.6 | 42.44 | 48 | 62.96 | 66.56 | 59.9 | 53.4 | 41.54 | 33.1 | 7
MN | OWATONNA (AWOS) | 14.9 | 18.8 | 31.8 | 46.3 | 58.1 | 68.1 | 71.8 | 69.3 | 61.5 | 49 | 34.6 | 21 | 11.3 | 13.1 | 28.6 | 32.9 | 43.2 | 58.82 | 60.98 | 62.42 | 54 | 35.6 | 26.2 | 19.2
CT | OXFORD (AWOS) | 26.3 | 28.5 | 35.9 | 46.9 | 55.9 | 65.9 | 70.2 | 68.8 | 61.6 | 50.3 | 41.3 | 31.4 | 14.7 | 22.1 | 20.5 | 35.6 | 45.1 | 57.38 | 61.88 | 61.16 | 57.9 | 45.14 | 30.9 | 22.3
CA | OXNARD AIRPORT | 55.8 | 55 | 56.1 | 57.1 | 60.2 | 62.9 | 65.7 | 65.5 | 64.9 | 62.5 | 58.8 | 55.1 | 41.2 | 40.82 | 50.4 | 48.74 | 55.2 | 52.34 | 57.74 | 56.12 | 57 | 54.5 | 42.8 | 40.8
KY | PADUCAH BARKLEY REGIONAL AP | 35.9 | 39.9 | 48.7 | 58.6 | 67.6 | 75.9 | 78.8 | 77.6 | 70 | 59 | 47.8 | 38.7 | 30.4 | 26.1 | 38.1 | 47.3 | 56.3 | 66.6 | 69.8 | 67.1 | 56.3 | 49.6 | 41 | 36.1
AZ | PAGE MUNI (AMOS) | 37.1 | 42.3 | 50.8 | 58.1 | 68.7 | 78.6 | 84.4 | 81 | 73.7 | 60.2 | 46.3 | 36.3 | 20.7 | 24.62 | 28.2 | 22.82 | 22.1 | 32 | 38.48 | 50.36 | 39.7 | 35.6 | 30.4 | 19
TX | PALACIOS MUNICIPAL AP | 55.3 | 58.4 | 63.8 | 70.4 | 77.2 | 82.8 | 84.2 | 84.4 | 80.3 | 72.8 | 63.6 | 56.8 | 45.7 | 49.82 | 48.6 | 62.24 | 72 | 75.2 | 75.38 | 74.84 | 68.4 | 61.7 | 54.9 | 48
CA | PALM SPRINGS INTL | 59.1 | 60.4 | 66.7 | 71.3 | 80 | 87.3 | 93.6 | 92.6 | 87.7 | 76.7 | 65.9 | 57.3 | 30 | 35.96 | 41.7 | 44.78 | 49.1 | 50.9 | 56.12 | 55.94 | 48.7 | 44.96 | 32.4 | 23.2
CA | PALM SPRINGS THERMAL AP | 55.2 | 58.5 | 65.2 | 71.1 | 79.2 | 86.1 | 91.6 | 90.6 | 85.3 | 73.8 | 61.8 | 53.5 | 36.7 | 42.26 | 44.4 | 37.4 | 45.7 | 52.88 | 57.92 | 60.26 | 58.3 | 42.62 | 36.9 | 32
CA | PALMDALE AIRPORT | 45.8 | 48.1 | 53.9 | 58.8 | 67.9 | 75.2 | 82.3 | 81.6 | 75.1 | 63.6 | 52.4 | 44.8 | 25.2 | 25.52 | 25.3 | 32.18 | 38.8 | 42.26 | 46.94 | 42.26 | 43.2 | 37.22 | 30.2 | 19.9
AK | PALMER MUNICIPAL | 16 | 21.4 | 25.5 | 37.8 | 48.7 | 55.7 | 58.5 | 56 | 48.4 | 35.7 | 21.9 | 17.7 | 22.6 | 25.16 | 19.9 | 26.96 | 34.7 | 36.86 | 47.3 | 48.38 | 34.3 | 26.42 | 29.8 | 19.2
FL | PANAMA CITY BAY CO | 54 | 56 | 62.1 | 68.2 | 75.7 | 81.1 | 82.8 | 82.5 | 79.5 | 71.8 | 62.6 | 55.7 | 48.2 | 49.64 | 48.9 | 54.5 | 70.3 | 70.88 | 74.3 | 74.66 | 72.5 | 57.02 | 57.2 | 44.2
MN | PARK RAPIDS MUNICIPAL AP | 7.7 | 13.3 | 25.2 | 41.2 | 53.6 | 63.3 | 68.8 | 66.7 | 57.5 | 43.8 | 28 | 13.9 | 5.2 | 8.96 | 14.7 | 30.74 | 43.7 | 54.14 | 57.74 | 54.14 | 51.3 | 32.72 | 23.4 | 9.5
WV | PARKERSBURG WOOD COUNTY AP | 32.7 | 35.2 | 43.6 | 54.7 | 62.9 | 70.7 | 74.3 | 73.1 | 66.1 | 54.9 | 44.7 | 36.2 | 16.9 | 23 | 32.2 | 43.34 | 52.3 | 64.22 | 66.74 | 64.94 | 58.1 | 45.5 | 36 | 25
WA | PASCO | 35.2 | 39.1 | 46.3 | 53 | 61.1 | 67.7 | 75.2 | 73.6 | 64.7 | 52.3 | 41.2 | 33.8 | 31.1 | 28.94 | 36.7 | 42.08 | 42.4 | 50.54 | 51.26 | 51.44 | 45.1 | 38.84 | 37.6 | 30.9
CA | PASO ROBLES MUNICIPAL ARPT | 48.4 | 50.5 | 54 | 57.4 | 63.9 | 69.2 | 73.7 | 73.8 | 70.3 | 62.5 | 53.3 | 47.2 | 38.5 | 39.2 | 46 | 39.92 | 43 | 46.22 | 48.74 | 48.02 | 48.2 | 41.18 | 41 | 36.9
LA | PATTERSON MEMORIAL | 54.1 | 56.6 | 62.3 | 68.3 | 75.2 | 80.3 | 81.9 | 82.2 | 78.9 | 69.7 | 60.4 | 55 | 42.4 | 48.38 | 46.4 | 55.94 | 65.1 | 70.88 | 75.2 | 72.14 | 68.7 | 42.8 | 49.1 | 37.4
MD | PATUXENT RIVER NAS | 37.1 | 39.1 | 45.9 | 56.1 | 65.7 | 74.2 | 78.6 | 76.7 | 70.2 | 59.8 | 49.4 | 41.5 | 34.7 | 33.98 | 40.6 | 47.12 | 60.1 | 63.68 | 69.08 | 70.88 | 63 | 50.18 | 42.3 | 30.7
RI | PAWTUCKET (AWOS) | 27.8 | 29.4 | 36.9 | 47.7 | 56.4 | 65.4 | 70.8 | 69.2 | 61.9 | 51.4 | 41.9 | 32.8 | 13.8 | 16.88 | 20.1 | 35.6 | 45.3 | 54.5 | 58.64 | 59.9 | 56.8 | 41.18 | 24.4 | 23.5
NH | PEASE INTL TRADEPOR | 25.3 | 28.3 | 35.7 | 46.6 | 56 | 65.8 | 71.4 | 70.3 | 62.5 | 51.5 | 41.5 | 31.8 | 23 | 17.06 | 25.3 | 29.66 | 41.4 | 53.78 | 58.46 | 58.64 | 52.3 | 40.1 | 30.2 | 24.4
MI | PELLSTON EMMET COUNTY AP | 18.6 | 19 | 27.7 | 40.7 | 52.8 | 62.6 | 66.3 | 65 | 57.2 | 46.2 | 35.7 | 25.3 | 18.5 | 18.68 | 27.9 | 33.98 | 43.2 | 53.06 | 59.9 | 57.56 | 52.9 | 39.02 | 29.8 | 19.2
OR | PENDLETON E OR REGIONAL AP | 35.4 | 38.5 | 45 | 50.4 | 57.8 | 64.4 | 73.3 | 72.1 | 64.5 | 51.9 | 41.2 | 34.3 | 26.1 | 31.46 | 33.6 | 37.4 | 39.6 | 43.88 | 43.7 | 41.36 | 40.1 | 36.14 | 33.4 | 28.4
FL | PENSACOLA FOREST SHERMAN NAS | 52.3 | 55.4 | 60.4 | 66.7 | 74.4 | 80.4 | 82.1 | 81.9 | 78.7 | 69.6 | 60 | 55.1 | 41.7 | 42.26 | 52 | 62.06 | 68.2 | 70.88 | 74.66 | 73.76 | 69.3 | 60.08 | 49.1 | 43
FL | PENSACOLA REGIONAL AP | 52.6 | 55.6 | 61.3 | 67.4 | 75.2 | 81 | 82.4 | 82.2 | 78.9 | 70 | 60.4 | 54.4 | 43 | 48.38 | 53.2 | 62.42 | 70.7 | 70.34 | 74.12 | 73.22 | 64.8 | 63.14 | 55.9 | 50.4
BC | PENTICTON AP | 30.8 | 33.6 | 40.6 | 48.1 | 56.9 | 63.3 | 70.5 | 69.1 | 60 | 48.1 | 37.7 | 30.9 | 24.6 | 25.52 | 27.9 | 31.82 | 38.8 | 45.32 | 48.2 | 48.02 | 43.5 | 36.86 | 30.6 | 24.8
IL | PEORIA GREATER PEORIA AP | 25.5 | 29.9 | 41 | 52.5 | 62.6 | 71.9 | 75.5 | 74 | 66.1 | 54.2 | 41.6 | 30 | 14.7 | 17.78 | 28.8 | 41.9 | 48.6 | 57.92 | 64.04 | 64.22 | 55 | 41.9 | 30.4 | 22.6
ON | PETERBOROUGH AP | 18.4 | 20.6 | 29.6 | 42.9 | 54.5 | 63.8 | 67.4 | 65.7 | 58.1 | 46.9 | 35.9 | 25.2 | 12 | 12.38 | 19.8 | 31.46 | 43.2 | 55.22 | 59 | 58.64 | 52.3 | 40.1 | 31.3 | 19.2
AK | PETERSBURG | 30.5 | 33 | 34.4 | 40.6 | 47.4 | 53.3 | 55.9 | 55.3 | 50.5 | 43.4 | 35.8 | 32.2 | 23.5 | 28.4 | 26.1 | 32.54 | 35.4 | 46.76 | 50.36 | 49.46 | 42.4 | 36.32 | 30.2 | 25.7
PA | PHILADELPHIA INTERNATIONAL AP | 34.3 | 36.2 | 44.1 | 54.8 | 64.4 | 73.7 | 78.7 | 76.9 | 69.7 | 58.4 | 47.9 | 38.8 | 19 | 20.12 | 31.1 | 37.94 | 50.2 | 60.8 | 65.66 | 63.5 | 58.3 | 42.8 | 36.1 | 24.8
PA | PHILADELPHIA NE PHILADELPHIA | 33.6 | 35.5 | 42.9 | 53.6 | 63.1 | 72.3 | 77.4 | 75.5 | 68.2 | 56.8 | 46.7 | 38 | 17.8 | 18.68 | 33.1 | 44.06 | 48.4 | 58.46 | 64.76 | 65.66 | 57.6 | 45.5 | 35.4 | 29.5
WI | PHILLIPS/PRICE CO. | 12.6 | 16.5 | 28 | 41.4 | 53.9 | 63.5 | 67.5 | 65.9 | 57.5 | 45.4 | 31.3 | 18.6 | 8.4 | 3.74 | 17.8 | 35.6 | 37 | 51.26 | 58.46 | 58.46 | 53.8 | 35.24 | 28.4 | 17.4
AZ | PHOENIX SKY HARBOR INTL AP | 56.7 | 59.5 | 65.6 | 72.6 | 81.9 | 90.9 | 94.8 | 93.6 | 88.8 | 76.9 | 64.6 | 55.6 | 28 | 39.38 | 36.5 | 29.12 | 36.1 | 42.62 | 56.48 | 56.3 | 48 | 43.52 | 35.4 | 32.9
SD | PIERRE MUNICIPAL AP | 20.1 | 24.5 | 34.7 | 46.7 | 57.7 | 67.8 | 75.2 | 73.6 | 64.2 | 49.4 | 34.3 | 23 | 9.3 | 14.9 | 26.1 | 33.8 | 43.7 | 57.02 | 57.38 | 58.28 | 46 | 33.08 | 25.9 | 9.5
AR | PINE BLUFF FAA AP | 43.5 | 47.3 | 54.8 | 63.8 | 72 | 79.7 | 82.3 | 81.5 | 74.8 | 64 | 53 | 45.3 | 31.3 | 38.84 | 35.4 | 55.22 | 64.4 | 68.36 | 72.32 | 70.16 | 67.8 | 55.94 | 40.5 | 27
MN | PIPESTONE (AWOS) | 15.3 | 19.4 | 31.2 | 44.9 | 57.1 | 67.3 | 71.9 | 69.3 | 61.2 | 48.6 | 32.9 | 20.1 | 6.6 | 7.16 | 26.8 | 31.1 | 40.3 | 56.48 | 65.84 | 61.52 | 53.4 | 32.72 | 25.5 | 6.8
NC | PITT GREENVILLE ARP | 43.2 | 45.6 | 52.4 | 61.5 | 69.5 | 77.3 | 80.3 | 79 | 72.8 | 62.4 | 52.2 | 45.5 | 29.1 | 27.68 | 30.2 | 41 | 53.2 | 63.32 | 67.82 | 64.58 | 57.7 | 51.62 | 45 | 42.1
BC | PITT MEADOWS | 38.2 | 40.3 | 43.8 | 48.8 | 55 | 60.1 | 65.3 | 65.1 | 59.9 | 50.5 | 42.5 | 37.4 | 31.5 | 33.26 | 37.2 | 40.1 | 46.4 | 51.44 | 55.58 | 55.94 | 52.3 | 46.04 | 39.4 | 31.3
PA | PITTSBURGH ALLEGHENY CO AP | 30 | 32.1 | 40.7 | 52.5 | 61.6 | 69.8 | 73.4 | 72.2 | 64.9 | 54.1 | 43.6 | 34.2 | 23.7 | 19.04 | 32.9 | 40.46 | 47.8 | 58.28 | 63.32 | 60.44 | 55.6 | 44.24 | 35.2 | 27.1
PA | PITTSBURGH INTERNATIONAL AP | 29.4 | 31.5 | 40.2 | 51.9 | 60.9 | 69.5 | 73 | 71.8 | 64.5 | 53.4 | 42.9 | 33.7 | 17.6 | 15.44 | 25.9 | 34.34 | 46.8 | 58.46 | 61.16 | 60.44 | 54.1 | 38.66 | 34.9 | 22.1
MA | PLYMOUTH MUNICIPAL | 28.8 | 30.6 | 36.8 | 46.3 | 56.1 | 65.5 | 71.8 | 70.2 | 63.1 | 52.3 | 43.1 | 34.2 | 22.1 | 18.86 | 31.5 | 38.12 | 47.7 | 56.3 | 62.24 | 61.7 | 57.9 | 47.66 | 36.3 | 30.7
ID | POCATELLO REGIONAL AP | 25.6 | 29.5 | 38.9 | 45.7 | 54.3 | 62.1 | 70.9 | 69.5 | 60.2 | 47.5 | 35 | 25.8 | 16.7 | 20.84 | 23.4 | 28.94 | 33.3 | 41.54 | 42.98 | 39.2 | 34.9 | 27.32 | 29.5 | 19.9
AK | POINT HOPE (AWOS) | -4.2 | -3.7 | -0.3 | 10.1 | 27.8 | 37.8 | 46 | 46.4 | 40.3 | 26.4 | 14.8 | 3.3 | 3.2 | -5.08 | 1.9 | 4.82 | 27.1 | 30.38 | 30.38 | 39.74 | 30.6 | 26.42 | 14.2 | 8.8
CA | POINT MUGU NF | 55.6 | 55 | 55.9 | 57 | 59.3 | 62.1 | 65.1 | 65.8 | 65.3 | 63 | 59.4 | 54.9 | 42.6 | 43.7 | 48.6 | 49.64 | 55 | 53.78 | 58.28 | 58.46 | 57.4 | 56.84 | 47.3 | 40.3
QC | POINT-AU-PERE | 14.1 | 16.6 | 24.8 | 36.6 | 46.7 | 54.9 | 60.2 | 58.9 | 52.8 | 43.2 | 33.9 | 22.5 | 4.8 | 7.88 | 16.5 | 27.32 | 37.4 | 47.3 | 53.96 | 52.88 | 46.4 | 36.68 | 27.3 | 14
OK | PONCA CITY MUNICIPAL AP [SGP - ARM] | 36.7 | 41 | 49.9 | 59.3 | 68.8 | 78.1 | 82.9 | 82 | 72.9 | 61.3 | 48.8 | 38.5 | 21.9 | 25.52 | 37.4 | 46.94 | 55.8 | 63.86 | 68.36 | 63.68 | 64.2 | 46.22 | 41.7 | 28.8
MO | POPLAR BLUFF(AMOS) | 36.1 | 40.2 | 48.8 | 59.6 | 68 | 76.3 | 79.3 | 77.9 | 70.2 | 59.4 | 48.1 | 38.6 | 26.2 | 28.76 | 41 | 52.16 | 55.9 | 67.28 | 71.96 | 68.54 | 59 | 53.78 | 35.4 | 27.1
TX | PORT ARTHUR JEFFERSON COUNTY | 53.5 | 56.8 | 62.5 | 68.9 | 76.2 | 81.7 | 83 | 83.3 | 79.4 | 70.9 | 61.3 | 55 | 42.1 | 45.14 | 55.9 | 61.34 | 68.5 | 73.04 | 74.48 | 73.94 | 70.5 | 59.36 | 56.7 | 45.9
AK | PORT HEIDEN | 24 | 24.8 | 26.3 | 33.4 | 40.2 | 46.6 | 51 | 52.5 | 47.5 | 38.4 | 31.9 | 27.6 | 28.8 | 17.42 | 20.8 | 25.7 | 27.7 | 30.74 | 35.06 | 36.5 | 29.7 | 28.04 | 28.4 | 19
ON | PORT WELLER | 27.5 | 28.3 | 34.8 | 44.2 | 54.3 | 65.3 | 71.2 | 71.1 | 64.7 | 53.1 | 42.3 | 33.3 | 19.8 | 19.76 | 26.2 | 35.6 | 46.4 | 57.2 | 60.98 | 60.98 | 55.4 | 44.6 | 35.6 | 24.3
CA | PORTERVILLE (AWOS) | 47.2 | 50.6 | 55.2 | 59.5 | 67.6 | 74.5 | 80.2 | 78.9 | 74.3 | 64.2 | 53.3 | 46.7 | 32 | 37.4 | 41 | 37.4 | 42.3 | 37.94 | 47.66 | 51.44 | 49.5 | 43.88 | 41.2 | 41.5
OR | PORTLAND INTERNATIONAL AP | 41.5 | 43.8 | 47.9 | 52.3 | 58.4 | 63.2 | 69.5 | 69.9 | 65.3 | 55.3 | 46.7 | 40.9 | 36.9 | 37.22 | 38.3 | 44.06 | 46.9 | 51.8 | 54.5 | 55.76 | 52.9 | 45.68 | 41.9 | 35.8
ME | PORTLAND INTL JETPORT | 23.5 | 25.7 | 33.8 | 44.3 | 54 | 63.7 | 69.5 | 68.4 | 60.6 | 49.9 | 39.9 | 30.1 | 9.5 | 12.38 | 20.5 | 34.7 | 44.6 | 52.7 | 60.08 | 58.46 | 48.9 | 37.22 | 26.1 | 14.4
OR | PORTLAND/HILLSBORO | 40.7 | 42.7 | 46.5 | 50.2 | 56.3 | 60.9 | 67.2 | 67 | 62.4 | 52.7 | 44.6 | 39.6 | 37.6 | 38.12 | 41.2 | 43.88 | 43.7 | 49.64 | 52.52 | 55.04 | 46.6 | 44.42 | 40.1 | 37
OR | PORTLAND/TROUTDALE | 41 | 43.4 | 47.3 | 51.4 | 57.2 | 62.5 | 68.8 | 68.9 | 64.1 | 54.8 | 46.7 | 40.7 | 34.2 | 34.88 | 35.2 | 41 | 44.1 | 51.62 | 54.68 | 52.34 | 46 | 45.32 | 41.5 | 36
NY | POUGHKEEPSIE DUTCHESS CO AP | 27.2 | 29.1 | 37.7 | 49.2 | 59.1 | 68.3 | 73.4 | 71.6 | 63.7 | 52.1 | 41.7 | 32.2 | 15.3 | 19.94 | 30 | 38.66 | 49.5 | 59.54 | 62.24 | 62.24 | 57 | 42.08 | 37 | 22.1
AZ | PRESCOTT LOVE FIELD | 39.2 | 41.8 | 47.3 | 53.2 | 62.2 | 71.3 | 76.2 | 74.2 | 68.6 | 57.4 | 46.6 | 38.3 | 24.8 | 23.54 | 25 | 24.44 | 27 | 33.8 | 48.74 | 53.42 | 38.3 | 35.78 | 25 | 17.4
ME | PRESQUE ISLE MUNICIP | 11.6 | 13.7 | 25 | 38.2 | 50.9 | 60.6 | 65.6 | 63.7 | 55.7 | 43.5 | 32.5 | 20.3 | 3.4 | 8.06 | 20.7 | 27.5 | 34.3 | 45.14 | 51.62 | 51.44 | 40.1 | 33.8 | 28.8 | 17.8
SK | PRINCE ALBERT AP | 1.1 | 6.8 | 19.2 | 37.2 | 49.9 | 59.2 | 64.1 | 62.3 | 52.3 | 37.9 | 19.8 | 5.2 | -2.7 | -0.94 | 9.9 | 24.8 | 32.9 | 46.22 | 54.32 | 51.26 | 42.4 | 28.94 | 17.2 | 0.3
BC | PRINCE GEORGE | 17.7 | 23.5 | 30.7 | 40.6 | 49.8 | 56.6 | 60.4 | 59 | 50.9 | 39.7 | 27.8 | 19.7 | 14.4 | 15.8 | 20.3 | 25.7 | 33.6 | 42.8 | 48.02 | 46.76 | 41.5 | 32.36 | 24.6 | 14.9
RI | PROVIDENCE T F GREEN STATE AR | 30.3 | 31.9 | 39 | 49.3 | 58.6 | 68.1 | 74 | 72.5 | 65.1 | 54.4 | 44.7 | 35.6 | 18.9 | 18.14 | 28.4 | 31.82 | 46.2 | 54.68 | 62.24 | 61.88 | 56.5 | 43.34 | 34.5 | 19.6
MA | PROVINCETOWN (AWOS) | 32.4 | 32.3 | 37.8 | 45.7 | 54.9 | 64.3 | 70.8 | 69.4 | 63.2 | 54.1 | 45.2 | 37.7 | 21.2 | 25.16 | 22.8 | 35.24 | 44.2 | 55.04 | 62.6 | 62.6 | 50.7 | 46.22 | 36.5 | 28
UT | PROVO MUNI (AWOS) | 29.6 | 33.4 | 42.7 | 48.8 | 58.4 | 66.7 | 74.8 | 73.4 | 62.7 | 50.4 | 37.5 | 29.6 | 26.1 | 23.18 | 27.9 | 32 | 36.5 | 42.44 | 47.84 | 51.98 | 38.5 | 30.92 | 30 | 21.9
CO | PUEBLO MEMORIAL AP | 31.4 | 34.3 | 43.1 | 50.7 | 60.8 | 70.9 | 76.1 | 73.8 | 65.5 | 52.3 | 39.8 | 30.9 | 17.4 | 18.68 | 24.6 | 35.06 | 39.6 | 47.84 | 51.98 | 50.36 | 42.1 | 28.22 | 24.4 | 18.9
VA | PULASKI-NEW RIVER VALLEY AP | 35 | 38 | 46 | 55 | 64 | 71 | 74 | 73 | 67 | 57 | 46 | 39 | 28.4 | 26.96 | 27.5 | 35.6 | 42.6 | 54.14 | 55.58 | 53.96 | 53.1 | 44.06 | 30.6 | 25.3
WA | PULLMAN/MOSCOW RGNL | 32.2 | 34.7 | 40.8 | 46.3 | 53.2 | 58.9 | 66.7 | 66.4 | 59.5 | 48 | 37.7 | 31.1 | 26.1 | 27.5 | 31.3 | 38.3 | 39.9 | 44.78 | 42.44 | 41.72 | 48.7 | 37.4 | 26.4 | 29.1
VA | QUANTICO MCAS | 36.4 | 38.8 | 46.3 | 56.8 | 65.4 | 74 | 78.4 | 76.7 | 69.7 | 58.3 | 47.9 | 39.6 | 28.6 | 24.44 | 34.7 | 44.06 | 49.3 | 65.3 | 66.92 | 67.46 | 61.7 | 50.54 | 40.5 | 31.3
QC | QUEBEC AP | 11.1 | 14 | 24.9 | 39.2 | 53.1 | 62.7 | 67.3 | 65.5 | 56.9 | 44.8 | 32.5 | 19.2 | 5 | 6.62 | 16.2 | 27.32 | 39.2 | 51.62 | 57.74 | 56.48 | 49.6 | 37.94 | 28 | 14.2
WA | QUILLAYUTE STATE AIRPORT | 41.8 | 42.4 | 44 | 46.9 | 51.5 | 55.4 | 59.2 | 59.7 | 57.2 | 50.5 | 44.9 | 40.9 | 38.3 | 37.94 | 39.7 | 41.54 | 45.3 | 48.92 | 53.24 | 53.6 | 51.3 | 44.96 | 42.3 | 38.5
IL | QUINCY MUNI BALDWIN FLD | 26.9 | 31.5 | 42 | 53.3 | 63.2 | 72.3 | 76 | 74.7 | 66.3 | 55 | 42.5 | 31.1 | 21.4 | 21.02 | 35.4 | 44.42 | 53.8 | 59 | 65.66 | 66.92 | 60.4 | 43.88 | 36.5 | 27.3
NC | RALEIGH DURHAM INTERNATIONAL | 41.9 | 44.6 | 51.5 | 60.4 | 68.1 | 76.1 | 79.8 | 78.1 | 71.7 | 61 | 51.3 | 44.1 | 30 | 25.88 | 35.4 | 46.22 | 59 | 64.22 | 68.54 | 68 | 63.9 | 51.08 | 39.2 | 32.4
TX | RANDOLPH AFB | 52.4 | 57 | 62.2 | 68.9 | 76.4 | 82.6 | 84.5 | 85.1 | 79.5 | 70.7 | 60.4 | 53.6 | 37.6 | 38.66 | 39.9 | 48.74 | 67.6 | 69.98 | 70.34 | 69.62 | 61.9 | 52.52 | 45 | 37.8
SD | RAPID CITY REGIONAL ARPT | 25 | 27.4 | 35.7 | 44.6 | 54.8 | 64.6 | 72.8 | 71.9 | 62 | 48.1 | 35 | 25.9 | 9.9 | 11.66 | 22.3 | 29.48 | 39.6 | 50.72 | 55.58 | 50.54 | 39.9 | 30.56 | 20.8 | 15.8
WY | RAWLINS MUNICIPAL AP | 22.4 | 22.9 | 33.2 | 40.7 | 50 | 60.3 | 69.5 | 66.1 | 56.8 | 43.9 | 31.2 | 21.9 | 18.3 | 19.58 | 19 | 22.46 | 30 | 37.22 | 38.12 | 41.9 | 34.2 | 26.96 | 20.8 | 16.3
PA | READING SPAATZ FIELD | 31.3 | 32.4 | 41.6 | 52.7 | 62.3 | 71.2 | 75.8 | 73.6 | 66.5 | 54.6 | 44.7 | 35.1 | 17.2 | 21.2 | 29.1 | 39.56 | 52.3 | 60.26 | 63.86 | 64.04 | 57.9 | 46.94 | 36.5 | 27
CA | RED BLUFF MUNICIPAL ARPT | 47 | 50.5 | 54.9 | 59.3 | 67.9 | 75.9 | 81.8 | 79.8 | 75 | 64.9 | 53.4 | 46.7 | 40.1 | 35.6 | 38.1 | 42.44 | 45 | 48.38 | 52.88 | 49.28 | 45.9 | 40.82 | 39 | 38.3
AB | RED DEER AP | 11 | 15.3 | 24.4 | 38.6 | 49.1 | 56.4 | 60.9 | 59.2 | 51.2 | 38.6 | 23.6 | 12.8 | 5 | 6.62 | 14.2 | 24.62 | 32.5 | 44.06 | 50.36 | 47.48 | 39 | 27.32 | 16.9 | 5.5
IA | RED OAK | 25.2 | 29.6 | 40.6 | 52.9 | 63.7 | 72.8 | 77 | 74.6 | 65.4 | 54.2 | 41 | 28.9 | 12.6 | 14.9 | 33.3 | 45.68 | 51.6 | 63.5 | 65.66 | 63.86 | 53.6 | 40.46 | 25.7 | 19.2
MN | RED WING | 15.5 | 20.2 | 32.2 | 46.4 | 57.9 | 67.8 | 72.4 | 70 | 61.6 | 49.6 | 34.9 | 21.2 | 10 | 14.72 | 27.3 | 31.64 | 42.1 | 56.48 | 66.38 | 58.64 | 54.1 | 43.7 | 23.7 | 14.4
CA | REDDING MUNICIPAL ARPT | 46.7 | 49.7 | 54.1 | 58.7 | 67.3 | 75.6 | 82.6 | 80 | 74.9 | 64.3 | 52.4 | 46 | 38.5 | 33.98 | 41.5 | 42.26 | 43.9 | 48.2 | 52.7 | 42.98 | 45.7 | 40.82 | 39 | 37
OR | REDMOND ROBERTS FIELD | 33.7 | 35.4 | 40.3 | 44.4 | 51.8 | 58.1 | 66.7 | 65.5 | 58.4 | 47.5 | 38.3 | 31.8 | 22.1 | 24.26 | 26.2 | 31.1 | 33.3 | 39.74 | 42.8 | 39.38 | 35.1 | 31.82 | 28.6 | 28.8
MN | REDWOOD FALLS MUNI | 14.9 | 19.5 | 31.4 | 46.1 | 58.8 | 68.8 | 72.7 | 70.3 | 62.1 | 48.8 | 33 | 19.5 | 13.1 | 7.34 | 27.3 | 36.86 | 46 | 60.44 | 64.04 | 58.64 | 50.5 | 35.24 | 27.1 | 7.3
SK | REGINA | 7 | 7.9 | 20.9 | 39.4 | 50.9 | 59.8 | 66 | 63.7 | 54.8 | 39.7 | 23.1 | 9.8 | 1.8 | 3.74 | 16.9 | 27.86 | 34.5 | 45.86 | 53.06 | 51.08 | 42.3 | 29.84 | 19.2 | 3.6
NV | RENO TAHOE INTERNATIONAL AP | 35.5 | 39.2 | 45.6 | 50.4 | 59.1 | 67.4 | 75.9 | 73.5 | 65.9 | 54.3 | 42.8 | 34.8 | 20.7 | 22.1 | 26.6 | 28.22 | 30.6 | 37.58 | 40.64 | 35.6 | 36.3 | 28.94 | 22.3 | 19.9
WA | RENTON MUNI | 42.3 | 43.5 | 46.5 | 50.6 | 56.5 | 61.8 | 67 | 67.3 | 62.2 | 53.6 | 46.1 | 41.7 | 37.2 | 35.42 | 41 | 41.72 | 45.1 | 50.18 | 53.24 | 53.78 | 52 | 44.78 | 41.4 | 38.1
NY | REPUBLIC | 32 | 34.3 | 40.8 | 50.5 | 59.8 | 69.3 | 75.2 | 74 | 67.2 | 56.3 | 46.2 | 37.4 | 23.7 | 17.78 | 31.6 | 37.22 | 45.7 | 57.92 | 63.68 | 66.92 | 58.1 | 44.24 | 40.5 | 25
WI | RHINELANDER ONEIDA | 13.5 | 16.9 | 27.7 | 41.4 | 53.5 | 62.4 | 67.2 | 64.8 | 56.8 | 44.4 | 32 | 18.1 | 10.2 | 2.48 | 21.7 | 34.34 | 42.6 | 57.56 | 59 | 57.2 | 49.8 | 36.14 | 27.3 | 2.7
WI | RICE LAKE MUNICIPAL | 14.4 | 17.8 | 30.1 | 44.6 | 55.2 | 64.8 | 69.8 | 67 | 59.2 | 46.6 | 33.8 | 19.5 | 8.1 | 6.26 | 21.2 | 37.04 | 37.8 | 57.56 | 63.32 | 62.78 | 54.9 | 32.36 | 21 | 8.4
VA | RICHMOND INTERNATIONAL AP | 39.2 | 41.5 | 48.9 | 58.8 | 66.7 | 75.2 | 79.4 | 77.5 | 70.9 | 60.2 | 50.2 | 42.2 | 23.5 | 26.06 | 31.8 | 44.78 | 54.1 | 60.44 | 69.08 | 66.02 | 63.9 | 49.82 | 37.6 | 32.7
CO | RIFLE/GARFIELD RGNL | 25.1 | 31 | 40.4 | 47.2 | 57 | 66.7 | 73.9 | 70.7 | 62.3 | 49.4 | 36.5 | 24.8 | 14.7 | 24.44 | 19.6 | 23.18 | 33.1 | 33.8 | 47.12 | 46.04 | 41.2 | 36.5 | 24.6 | 11.3
CA | RIVERSIDE MUNI | 56.2 | 55.7 | 58.8 | 61.5 | 67.7 | 71.9 | 78 | 78.7 | 76.1 | 68.1 | 60.6 | 54.8 | 34.7 | 37.58 | 49.1 | 42.98 | 51.4 | 54.5 | 56.12 | 57.38 | 54.3 | 51.62 | 41.9 | 28.9
WY | RIVERTON MUNICIPL AP | 21.3 | 25.1 | 35.9 | 43.8 | 53.7 | 63.5 | 73.4 | 70.3 | 59.6 | 45.7 | 32 | 20.9 | 14.2 | 9.86 | 18 | 30.02 | 33.3 | 34.52 | 38.66 | 40.82 | 41.9 | 28.22 | 21 | 13.5
VA | ROANOKE REGIONAL AP | 37.9 | 40.4 | 47.9 | 57.5 | 65.2 | 73.1 | 76.8 | 75.5 | 68.5 | 58.2 | 48.1 | 40.2 | 19.9 | 21.74 | 33.4 | 41.9 | 48.7 | 60.62 | 64.22 | 64.76 | 59 | 46.04 | 40.8 | 25.9
NY | ROCHESTER GREATER ROCHESTER I | 25.8 | 26.7 | 34.7 | 46.5 | 57.6 | 67 | 71 | 69.6 | 62.2 | 51.3 | 40.9 | 31.3 | 18.5 | 16.16 | 26.2 | 36.32 | 47.3 | 56.12 | 62.6 | 61.52 | 55.6 | 43.34 | 33.6 | 23.9
MN | ROCHESTER INTERNATIONAL ARPT | 15.2 | 19.5 | 31.7 | 45.6 | 57.4 | 67.3 | 70.4 | 68.3 | 60.6 | 48.3 | 33.7 | 20.4 | 4.6 | 12.56 | 24.4 | 34.88 | 48 | 56.84 | 61.34 | 59.54 | 46.6 | 34.88 | 25 | 12.9
IL | ROCKFORD GREATER ROCKFORD AP | 21.6 | 25.7 | 37 | 49 | 59.9 | 69.7 | 73.1 | 71.5 | 63.6 | 51.7 | 38.6 | 26.4 | 10 | 14.36 | 26.1 | 37.22 | 46 | 57.74 | 60.8 | 62.42 | 53.8 | 41.54 | 27.3 | 17.6
ME | ROCKLAND/KNOX(AWOS) | 22.4 | 25 | 32.4 | 41.9 | 51 | 59.8 | 65.6 | 64.8 | 57.9 | 47.9 | 39.2 | 29.7 | 19.8 | 13.82 | 24.6 | 23.72 | 39 | 46.76 | 50.54 | 52.88 | 54.1 | 42.98 | 29.3 | 22.1
TX | ROCKPORT/ARANSAS CO | 57.4 | 60.3 | 65.9 | 72.6 | 78.7 | 83.8 | 84.4 | 85.4 | 81.9 | 75.2 | 66.1 | 58.4 | 52.3 | 55.04 | 60.8 | 63.86 | 72.1 | 75.2 | 76.1 | 75.74 | 72.9 | 67.64 | 63.5 | 55.6
NC | ROCKY MOUNT WILSON | 41.1 | 43.5 | 51 | 60.8 | 68.2 | 76.5 | 79.2 | 78 | 71.8 | 61.2 | 51.1 | 43.7 | 28.2 | 34.16 | 40.6 | 47.12 | 56.7 | 66.56 | 65.66 | 63.86 | 59.9 | 51.44 | 43.9 | 30.2
AR | ROGERS (AWOS) | 36.6 | 40.3 | 47.8 | 57 | 65.3 | 74.1 | 78.3 | 77.5 | 69.7 | 59.1 | 48.3 | 38.8 | 22.3 | 24.26 | 25.2 | 36.5 | 53.1 | 65.48 | 66.56 | 64.58 | 60.1 | 43.34 | 37.6 | 31.6
GA | ROME R B RUSSELL AP | 42.2 | 45.7 | 53.1 | 61.2 | 69.2 | 76.7 | 79.8 | 79.5 | 73 | 61.8 | 51.1 | 44.5 | 31.5 | 36.32 | 31.3 | 49.1 | 56.7 | 65.84 | 67.64 | 64.94 | 64.8 | 59.54 | 33.6 | 28.9
MN | ROSEAU MUNI (AWOS) | 5.5 | 10.2 | 23.7 | 40.4 | 52.6 | 62.8 | 67.3 | 65.5 | 57.3 | 43.8 | 27.8 | 11.9 | 6.6 | 1.04 | 14.4 | 31.28 | 39.9 | 55.04 | 60.98 | 57.74 | 48.9 | 42.62 | 26.6 | 13.3
OR | ROSEBURG REGIONAL AP | 43.3 | 45.1 | 48.4 | 52.1 | 58.3 | 64 | 71.3 | 71.1 | 66.1 | 55.8 | 47.5 | 42.2 | 37.6 | 42.08 | 42.6 | 40.64 | 46.8 | 48.38 | 53.96 | 53.42 | 51.6 | 46.04 | 43.3 | 37.6
NM | ROSWELL INDUSTRIAL AIR PARK | 41.7 | 46.4 | 54 | 62.2 | 71.3 | 79.8 | 81.1 | 79.8 | 72.9 | 62.2 | 49.8 | 41.3 | 21.6 | 25.16 | 25.5 | 26.24 | 37.8 | 44.96 | 57.56 | 55.04 | 52.9 | 32.9 | 30 | 28.2
KS | RUSSELL MUNICIPAL AP | 30.2 | 34 | 43.8 | 53.4 | 64 | 74.7 | 79.9 | 77.8 | 68.9 | 56.2 | 42.5 | 31.7 | 17.1 | 17.96 | 27 | 41.36 | 57 | 56.66 | 60.8 | 61.16 | 54.1 | 41.72 | 32.2 | 27.9
VT | RUTLAND STATE | 20.6 | 23 | 31.8 | 44.1 | 55.3 | 64.1 | 68.2 | 66.6 | 59.3 | 47.9 | 38 | 27.1 | 8.1 | 10.04 | 17.2 | 33.62 | 44.8 | 53.42 | 60.26 | 56.84 | 52.9 | 40.28 | 24.6 | 15.1
CA | SACRAMENTO EXECUTIVE ARPT | 47.2 | 51.1 | 55.2 | 59.1 | 65.8 | 71.4 | 75.5 | 74.9 | 72.2 | 64.3 | 53.8 | 47 | 41.5 | 41.18 | 42.6 | 47.3 | 47.8 | 51.08 | 53.42 | 54.86 | 51.1 | 46.4 | 43.3 | 39
CA | SACRAMENTO METROPOLITAN AP | 47 | 50.8 | 55.2 | 59.5 | 66.7 | 72.8 | 76.8 | 75.8 | 72.6 | 64.3 | 53.7 | 46.8 | 41 | 42.08 | 46.2 | 44.78 | 46.8 | 53.42 | 55.04 | 55.04 | 51.6 | 47.3 | 42.4 | 41
AZ | SAFFORD (AMOS) | 47.3 | 50.9 | 57 | 64.5 | 73.5 | 83.1 | 85.3 | 83.4 | 78.8 | 67.3 | 55 | 46.6 | 19.8 | 21.2 | 36.1 | 28.94 | 30.6 | 33.8 | 46.4 | 56.3 | 43.3 | 41.36 | 27 | 27
MI | SAGINAW TRI CITY INTL AP | 23 | 24.6 | 33.8 | 46 | 57.7 | 67.9 | 71.1 | 69.1 | 61.6 | 50.5 | 38.7 | 28.4 | 9.7 | 11.12 | 30.4 | 32.9 | 41.9 | 53.78 | 57.56 | 66.02 | 51.4 | 42.8 | 33.1 | 22.1
UT | SAINT GEORGE (AWOS) | 42.6 | 46.9 | 55.3 | 61.9 | 72.9 | 82.2 | 88.5 | 86.3 | 78.4 | 64.5 | 50.2 | 40.8 | 26.1 | 35.24 | 23.4 | 25.7 | 21.7 | 30.02 | 42.08 | 47.12 | 37.6 | 35.06 | 32.7 | 23.2
AK | SAINT MARY`S (AWOS) | 6.3 | 10.7 | 11 | 24.7 | 39.5 | 50.1 | 53.2 | 51.3 | 44.1 | 28.9 | 17.6 | 9.1 | 7.3 | 13.46 | 17.8 | 24.98 | 27 | 38.84 | 44.96 | 43.88 | 33.4 | 28.94 | 19.9 | 11.8
OR | SALEM MCNARY FIELD | 41.6 | 43.5 | 47.1 | 50.7 | 56.7 | 61.6 | 68.5 | 68.3 | 63.8 | 53.8 | 46 | 40.8 | 36.9 | 35.24 | 41 | 42.8 | 46 | 49.82 | 52.34 | 52.52 | 49.8 | 44.06 | 43 | 35.6
KS | SALINA MUNICIPAL AP | 31.5 | 35.7 | 45.5 | 55.2 | 65.9 | 76.5 | 81.5 | 79.7 | 70.4 | 57.9 | 44.2 | 33.1 | 18.1 | 21.92 | 34.2 | 38.84 | 52.2 | 63.14 | 64.58 | 66.38 | 55.2 | 42.08 | 34.2 | 29.5
CA | SALINAS MUNICIPAL AP | 51.7 | 52.8 | 54.8 | 56.4 | 59.1 | 61.1 | 62.7 | 63.6 | 63.7 | 61.3 | 56.2 | 51.1 | 40.1 | 46.58 | 43.5 | 44.06 | 48.9 | 52.52 | 52.52 | 55.4 | 54.3 | 48.2 | 42.8 | 41.4
MD | SALISBURY WICOMICO CO AP | 36.8 | 38.3 | 45.2 | 55 | 63.3 | 72.5 | 77.4 | 75.3 | 68.8 | 58 | 48.2 | 40.4 | 25.2 | 29.12 | 37.6 | 46.76 | 54.3 | 62.24 | 66.92 | 66.74 | 61.7 | 50.18 | 39.6 | 37.2
ID | SALMON/LEMHI (AWOS) | 20.1 | 25.2 | 37.2 | 44 | 52.7 | 58.9 | 67.8 | 65.5 | 56.3 | 44 | 31.1 | 20.6 | 16 | 19.58 | 22.3 | 29.66 | 35.1 | 40.28 | 45.5 | 42.26 | 37.2 | 29.12 | 23 | 22.1
UT | SALT LAKE CITY INT ARPT [ISIS] | 30.2 | 35.1 | 44.4 | 50.6 | 60.2 | 70.1 | 79.8 | 77.8 | 67.5 | 53.6 | 40.5 | 30.8 | 22.6 | 24.44 | 29.7 | 31.82 | 39.7 | 38.3 | 46.94 | 43.88 | 41.2 | 37.22 | 28.4 | 25.2
TX | SAN ANGELO MATHIS FIELD | 47.4 | 51.2 | 58.7 | 67 | 75.2 | 81.7 | 83.7 | 83.1 | 76.1 | 66.5 | 55.4 | 48 | 27.7 | 33.98 | 34.5 | 47.3 | 57 | 61.7 | 63.86 | 63.68 | 59.4 | 47.84 | 44.2 | 31.3
TX | SAN ANTONIO INTL AP | 52.9 | 56.9 | 62.8 | 70 | 77.1 | 83 | 84.7 | 85.6 | 80 | 71.5 | 61.1 | 53.9 | 39.4 | 40.1 | 41.5 | 56.66 | 65.5 | 70.52 | 70.34 | 69.44 | 65.7 | 57.74 | 49.3 | 40.6
TX | SAN ANTONIO KELLY FIELD AFB | 53.1 | 57.5 | 62.8 | 70.4 | 77.8 | 83.3 | 85 | 85.6 | 80.1 | 71.5 | 60.8 | 54.3 | 37 | 39.2 | 40.8 | 49.28 | 66.9 | 67.28 | 71.42 | 69.26 | 62.1 | 53.06 | 48.2 | 40.5
TX | SAN ANTONIO/STINSON | 53.6 | 57.6 | 64.2 | 71.5 | 78 | 83.7 | 84.8 | 86.2 | 80.8 | 72.3 | 62.3 | 54.2 | 41.5 | 33.26 | 45.7 | 62.96 | 64.8 | 69.98 | 66.56 | 69.44 | 67.3 | 56.84 | 50 | 36.7
CA | SAN DIEGO LINDBERGH FIELD | 57.5 | 57.9 | 59.6 | 61.7 | 64.2 | 66.3 | 69.7 | 71.3 | 70.6 | 66.9 | 61.8 | 57.1 | 46.4 | 50 | 49.5 | 50.72 | 54 | 57.92 | 61.7 | 63.14 | 62.2 | 55.22 | 45.9 | 39.6
CA | SAN DIEGO MIRAMAR NAS | 56.5 | 56.6 | 57.6 | 60.2 | 63.4 | 66.7 | 71 | 72.5 | 71.2 | 66.2 | 60.7 | 55.7 | 44.4 | 43.16 | 45.3 | 48.2 | 53.6 | 58.64 | 62.42 | 61.88 | 60.4 | 48.02 | 46.8 | 37.2
CA | SAN DIEGO NORTH ISLAND NAS | 57.9 | 58.2 | 59.8 | 62 | 64.5 | 66.7 | 69.9 | 71.4 | 70.9 | 67.3 | 62.4 | 57.6 | 47.1 | 50 | 47.8 | 51.08 | 54.5 | 58.46 | 63.5 | 64.22 | 63 | 57.74 | 51.6 | 51.4
CA | SAN DIEGO/MONTGOMER | 56.5 | 56.1 | 58.2 | 60.1 | 63.7 | 66.5 | 71 | 72.6 | 71.5 | 66.5 | 60.9 | 55.8 | 43.2 | 45.14 | 48 | 47.12 | 52.7 | 56.66 | 59.9 | 59.72 | 55.9 | 55.4 | 44.2 | 40.6
CA | SAN FRANCISCO INTL AP | 50.7 | 52.7 | 54.8 | 56.7 | 59.3 | 61.7 | 63.3 | 64.1 | 64.5 | 62.1 | 56.1 | 51 | 43.5 | 43.88 | 46.6 | 46.76 | 48.9 | 50 | 51.26 | 52.7 | 54.5 | 48.92 | 46.9 | 43
CA | SAN JOSE INTL AP | 51.1 | 53.4 | 56.5 | 58.7 | 63.1 | 66.9 | 69.6 | 69.8 | 68.9 | 64.2 | 56.6 | 50.9 | 41.4 | 41.9 | 46.2 | 44.78 | 48.2 | 51.08 | 54.5 | 55.22 | 52.9 | 49.28 | 41.5 | 41
CA | SAN LUIS CO RGNL | 53.4 | 53.9 | 55.8 | 57.3 | 60.4 | 62.9 | 65.9 | 66.5 | 66 | 63.4 | 58 | 52.7 | 40.3 | 41.72 | 48.7 | 46.22 | 47.8 | 50.54 | 52.88 | 53.96 | 49.8 | 50.18 | 43 | 39.6
AK | SAND POINT | 31.4 | 32.7 | 31.6 | 35.7 | 41.6 | 47.3 | 51.6 | 53.3 | 49.7 | 42.4 | 37.2 | 33.7 | 28.6 | 24.62 | 28.2 | 27.68 | 30.4 | 39.2 | 42.98 | 47.12 | 38.1 | 32.18 | 23.9 | 23.2
CA | SANDBERG | 44.1 | 43.8 | 48 | 50.8 | 58.6 | 66.9 | 74.9 | 75.1 | 70.8 | 60.4 | 50.4 | 43.2 | 22.3 | 17.96 | 36.1 | 32 | 34.3 | 37.76 | 39.02 | 40.28 | 36.3 | 34.52 | 23.2 | 28.2
ME | SANFORD MUNI (AWOS) | 21.3 | 23.1 | 32.5 | 44 | 53.6 | 63.8 | 69 | 66.6 | 58.9 | 47.8 | 38 | 28 | 18.1 | 11.12 | 23.7 | 24.26 | 36.7 | 45.86 | 57.02 | 49.28 | 45.9 | 32.9 | 30.4 | 19
CA | SANTA ANA-JOHN WAYNE AP | 58 | 58 | 60 | 62 | 65 | 68 | 72 | 73 | 72 | 69 | 63 | 57 | 46.4 | 49.28 | 51.6 | 50 | 56.5 | 56.66 | 60.62 | 62.06 | 60.8 | 57.38 | 50.7 | 43.2
CA | SANTA BARBARA MUNICIPAL AP | 53 | 54 | 55.9 | 58 | 60.8 | 62.8 | 65.7 | 66.2 | 65.4 | 62.1 | 57.3 | 52.5 | 46 | 42.98 | 49.3 | 46.76 | 50.2 | 55.94 | 58.64 | 59.18 | 57.9 | 51.44 | 44.4 | 40.3
NM | SANTA FE COUNTY MUNICIPAL AP | 32.7 | 35.9 | 43.3 | 50.5 | 60.1 | 70 | 73.3 | 71.1 | 64.7 | 52.8 | 40.7 | 31.3 | 14.4 | 22.46 | 23.4 | 23.36 | 34.7 | 33.26 | 51.44 | 50.54 | 43.3 | 30.74 | 22.1 | 15.1
CA | SANTA MARIA PUBLIC ARPT | 52.4 | 53.1 | 54.8 | 56 | 58.5 | 60.6 | 63.2 | 63.6 | 63.5 | 61.4 | 56.7 | 51.8 | 40.6 | 41.72 | 46.9 | 46.22 | 48.6 | 51.8 | 53.6 | 54.14 | 54.3 | 49.64 | 45.9 | 37.4
CA | SANTA MONICA MUNI | 57.5 | 56.5 | 58.5 | 59.7 | 63.2 | 65.6 | 68.5 | 68.7 | 68.3 | 65 | 61.1 | 56.4 | 44.6 | 43.88 | 50.9 | 48.02 | 53.6 | 55.58 | 61.34 | 59.72 | 61.9 | 56.12 | 44.1 | 43
CA | SANTA ROSA (AWOS) | 47.2 | 49.8 | 53 | 55.5 | 60.9 | 65.5 | 67.2 | 67.4 | 65.9 | 60.7 | 52.9 | 47.4 | 42.4 | 45.14 | 44.6 | 45.68 | 48.7 | 52.34 | 52.34 | 54.32 | 51.6 | 47.12 | 42.6 | 43.9
FL | SARASOTA BRADENTON | 61.9 | 63.9 | 67.2 | 71.6 | 77.2 | 81 | 82.5 | 82.7 | 81.4 | 76.3 | 69 | 64.2 | 47.5 | 53.24 | 59.7 | 60.44 | 67.1 | 71.42 | 75.02 | 73.94 | 72.7 | 72.14 | 59.7 | 58.6
SK | SASKATOON | 4 | 8.8 | 21.3 | 39.2 | 51.1 | 59.7 | 64.5 | 63.3 | 53.8 | 39 | 21.8 | 7.9 | 0.9 | 2.48 | 14.4 | 27.32 | 34 | 47.66 | 55.04 | 51.08 | 43 | 29.3 | 18.5 | 3.6
ON | SAULT STE MARIE | 15.2 | 16.4 | 24.8 | 38.1 | 50.2 | 59.7 | 64.1 | 63.8 | 56.7 | 45.3 | 34.2 | 22.9 | 10.8 | 11.3 | 17.6 | 28.04 | 39 | 50.9 | 55.76 | 56.12 | 51.3 | 38.84 | 29.8 | 18.1
MI | SAULT STE MARIE SANDERSON FIE | 15.7 | 17.6 | 26.4 | 39.1 | 51.3 | 60.5 | 64.9 | 64.6 | 57.1 | 45.6 | 34.1 | 23 | 4.6 | 8.6 | 18.7 | 26.42 | 41.7 | 51.08 | 55.22 | 56.12 | 49.1 | 36.5 | 29.7 | 14.5
GA | SAVANNAH INTL AP | 50.7 | 53.6 | 59.5 | 66.2 | 73.5 | 79.6 | 82.4 | 81.5 | 77.1 | 68.1 | 58.7 | 52.6 | 38.8 | 41.18 | 50.4 | 50.9 | 60.1 | 70.7 | 72.68 | 71.6 | 69.1 | 55.4 | 51.6 | 39.6
AK | SAVOONGA | 3.8 | 3.5 | 7.2 | 16.2 | 29.6 | 40 | 47 | 46.6 | 41 | 32.9 | 25.4 | 12.1 | 3.9 | 9.68 | 3.2 | 13.1 | 28.6 | 32.36 | 32.36 | 33.98 | 34 | 26.96 | 21.7 | 13.3
NE | SCOTTSBLUFF W B HEILIG FIELD | 27.9 | 30.5 | 39 | 46.6 | 57.2 | 67.6 | 74.3 | 72.2 | 62.5 | 48.7 | 36.3 | 27.2 | 8.8 | 15.98 | 19.9 | 28.4 | 42.6 | 49.28 | 53.42 | 53.78 | 42.6 | 29.48 | 22.5 | 16.9
AZ | SCOTTSDALE MUNI | 55 | 56.7 | 63.9 | 70.5 | 79.7 | 89.3 | 93.5 | 91.8 | 86.6 | 74.7 | 63.4 | 53.4 | 29.1 | 33.62 | 31.1 | 35.06 | 37.4 | 37.94 | 57.2 | 61.7 | 50.4 | 42.98 | 37 | 30
WA | SEATTLE BOEING FIELD [ISIS] | 42.7 | 44.1 | 47.3 | 51.5 | 57.4 | 62.1 | 67.4 | 67.5 | 62.9 | 53.9 | 46.4 | 41.8 | 36 | 35.42 | 40.3 | 42.44 | 45.9 | 49.46 | 52.16 | 54.32 | 48.9 | 47.3 | 43 | 38.8
WA | SEATTLE SEATTLE-TACOMA INTL A | 41.9 | 43.3 | 46.2 | 50.1 | 55.9 | 60.6 | 66 | 66.1 | 61.7 | 52.8 | 45.6 | 41 | 34.2 | 35.24 | 37.2 | 41.54 | 45.5 | 48.02 | 50.72 | 53.42 | 51.3 | 44.96 | 41.5 | 36.5
AK | SELAWIK | -5.1 | -2.1 | 1.3 | 15 | 34.7 | 51.4 | 57.2 | 53.7 | 43.3 | 24 | 6.4 | -0.9 | -14.6 | -6.34 | 8.6 | 16.52 | 29.5 | 38.12 | 44.6 | 41 | 29.1 | 25.7 | 4.6 | 5
AK | SEWARD | 25.8 | 27.4 | 30.9 | 38.1 | 45.8 | 51.9 | 55.6 | 55.2 | 49.6 | 39.8 | 31.1 | 27.1 | 27 | 23 | 22.6 | 31.64 | 33.6 | 43.52 | 49.1 | 46.4 | 38.3 | 27.32 | 20.1 | 26.6
OR | SEXTON SUMMIT | 37.8 | 37.9 | 39.4 | 42.6 | 49.8 | 55.4 | 64.5 | 64.3 | 60.8 | 50.1 | 41 | 36.8 | 30 | 30.02 | 29.1 | 35.06 | 36.5 | 43.88 | 48.38 | 48.2 | 37.9 | 37.22 | 30 | 27.3
VA | SHANNON ARPT | 37.3 | 39.4 | 47 | 57.3 | 66.1 | 74.5 | 78.5 | 77.5 | 70 | 58.8 | 48.4 | 40.4 | 27.7 | 24.8 | 27 | 36.14 | 50.9 | 63.68 | 63.5 | 67.1 | 57.6 | 46.76 | 32 | 32.4
NS | SHEARWATER | 23.4 | 24.3 | 31.3 | 39.7 | 48.4 | 57.9 | 64.3 | 65.7 | 59.7 | 49.6 | 40.3 | 30.7 | 16.3 | 15.8 | 22.1 | 30.38 | 39.4 | 50 | 57.74 | 57.92 | 52 | 42.62 | 33.8 | 23.5
IA | SHELDON | 18.5 | 22.5 | 34.2 | 48.1 | 59.8 | 69.8 | 73.4 | 70.2 | 61.6 | 49.2 | 35.3 | 23.2 | 13.5 | 29.48 | 35.4 | 41.9 | 47.8 | 60.08 | 68.9 | 65.66 | 52.5 | 43.7 | 18.1 | 17.4
AK | SHEMYA AFB | 31.1 | 31.9 | 32.1 | 35.4 | 39 | 43.3 | 47.5 | 50.3 | 48.6 | 43.1 | 37.8 | 33 | 23.9 | 25.7 | 24.4 | 28.04 | 32.9 | 37.58 | 43.7 | 46.58 | 43 | 34.34 | 27.7 | 24.3
IA | SHENANDOAH MUNI | 25.9 | 29.6 | 41.1 | 53 | 64.5 | 73.1 | 77.6 | 74.7 | 66.2 | 55.1 | 40.9 | 29.4 | 18.7 | 18.86 | 28.6 | 42.26 | 55 | 64.58 | 64.4 | 70.52 | 56.7 | 40.64 | 28.9 | 19.4
QC | SHERBROOKE AP | 13.4 | 15.5 | 26.1 | 40.1 | 52.5 | 61.5 | 65.6 | 63.9 | 55.9 | 44.6 | 33.5 | 21 | 5.9 | 6.8 | 15.4 | 28.4 | 40.5 | 53.06 | 57.74 | 57.02 | 49.8 | 37.4 | 28.6 | 15.4
WY | SHERIDAN COUNTY ARPT | 24.3 | 26.9 | 35.8 | 43.6 | 52.6 | 61.5 | 70.8 | 69.5 | 59.4 | 46 | 33.6 | 24.1 | 11.5 | 15.44 | 22.3 | 29.84 | 40.8 | 46.58 | 50.36 | 47.84 | 39.6 | 30.56 | 21.6 | 15.6
AK | SHISHMAREF (AWOS) | -0.2 | 0.5 | -0.7 | 11.8 | 28.9 | 39.1 | 49.3 | 48.5 | 41.8 | 29.5 | 16.3 | 3.8 | -0.9 | -8.5 | 1.9 | 14.54 | 27.1 | 33.8 | 42.8 | 41 | 32 | 26.78 | 15.6 | 7.7
AZ | SHOW LOW MUNI AP | 33 | 38 | 45 | 50 | 57 | 69 | 72 | 69 | 64 | 54 | 44 | 34 | 18.3 | 21.2 | 18.9 | 23.9 | 31.8 | 32.54 | 39.2 | 50.36 | 41.2 | 32.54 | 22.1 | 19.8
LA | SHREVEPORT DOWNTOWN | 48 | 50.6 | 57.9 | 66 | 74.2 | 81.2 | 83.7 | 84.5 | 77.6 | 66.7 | 56.2 | 48.2 | 32.5 | 33.44 | 39 | 48.92 | 58.3 | 69.26 | 73.22 | 71.96 | 65.8 | 57.56 | 44.4 | 37.2
LA | SHREVEPORT REGIONAL ARPT | 48.1 | 51.7 | 58.6 | 65.9 | 73.8 | 80.7 | 83.4 | 83.7 | 77.8 | 67.1 | 56.4 | 49.1 | 35.8 | 37.4 | 48.9 | 55.58 | 62.4 | 68.54 | 70.7 | 71.42 | 66.2 | 53.06 | 44.8 | 35.6
NE | SIDNEY MUNICIPAL AP | 28.4 | 30 | 38.6 | 45.6 | 56 | 67 | 74 | 72 | 62.8 | 48.8 | 36.7 | 27.9 | 12 | 18.32 | 28 | 33.98 | 43.3 | 50.36 | 45.86 | 49.82 | 44.2 | 23.9 | 23.2 | 17.1
MT | SIDNEY-RICHLAND | 15 | 19.2 | 30.6 | 44 | 54.3 | 63.3 | 70.7 | 69.1 | 58.9 | 45.1 | 29.8 | 19.6 | -5.3 | 13.64 | 10 | 27.5 | 37.9 | 47.12 | 58.1 | 48.2 | 42.8 | 25.52 | 25.2 | 3.4
NM | SIERRA BLANCA RGNL | 39 | 40.5 | 46.2 | 52.8 | 62 | 69.7 | 70.1 | 68.3 | 63.5 | 54.8 | 45.5 | 37.9 | 23.2 | 19.76 | 23.5 | 23.54 | 25.5 | 33.62 | 45.5 | 47.48 | 44.8 | 37.22 | 19.6 | 18.9
AR | SILOAM SPRING(AWOS) | 36.8 | 40.5 | 48.8 | 58.1 | 66.3 | 73.8 | 79.1 | 78.3 | 69.6 | 59.2 | 48.4 | 39 | 27 | 33.8 | 35.4 | 44.78 | 57.2 | 63.86 | 67.46 | 61.7 | 58.3 | 45.68 | 40.5 | 26.1
MN | SILVER BAY | 10.5 | 14.3 | 24.5 | 36.8 | 48.1 | 57.7 | 63.8 | 62.1 | 53.7 | 42 | 28.4 | 16.1 | -0.8 | -2.02 | 22.3 | 26.78 | 28 | 49.82 | 53.24 | 50.9 | 50.5 | 29.48 | 16.7 | 7.3
IA | SIOUX CITY SIOUX GATEWAY AP | 20.4 | 25.5 | 37 | 49.6 | 61.2 | 70.8 | 74.5 | 72.4 | 64 | 51.3 | 36.4 | 24.1 | 7.2 | 20.48 | 26.1 | 38.3 | 49.3 | 56.66 | 62.42 | 62.42 | 53.1 | 37.58 | 25.2 | 12
SD | SIOUX FALLS FOSS FIELD | 17.1 | 22 | 33.5 | 46.4 | 58.2 | 68.4 | 73.2 | 71.1 | 62.4 | 48.9 | 33.6 | 21 | 4.5 | 10.76 | 25.3 | 33.26 | 47.7 | 57.74 | 62.6 | 59 | 49.8 | 35.6 | 24.8 | 12.7
AK | SITKA JAPONSKI AP | 36 | 36.6 | 37.3 | 42.5 | 47.8 | 52.8 | 56.1 | 57.1 | 53.1 | 46.1 | 39.7 | 37 | 24.8 | 19.04 | 25.5 | 27.14 | 37.4 | 46.22 | 50.18 | 51.08 | 46.4 | 36.86 | 26.6 | 20.7
AK | SKAGWAY AIRPORT | 26.5 | 30.2 | 32.2 | 40.9 | 49.4 | 55.3 | 57.2 | 56.4 | 50.7 | 43 | 33.1 | 28.7 | 21.9 | 19.22 | 24.1 | 27.68 | 36 | 45.68 | 47.66 | 48.38 | 40.3 | 31.1 | 24.6 | 12.9
AK | SLEETMUTE | -2.6 | 8.7 | 14.2 | 31.2 | 45 | 54.2 | 56.4 | 53.5 | 45.6 | 28.3 | 12.6 | 0.6 | -9.4 | 17.6 | 7.9 | 36.32 | 30.4 | 38.12 | 41.72 | 39.38 | 32.7 | 28.04 | 13.5 | 5.7
BC | SMITHERS AP | 18.8 | 24.4 | 31.3 | 40.5 | 48.9 | 55.3 | 59.2 | 58.2 | 50.4 | 39.6 | 28.3 | 20.2 | 15.6 | 17.42 | 20.8 | 26.24 | 34.2 | 43.16 | 48.74 | 47.48 | 42.3 | 33.62 | 25.2 | 15.6
WA | SNOHOMISH CO | 41 | 42.1 | 44.7 | 48.5 | 53.7 | 58.3 | 62.9 | 63.7 | 59.7 | 51.7 | 44.7 | 40.2 | 39.9 | 34.7 | 38.5 | 40.28 | 45.9 | 49.64 | 52.7 | 53.06 | 51.4 | 45.5 | 41 | 37
AK | SOLDOTNA | 12.2 | 19.5 | 23.2 | 35.5 | 44.6 | 51.7 | 55.9 | 54.6 | 46.9 | 34.4 | 21.2 | 15.4 | 17.8 | 26.42 | 16.3 | 27.68 | 32.9 | 39.56 | 44.78 | 39.38 | 34.9 | 26.78 | 14.5 | 20.5
KY | SOMERSET(AWOS) | 37.9 | 40.6 | 48.1 | 58 | 66.3 | 74.2 | 77.4 | 76.7 | 69.9 | 58.4 | 47.5 | 39.8 | 25.7 | 30.4 | 39.7 | 47.5 | 58.5 | 63.9 | 65.1 | 65.3 | 57.4 | 41.7 | 37.2 | 29.5
IN | SOUTH BEND MICHIANA RGNL AP | 25.3 | 28.2 | 37.9 | 49.3 | 59.9 | 69.5 | 73 | 71.4 | 64 | 52.7 | 40.8 | 30.2 | 20.3 | 20.48 | 30 | 35.6 | 49.6 | 55.94 | 64.94 | 63.86 | 54.5 | 42.08 | 34.7 | 23.5
CA | SOUTH LAKE TAHOE-LAKE TAHOE AP | 31 | 31 | 36 | 40 | 48 | 56 | 63 | 61 | 55 | 46 | 37 | 31 | 22.3 | 18.14 | 25.3 | 25.7 | 30 | 30.74 | 36.86 | 36.86 | 31.6 | 25.7 | 20.7 | 20.3
MN | SOUTH ST PAUL MUNI | 16.8 | 21.3 | 32.8 | 47.2 | 59.1 | 68.5 | 74 | 71.4 | 63.3 | 49.7 | 35.3 | 22 | 7 | 17.96 | 22.3 | 35.78 | 41.9 | 60.98 | 64.4 | 61.7 | 55.8 | 41.9 | 25.5 | 4.3
IL | SOUTHERN ILLINOIS | 33.9 | 37.5 | 46.8 | 57.8 | 66.9 | 75.3 | 77.9 | 76.9 | 68.6 | 57.6 | 46.8 | 36.5 | 19 | 28.94 | 38.5 | 41.18 | 63.5 | 65.48 | 68.9 | 67.46 | 61.5 | 50 | 41.9 | 27
NC | SOUTHERN PINES AWOS | 42 | 44.2 | 52 | 60.6 | 68.8 | 76.1 | 79.7 | 77.9 | 71.6 | 60.8 | 51 | 44.1 | 31.3 | 28.04 | 28.2 | 35.78 | 45.7 | 63.5 | 66.92 | 57.92 | 48.2 | 48.02 | 35.1 | 34.3
FL | SOUTHWEST FLORIDA I | 64.1 | 66.2 | 68.8 | 73.1 | 77.8 | 81.3 | 82.5 | 82.9 | 81.7 | 77.3 | 70.5 | 66.3 | 56.8 | 60.98 | 59.4 | 64.76 | 63.9 | 73.94 | 73.94 | 74.84 | 74.1 | 65.3 | 58.3 | 56.1
IA | SPENCER | 17 | 21.4 | 33.3 | 47 | 58.8 | 68.8 | 72.7 | 70 | 62.2 | 49.1 | 34.4 | 21.1 | 10.2 | 18.32 | 24.4 | 39.56 | 45 | 54.68 | 63.5 | 60.26 | 50.4 | 35.42 | 28.8 | 3.2
WA | SPOKANE INTERNATIONAL AP [CHENEY - UO] | 29.3 | 32.6 | 39.7 | 46.3 | 54.8 | 61.1 | 70.4 | 69.4 | 61.1 | 47.5 | 35.7 | 28.3 | 23.5 | 23.18 | 28.4 | 32 | 37.6 | 40.28 | 44.78 | 43.34 | 39 | 36.32 | 30.2 | 25.9
AB | SPRINGBANK | 15.1 | 20.8 | 25.9 | 37.1 | 45.7 | 52.5 | 57.3 | 57.3 | 49.6 | 38.1 | 24.8 | 16.6 | 9 | 10.4 | 15.4 | 22.82 | 30.7 | 41.54 | 46.4 | 43.88 | 36.1 | 25.88 | 17.1 | 9.9
AR | SPRINGDALE MUNI | 36.1 | 38.3 | 48.9 | 57.5 | 65.5 | 74.3 | 78 | 78.1 | 69.4 | 58.1 | 48.1 | 38.3 | 24.8 | 27.5 | 36.7 | 46.4 | 54.9 | 63.32 | 65.48 | 67.1 | 57.2 | 46.4 | 37.4 | 27.7
IL | SPRINGFIELD CAPITAL AP | 27.6 | 32.2 | 42.8 | 54 | 64.1 | 72.7 | 75.7 | 74.5 | 66.7 | 55.4 | 43.3 | 32.1 | 14 | 18.32 | 36.1 | 43.88 | 51.8 | 60.44 | 65.66 | 65.48 | 55.9 | 40.46 | 32.9 | 23.9
MO | SPRINGFIELD REGIONAL ARPT | 33.8 | 38.3 | 46.7 | 56.3 | 65.1 | 73.9 | 78.2 | 77.7 | 68.9 | 57.8 | 46.3 | 36.3 | 24.8 | 21.92 | 33.8 | 44.6 | 53.4 | 63.86 | 64.22 | 64.94 | 56.1 | 48.02 | 31.3 | 27.7
VT | SPRINGFIELD/HARTNES | 20.8 | 23.9 | 31.8 | 44.6 | 55.8 | 64.7 | 69.5 | 67.8 | 60.3 | 48 | 37.5 | 27.3 | 13.1 | 13.46 | 27.7 | 32.18 | 45.3 | 54.86 | 57.02 | 57.74 | 53.8 | 43.16 | 29.7 | 25.9
QC | ST ANICET | 15.8 | 18.1 | 28.7 | 43.2 | 55.7 | 65.5 | 69.1 | 66.7 | 59.5 | 47.7 | 36.4 | 23.6 | 7.5 | 9.5 | 19.6 | 31.64 | 42.8 | 55.4 | 60.44 | 59.9 | 52.7 | 40.46 | 31.1 | 15.6
MN | ST CLOUD REGIONAL ARPT | 12.1 | 17 | 29.3 | 43.9 | 56.2 | 66 | 70.3 | 68.1 | 59.4 | 46.3 | 31.1 | 17.7 | 0.1 | 7.88 | 20.3 | 27.32 | 43.9 | 55.58 | 60.8 | 57.38 | 48.7 | 36.32 | 24.1 | 5
MO | ST JOSEPH ROSECRANS MEMORIAL | 27.7 | 32 | 43.3 | 54.7 | 65.1 | 73.8 | 77.7 | 76 | 67.3 | 55.6 | 42.8 | 30.5 | 19.9 | 22.82 | 21.9 | 36.32 | 49.1 | 64.22 | 69.98 | 69.8 | 55.8 | 42.26 | 30.2 | 28.4
MO | ST LOUIS LAMBERT INT ARPT | 32.6 | 37 | 46.9 | 57.7 | 67.2 | 76.2 | 80.1 | 78.9 | 70.4 | 59 | 46.8 | 36.2 | 18 | 22.82 | 35.8 | 41 | 53.4 | 59.9 | 64.22 | 65.3 | 55.9 | 45.14 | 35.6 | 24.1
MO | ST LOUIS SPIRIT OF ST LOUIS A | 31.9 | 36.2 | 46 | 56.3 | 65.6 | 74.3 | 78.3 | 76.8 | 68.1 | 57 | 45.4 | 35.2 | 23.7 | 21.92 | 31.8 | 47.12 | 54.7 | 62.96 | 65.3 | 67.82 | 52.2 | 47.3 | 40.5 | 31.8
FL | ST LUCIE CO INTL | 61.5 | 64.6 | 67.5 | 71.4 | 76.3 | 79.9 | 81.1 | 81.6 | 80.1 | 75.8 | 69.2 | 65.3 | 47.1 | 57.38 | 55.4 | 56.3 | 65.8 | 73.22 | 73.76 | 74.3 | 71.1 | 63.5 | 59 | 56.1
MN | ST PAUL DOWNTOWN AP | 15.9 | 20.7 | 32.7 | 47.2 | 59 | 68.7 | 73.6 | 71.3 | 62.7 | 49.7 | 34.8 | 21.5 | -2.7 | 14.9 | 28.2 | 30.2 | 43.9 | 57.92 | 59.9 | 62.06 | 56.3 | 36.14 | 30 | 11.5
AK | ST PAUL ISLAND ARPT | 24.4 | 24 | 24.4 | 29.1 | 35.8 | 42.2 | 47.1 | 48.9 | 45.5 | 38.9 | 33.6 | 28.7 | 24.3 | 22.46 | 22.3 | 26.96 | 32.2 | 38.66 | 44.42 | 46.4 | 42.1 | 34.7 | 25.7 | 26.2
FL | ST PETERSBURG ALBERT WHITTED | 61.9 | 64.5 | 68.8 | 74 | 79.3 | 82.9 | 83.9 | 84.4 | 82.5 | 77.6 | 69.8 | 64.9 | 54 | 55.76 | 53.6 | 58.1 | 68.2 | 73.04 | 76.1 | 74.84 | 73.4 | 71.24 | 56.3 | 62.1
FL | ST PETERSBURG CLEAR | 62.2 | 63.8 | 68.4 | 73.3 | 78.1 | 81.7 | 82.9 | 83.8 | 81.9 | 76.9 | 68.7 | 65.6 | 43.9 | 52.34 | 53.1 | 58.82 | 69.4 | 72.86 | 75.2 | 74.66 | 73.6 | 65.48 | 61 | 54.7
MI | ST.CLAIR COUNTY INT | 24.7 | 25.6 | 34.3 | 45.5 | 56.4 | 65.6 | 69.6 | 67.8 | 61 | 50.4 | 39.7 | 29.6 | 14.7 | 21.2 | 30.9 | 34.88 | 49.6 | 60.62 | 60.8 | 62.06 | 54.3 | 39.38 | 34.9 | 23.5
WA | STAMPEDE PASS | 27.4 | 29.4 | 33.4 | 37.7 | 44.2 | 49.6 | 57.1 | 57.6 | 53.2 | 42 | 32.6 | 26.4 | 28.2 | 22.82 | 26.2 | 29.84 | 35.6 | 41.54 | 45.68 | 46.94 | 41.5 | 31.1 | 27.1 | 24.6
PA | STATE COLLEGE [PENN STATE - SURFRAD] | 27.6 | 29.6 | 38.1 | 50.3 | 59.3 | 67.7 | 71.2 | 70.8 | 63.4 | 52 | 42 | 31 | 20.1 | 16.16 | 24.6 | 29.84 | 41 | 57.02 | 60.08 | 58.1 | 49.5 | 37.04 | 33.3 | 22.5
VA | STAUNTON/SHENANDOAH | 35.6 | 37.6 | 45.4 | 55.5 | 64.2 | 72.7 | 76 | 74.7 | 67.4 | 56.2 | 45.8 | 38.1 | 28.6 | 24.44 | 26.8 | 32.36 | 42.3 | 54.86 | 64.76 | 69.98 | 61.3 | 42.44 | 28 | 30.6
QC | STE ANNE DE BELLEVUE | 15.4 | 18.2 | 28.5 | 43.2 | 56.3 | 65.7 | 69.7 | 67.7 | 60 | 48.1 | 35.9 | 22.8 | 6.4 | 9.14 | 18.3 | 30.38 | 42.6 | 55.22 | 59.54 | 58.82 | 52.3 | 40.1 | 30.4 | 14.5
QC | STE FOY | 12.2 | 16.5 | 25.9 | 40 | 53.8 | 62.5 | 67.7 | 65.9 | 58 | 45.5 | 34 | 20.2 | 4.6 | 7.16 | 16.5 | 27.14 | 38.5 | 50.72 | 57.56 | 56.48 | 49.8 | 37.76 | 28 | 14.2
IL | STERLING ROCKFALLS | 21.2 | 25.4 | 37 | 49.6 | 60.8 | 70.1 | 72.8 | 70.9 | 63.2 | 52 | 39 | 26.8 | 6.4 | 23.36 | 28 | 39.2 | 42.3 | 55.76 | 64.04 | 58.82 | 54.5 | 39.56 | 28.9 | 23.7
NY | STEWART FIELD | 27.1 | 30.1 | 37.9 | 49.3 | 59 | 68.6 | 72.8 | 71.7 | 63.5 | 52.2 | 42.1 | 32.6 | 10.2 | 18.32 | 30.2 | 30.2 | 43.2 | 57.56 | 62.24 | 57.02 | 53.6 | 42.08 | 33.4 | 27
OK | STILLWATER RGNL | 38.4 | 41.9 | 50.9 | 60.3 | 69 | 77.6 | 82.9 | 82.4 | 73.6 | 61.6 | 50 | 39.6 | 28 | 27.68 | 40.3 | 51.62 | 59.9 | 64.58 | 69.44 | 66.2 | 54 | 47.48 | 42.3 | 28.9
CA | STOCKTON METROPOLITAN ARPT | 47 | 50.9 | 55.7 | 59.9 | 66.7 | 72.7 | 77.1 | 76.4 | 73 | 64.5 | 53.9 | 46.7 | 41.7 | 42.62 | 48.2 | 47.3 | 45.5 | 52.88 | 52.16 | 52.7 | 54.1 | 47.48 | 43.7 | 41.2
IA | STORM LAKE | 20.3 | 23.7 | 35.8 | 49.4 | 61.1 | 70.7 | 74.4 | 71.6 | 64 | 51.7 | 37.2 | 23.7 | 17.2 | 11.12 | 22.1 | 39.02 | 39.6 | 55.58 | 61.88 | 67.46 | 51.8 | 38.66 | 24.4 | 17.2
WI | STURGEON BAY | 19.2 | 21.4 | 30.2 | 41.9 | 53.2 | 63.4 | 68.5 | 67.4 | 60.1 | 48.9 | 36.6 | 25.6 | 12.7 | 17.42 | 20.3 | 31.46 | 37 | 52.88 | 54.5 | 59 | 53.6 | 39.74 | 28.9 | 20.8
AR | STUTTGART (AWOS) | 41.7 | 45.5 | 53.3 | 62.9 | 71.8 | 79.8 | 82.2 | 81.1 | 73.6 | 63.1 | 52.1 | 44.2 | 36 | 37.94 | 38.3 | 49.28 | 61.7 | 68 | 72.68 | 69.44 | 65.7 | 54.14 | 43 | 31.6
ON | SUDBURY AP | 9.7 | 12.9 | 23.9 | 38.4 | 52.3 | 62.3 | 66 | 64.3 | 55.7 | 43.4 | 30.5 | 17.8 | 4.5 | 5.72 | 13.6 | 25.52 | 38.1 | 50.72 | 55.04 | 54.5 | 49.3 | 37.04 | 27.1 | 12.7
BC | SUMMERLAND | 29.6 | 32.8 | 40.4 | 48 | 56.6 | 63.1 | 70.9 | 69.7 | 60.8 | 48.1 | 36.6 | 30.2 | 19.6 | 23 | 27.1 | 30.38 | 37.6 | 43.34 | 45.86 | 45.5 | 41 | 35.42 | 28.2 | 19.4
SC | SUMTER SHAW AFB | 45.8 | 49 | 55.6 | 63.7 | 71.6 | 78.2 | 81.3 | 79.8 | 74.5 | 64.6 | 54.6 | 48.2 | 30.4 | 34.16 | 35.4 | 43.7 | 51.3 | 66.56 | 72.5 | 68.9 | 62.8 | 46.22 | 39.4 | 33.3
NS | SYDNEY AP | 23 | 21.9 | 28.1 | 36.7 | 46.1 | 56 | 64.7 | 65 | 58.1 | 48.1 | 39.4 | 30.5 | 17.4 | 15.44 | 20.8 | 28.76 | 37 | 47.66 | 56.66 | 57.38 | 51.1 | 42.26 | 35.2 | 25.3
NY | SYRACUSE HANCOCK INT ARPT | 24.8 | 25.9 | 34.3 | 46.9 | 58.2 | 67.4 | 71.8 | 70.4 | 62.7 | 51.5 | 40.9 | 30.6 | 18.1 | 17.06 | 25.9 | 37.4 | 48.4 | 55.22 | 60.98 | 59.54 | 51.8 | 41.9 | 32.2 | 20.5
WA | TACOMA MCCHORD AFB | 40 | 41.5 | 44.9 | 48.8 | 54.8 | 59.7 | 65 | 65.1 | 60 | 51 | 43.9 | 39.2 | 34 | 30.92 | 33.8 | 34.7 | 42.4 | 46.04 | 52.34 | 52.88 | 47.7 | 41 | 33.8 | 36
WA | TACOMA NARROWS | 41.9 | 43 | 45.8 | 49.7 | 55.3 | 60 | 65 | 64.9 | 61.1 | 52.9 | 45.4 | 41.4 | 38.1 | 37.76 | 37.8 | 41 | 43 | 48.2 | 51.98 | 53.6 | 52.3 | 45.86 | 42.1 | 39.2
AK | TALKEETNA STATE ARPT | 13.8 | 18.3 | 23.9 | 36 | 47.5 | 56.9 | 59.6 | 56.4 | 47.4 | 33.7 | 19.4 | 15.3 | 11.8 | 6.26 | 14.9 | 24.62 | 34.2 | 41 | 49.28 | 48.74 | 42.1 | 28.94 | 10.4 | 7.3
FL | TALLAHASSEE REGIONAL AP [ISIS] | 52.4 | 55.3 | 61 | 67 | 74.9 | 80.5 | 82.2 | 82.1 | 78.7 | 69.6 | 59.9 | 54.1 | 40.6 | 42.08 | 50.4 | 53.96 | 63.9 | 71.6 | 73.76 | 71.06 | 67.5 | 56.48 | 53.4 | 42.4
FL | TAMPA INTERNATIONAL AP | 61.4 | 63.6 | 67.4 | 72.6 | 78.6 | 82 | 82.9 | 83.1 | 81.6 | 76.1 | 68.5 | 63.7 | 50.2 | 53.6 | 59.7 | 60.26 | 67.1 | 71.42 | 73.76 | 73.58 | 72.7 | 65.66 | 57.9 | 50.2
AK | TANANA RALPH M CALHOUN MEM AP | -9.1 | 0.2 | 5.3 | 26.9 | 46 | 58.3 | 59.4 | 53.7 | 43 | 25.4 | 2.6 | -5 | -9.6 | 3.38 | 7.2 | 13.64 | 24.8 | 41 | 48.56 | 40.28 | 28.9 | 26.42 | 3 | -0.8
NM | TAOS MUNI APT(AWOS) | 26 | 30.8 | 38.3 | 44.6 | 54 | 63.5 | 68.1 | 66 | 58.8 | 47.1 | 35 | 25.4 | 13.1 | 24.8 | 11.8 | 22.64 | 15.6 | 28.76 | 41.36 | 41.9 | 36 | 17.96 | 17.6 | 11.8
NE | TEKAMAH (ASOS) | 21.6 | 26.4 | 38.4 | 51.2 | 62.5 | 71.7 | 76.1 | 73 | 64.8 | 52.2 | 38.6 | 25.3 | 14.9 | 25.52 | 31.6 | 36.32 | 52.2 | 61.52 | 65.66 | 65.48 | 56.7 | 38.3 | 32.4 | 8.6
IN | TERRE HAUTE HULMAN REGIONAL A | 29.3 | 33.2 | 43.1 | 54.2 | 63.9 | 72.8 | 75.5 | 73.8 | 66.4 | 55.3 | 43.6 | 33.3 | 17.1 | 24.62 | 33.8 | 46.76 | 47.7 | 63.14 | 65.48 | 71.42 | 60.3 | 44.24 | 39.4 | 28
NJ | TETERBORO AIRPORT | 32.3 | 34.2 | 41.7 | 52.4 | 62 | 71.5 | 76.6 | 74.8 | 67.6 | 56.3 | 46.3 | 37.2 | 19.8 | 22.1 | 30.6 | 32.18 | 51.1 | 54.5 | 60.8 | 58.64 | 50.9 | 45.14 | 37.2 | 27.9
AR | TEXARKANA WEBB FIELD | 45.6 | 49.2 | 56.5 | 64.4 | 72.1 | 79.7 | 83.1 | 83 | 75.8 | 65.4 | 54.6 | 46.9 | 36.3 | 41.18 | 43.3 | 57.92 | 60.8 | 66.74 | 71.24 | 69.08 | 69.3 | 59.36 | 41.2 | 37.4
WA | THE DALLES MUNICIPAL ARPT | 37.1 | 40.4 | 46.7 | 52.4 | 60.5 | 66.7 | 75 | 74.1 | 66.7 | 54.7 | 42.4 | 36 | 31.5 | 31.28 | 35.8 | 39.92 | 43.2 | 47.84 | 52.88 | 51.44 | 45.7 | 40.28 | 35.8 | 34.3
MN | THIEF RIVER(AWOS) | 6.4 | 10.9 | 23.9 | 40.5 | 53.3 | 63.2 | 67.2 | 65.8 | 56.8 | 43.7 | 27.2 | 12.4 | 1.9 | 15.08 | 6.8 | 33.98 | 35.1 | 52.34 | 60.26 | 56.48 | 48.4 | 26.6 | 29.3 | 6.3
ON | THUNDER BAY AP | 7.6 | 12.2 | 23.2 | 36.8 | 48.4 | 58.4 | 63.8 | 62.9 | 53.9 | 41.6 | 28.3 | 14.7 | 1.9 | 3.2 | 13.6 | 25.88 | 36.3 | 49.28 | 55.22 | 54.86 | 48.7 | 34.7 | 23.5 | 8.2
ON | TIMMINS AP | 2.8 | 7.2 | 19.4 | 34.7 | 49.5 | 59.8 | 63.4 | 61.2 | 52.6 | 40.4 | 26.5 | 11.9 | -2 | -0.58 | 8.8 | 21.56 | 34.7 | 46.94 | 52.7 | 52.34 | 46.6 | 33.62 | 23.2 | 7.2
AK | TOGIAK VILLAGE AWOS | 16.8 | 19.8 | 19.1 | 31.4 | 41.6 | 49.7 | 53.4 | 52.6 | 46.4 | 34.7 | 23.5 | 18.2 | 20.5 | 30.2 | 20.3 | 21.02 | 28.4 | 39.2 | 47.48 | 44.96 | 33.8 | 30.2 | 23.9 | 17.8
OH | TOLEDO EXPRESS AIRPORT | 26.1 | 28.4 | 37.8 | 49.6 | 60.2 | 70 | 73.4 | 71.6 | 64.2 | 52.8 | 41.3 | 30.9 | 19 | 17.6 | 28.9 | 37.4 | 47.8 | 57.2 | 59.72 | 60.08 | 55.2 | 39.2 | 29.7 | 18.5
NV | TONOPAH AIRPORT | 33.4 | 36.8 | 43.6 | 49.4 | 58.8 | 68.3 | 75.2 | 73 | 65.4 | 53.3 | 40.9 | 32 | 20.1 | 19.58 | 21.7 | 20.84 | 25.3 | 28.4 | 31.82 | 35.6 | 30.4 | 28.22 | 21.9 | 19.9
KS | TOPEKA FORBES FIELD | 30.1 | 34.2 | 45.2 | 55.1 | 64.9 | 74 | 79 | 77.5 | 68.5 | 56.4 | 44 | 32.9 | 23.9 | 19.4 | 38.7 | 45.14 | 53.2 | 66.38 | 70.34 | 64.58 | 62.4 | 42.08 | 35.8 | 21.4
KS | TOPEKA MUNICIPAL AP | 30.3 | 35.1 | 45.2 | 55.3 | 65.5 | 75 | 79.6 | 78.1 | 68.7 | 57.2 | 44.2 | 33.4 | 18.1 | 24.26 | 32 | 44.96 | 55.9 | 61.7 | 65.84 | 64.94 | 59.2 | 46.58 | 32.5 | 19.4
ON | TORONTO | 25.2 | 26.3 | 35.1 | 46.6 | 57.9 | 67.7 | 72.8 | 71.6 | 64.4 | 51.9 | 41.5 | 31.3 | 16.3 | 16.52 | 22.5 | 31.64 | 42.4 | 54.32 | 58.46 | 58.46 | 53.4 | 41.9 | 33.1 | 21.6
ON | TORONTO AP | 21.7 | 22.7 | 31.7 | 44.1 | 55.7 | 66 | 70.2 | 68.7 | 60.7 | 48.9 | 38 | 27.8 | 14.7 | 15.08 | 21.6 | 31.28 | 42.3 | 53.6 | 57.38 | 57.56 | 52 | 41 | 32.4 | 20.7
ON | TORONTO ISLAND AP | 25.7 | 27.1 | 33.8 | 43.9 | 54.4 | 64.6 | 69.4 | 69.8 | 63 | 50.9 | 40.6 | 31.5 | 18 | 17.96 | 23.4 | 32.72 | 43.3 | 55.04 | 59.9 | 60.98 | 55.6 | 43.16 | 34.3 | 23.2
MI | TRAVERSE CITY CHERRY CAPITAL | 23 | 23.6 | 32 | 43.5 | 54.7 | 65.3 | 69.5 | 68.4 | 60.7 | 49.4 | 38.2 | 28.4 | 14.5 | 15.62 | 20.8 | 28.58 | 41.9 | 51.62 | 59.72 | 55.76 | 50.5 | 37.4 | 30 | 17.8
CA | TRAVIS FIELD AFB | 47.2 | 50.9 | 55.2 | 58.7 | 64.3 | 69.6 | 72.6 | 73 | 71.5 | 64.7 | 54.4 | 47.2 | 35.8 | 39.56 | 41.9 | 42.8 | 45.9 | 50.72 | 52.88 | 51.44 | 50 | 45.5 | 36.7 | 37.6
ON | TRENTON AP | 20.1 | 21.8 | 30.7 | 43.7 | 54.9 | 65 | 69.1 | 67.8 | 59.9 | 48.5 | 37.6 | 26.8 | 13.3 | 13.64 | 21 | 32.54 | 44.4 | 55.94 | 60.08 | 60.26 | 54.1 | 41.72 | 32.2 | 19.9
NJ | TRENTON MERCER COUNTY AP | 32.1 | 34.2 | 42.7 | 52.7 | 62.4 | 71.3 | 76.2 | 74.4 | 67.2 | 55.7 | 46.3 | 36.8 | 18.7 | 19.94 | 31.8 | 43.52 | 47.8 | 58.28 | 62.06 | 65.84 | 58.3 | 43.88 | 38.7 | 25.2
CO | TRINIDAD LAS ANIMAS COUNTY AP | 33.2 | 35.6 | 43.1 | 50 | 59.7 | 69.6 | 73.9 | 71.9 | 64.9 | 53.1 | 41 | 32.3 | 14.4 | 22.1 | 25.2 | 26.78 | 32.4 | 42.98 | 49.64 | 46.94 | 39.7 | 27.86 | 24.6 | 15.4
QC | TROIS RIVIERES | 13.6 | 16.3 | 26.6 | 40.3 | 54.1 | 64.4 | 69 | 67.5 | 59.5 | 47.4 | 35.2 | 22.3 | 5.4 | 8.6 | 17.8 | 29.12 | 41.9 | 54.14 | 60.08 | 58.82 | 52.2 | 39.92 | 30.2 | 13.6
AL | TROY AIR FIELD | 47 | 52 | 58 | 65 | 72 | 79 | 81 | 80 | 76 | 66 | 56 | 50 | 39 | 44.96 | 46 | 48.74 | 64 | 68.54 | 70.88 | 70.34 | 67.5 | 64.04 | 43.7 | 35.4
CA | TRUCKEE-TAHOE | 27.9 | 30.7 | 34.8 | 39.6 | 48 | 54.9 | 62.8 | 60.9 | 54.3 | 44.8 | 36.6 | 29 | 25.2 | 25.52 | 25.7 | 24.44 | 32 | 36.5 | 41 | 32.36 | 32.2 | 29.84 | 22.3 | 22.3
NM | TRUTH OR CONSEQUENCES MUNI AP | 42.6 | 46.9 | 53.6 | 61 | 70.1 | 79 | 79.9 | 77.7 | 72 | 62.1 | 49.9 | 41.6 | 19 | 22.1 | 16.3 | 24.08 | 22.3 | 37.58 | 53.6 | 54.5 | 43.9 | 37.4 | 24.4 | 21.9
AZ | TUCSON INTERNATIONAL AP | 53.3 | 55.6 | 61.3 | 67.6 | 76.7 | 85.8 | 87.5 | 86 | 82.4 | 72.1 | 61 | 52.5 | 22.3 | 35.42 | 29.1 | 30.2 | 28.8 | 39.56 | 57.02 | 57.56 | 52.3 | 40.64 | 31.6 | 30.2
NM | TUCUMCARI AP | 39 | 42 | 51 | 59 | 67 | 78 | 81 | 79 | 72 | 60 | 48 | 39 | 19.8 | 26.6 | 25 | 31.46 | 44.4 | 52.34 | 57.56 | 59.36 | 52.9 | 41 | 28.8 | 23.4
OK | TULSA INTERNATIONAL AIRPORT | 38.8 | 43.1 | 51.7 | 60.8 | 69.5 | 78.3 | 83.2 | 82.6 | 73.4 | 62.2 | 50.6 | 40.6 | 22.8 | 27.14 | 36.9 | 47.48 | 55.6 | 67.64 | 69.8 | 68.54 | 60.4 | 48.92 | 34.5 | 24.3
MS | TUPELO C D LEMONS ARPT | 42.6 | 46.4 | 54 | 62.4 | 70.6 | 78 | 81 | 80.5 | 74 | 63 | 52.1 | 44.8 | 32.4 | 38.84 | 45.1 | 52.7 | 55.9 | 67.1 | 73.04 | 65.84 | 63.5 | 48.02 | 43.2 | 34.5
AL | TUSCALOOSA MUNICIPAL AP | 45.4 | 49.3 | 56.4 | 64.1 | 71.9 | 78.9 | 81.6 | 81.3 | 75.5 | 64.5 | 54.1 | 47.8 | 39.6 | 39.02 | 37.6 | 56.66 | 65.5 | 65.48 | 70.7 | 67.46 | 68 | 50.36 | 52.3 | 28.8
CA | TWENTYNINE PALMS | 51 | 54 | 61 | 67 | 75 | 85 | 90 | 89 | 82 | 70 | 58 | 50 | 29.5 | 23.18 | 32.2 | 35.6 | 38.1 | 48.02 | 49.64 | 48.02 | 48.2 | 34.34 | 30 | 20.5
MN | TWO HARBORS MUNI AP | 12 | 15 | 27 | 39 | 50 | 60 | 66 | 64 | 56 | 44 | 30 | 18 | 7.2 | -0.94 | 25.7 | 29.48 | 43.2 | 54.68 | 57.74 | 56.3 | 49.3 | 29.66 | 26.6 | 14.7
TX | TYLER/POUNDS FLD | 48 | 51.2 | 58.8 | 66.5 | 73.9 | 80.9 | 83.8 | 84.7 | 78 | 67.5 | 57.5 | 48.7 | 37 | 40.28 | 43.2 | 54.14 | 58.5 | 69.8 | 72.32 | 66.2 | 60.8 | 60.26 | 40.3 | 36.3
FL | TYNDALL AFB | 53.1 | 56.2 | 61 | 67.2 | 74.5 | 79.9 | 81.9 | 81.8 | 79 | 70.9 | 61.4 | 55.6 | 39.4 | 46.22 | 46.9 | 55.22 | 63.3 | 69.62 | 73.58 | 72.86 | 70.2 | 56.3 | 48.7 | 43.2
CA | UKIAH MUNICIPAL AP | 47 | 48.9 | 52.6 | 55.2 | 61.9 | 68.2 | 74.3 | 73.3 | 69.6 | 61.1 | 51.6 | 46.1 | 40.6 | 42.44 | 38.8 | 41.9 | 43.3 | 46.4 | 52.34 | 52.34 | 47.5 | 42.62 | 40.3 | 40.3
AK | UNALAKLEET FIELD | 5.8 | 10.5 | 11.4 | 25 | 38.3 | 49.4 | 55.3 | 52.5 | 44.4 | 28.2 | 13.5 | 9.8 | 0.3 | 6.98 | 11.3 | 18.86 | 29.3 | 37.22 | 44.42 | 40.64 | 31.6 | 28.22 | 12.9 | 6.6
IL | UNIV OF ILLINOIS WI [BONDVILLE - SURFRAD] | 26 | 30.3 | 40.9 | 52.6 | 63.2 | 71.8 | 74.2 | 72.3 | 66.1 | 54.2 | 41.6 | 30.3 | 16.3 | 23 | 32.4 | 47.12 | 51.1 | 63.68 | 65.48 | 66.56 | 55.2 | 42.44 | 38.3 | 20.3
NY | UTICA ONEIDA COUNTY AP | 22.6 | 24.5 | 32.3 | 45.2 | 56.4 | 66 | 69.8 | 68.8 | 60.8 | 49.4 | 39.2 | 28.6 | 19.9 | 20.48 | 22.8 | 29.12 | 51.1 | 56.48 | 59.72 | 59.36 | 55 | 44.6 | 32.9 | 18.7
AK | VALDEZ PIONEER FIEL | 23.8 | 26.4 | 30.7 | 39.1 | 47.2 | 54.2 | 55.8 | 54.2 | 47.4 | 38.7 | 29.4 | 25.8 | 28.2 | 26.06 | 25.3 | 23.9 | 33.4 | 39.92 | 48.02 | 44.24 | 32.2 | 28.04 | 27.5 | 24.1
AK | VALDEZ WSO | 22.3 | 25.3 | 28 | 36.5 | 45.7 | 52 | 54.1 | 52.6 | 47.3 | 38.7 | 27.6 | 24.2 | 15.3 | 19.76 | 21.2 | 31.82 | 39.9 | 45.32 | 48.74 | 48.2 | 43.7 | 31.82 | 11.7 | 18.7
GA | VALDOSTA WB AIRPORT | 52.5 | 55.7 | 61.2 | 67 | 74.7 | 80.3 | 82.3 | 81.9 | 78 | 69.2 | 59.8 | 54.4 | 50.5 | 39.74 | 50.5 | 62.06 | 64 | 71.78 | 73.94 | 74.66 | 67.5 | 61.88 | 50.5 | 41.5
NE | VALENTINE MILLER FIELD | 24.1 | 27.3 | 36.6 | 46.4 | 57.4 | 67.6 | 74.5 | 72.9 | 63.1 | 48.7 | 35.1 | 25.2 | 16.5 | 22.46 | 23.5 | 31.46 | 40.8 | 52.7 | 56.84 | 54.68 | 45 | 37.76 | 25.3 | 17.2
FL | VALPARAISO EGLIN AFB | 51.5 | 55.1 | 60.1 | 66.5 | 74.4 | 80.1 | 81.8 | 81.6 | 78.5 | 69.6 | 59.8 | 53.8 | 37.6 | 44.42 | 45.1 | 53.24 | 66.6 | 71.06 | 73.4 | 70.88 | 68.4 | 52.16 | 47.3 | 37.2
FL | VALPARAISO HURLBURT | 52.2 | 54.8 | 59.7 | 66 | 73.6 | 79.8 | 81.7 | 81.4 | 78 | 69.3 | 59.4 | 54.9 | 39.7 | 45.32 | 45.3 | 59.18 | 67.3 | 70.7 | 75.56 | 71.96 | 68.9 | 54.32 | 46.9 | 43.5
CA | VAN NUYS AIRPORT | 56.9 | 55.9 | 59.6 | 61.7 | 67.2 | 70.8 | 76.8 | 77.7 | 75.2 | 67.9 | 61.1 | 55.5 | 32.2 | 45.32 | 50.7 | 48.02 | 52.2 | 55.04 | 57.56 | 58.1 | 53.6 | 50.54 | 42.3 | 35.8
OK | VANCE AFB | 36.1 | 42.2 | 49.6 | 57.6 | 68.1 | 78.4 | 82.7 | 81.6 | 72.6 | 60.7 | 47.5 | 37.2 | 31.1 | 28.4 | 26.8 | 35.24 | 56.8 | 65.12 | 63.68 | 61.16 | 48.6 | 40.82 | 34.2 | 26.2
BC | VANCOUVER | 39.4 | 40.8 | 44.2 | 48.9 | 55.1 | 60 | 64.5 | 64.6 | 59.2 | 50.7 | 43.6 | 38.8 | 35.4 | 35.06 | 36.9 | 40.28 | 45.9 | 50.36 | 54.86 | 55.22 | 51.8 | 45.5 | 39.2 | 34.5
QC | VARENNES | 14.8 | 17.7 | 28 | 42.7 | 56.1 | 65.5 | 69 | 66.9 | 59.3 | 47.5 | 35.6 | 22.7 | 5.7 | 8.42 | 18.9 | 30.56 | 41.5 | 53.96 | 59.54 | 58.28 | 51.6 | 39.56 | 30.6 | 14
UT | VERNAL | 18.1 | 26.5 | 39.3 | 47.2 | 57 | 66.3 | 74.4 | 70.7 | 61.5 | 48.5 | 34.8 | 20.6 | 19.4 | 21.38 | 25.9 | 28.76 | 34 | 36.86 | 42.08 | 39.56 | 48.7 | 24.26 | 24.8 | 14.7
BC | VERNON | 26.8 | 30.7 | 39.4 | 47.4 | 56.5 | 62.6 | 69.1 | 68.1 | 59.2 | 46 | 34.7 | 27.2 | 20.1 | 23.9 | 28.9 | 33.44 | 41.9 | 48.2 | 50.72 | 49.82 | 46.4 | 39.02 | 31.3 | 20.3
FL | VERO BEACH MUNICIPAL ARPT | 62.8 | 64.8 | 67.8 | 71.7 | 76.6 | 80.3 | 81.5 | 81.8 | 80.6 | 76.4 | 69.9 | 65.3 | 58.5 | 54.68 | 58.5 | 66.38 | 68.4 | 70.88 | 73.4 | 73.22 | 72.3 | 68.72 | 62.1 | 58.1
MO | VICHY ROLLA NATL ARPT | 32.1 | 35.7 | 45.5 | 56.1 | 64.6 | 72.7 | 77.4 | 77 | 68 | 56.7 | 45.8 | 34.6 | 18.7 | 33.98 | 36 | 48.2 | 54 | 62.06 | 69.98 | 62.78 | 54.9 | 44.42 | 39 | 23.9
BC | VICTORIA | 41.2 | 42.4 | 44.3 | 48.5 | 54.3 | 59.8 | 65 | 64.6 | 60.1 | 51.1 | 44.4 | 40.4 | 35.1 | 36.14 | 39.9 | 41.9 | 46.4 | 50.36 | 53.6 | 54.5 | 52.2 | 47.12 | 42.3 | 34.9
BC | VICTORIA AP | 40.2 | 41.2 | 44.1 | 48.2 | 53.9 | 58.8 | 62.7 | 62.4 | 57.9 | 50.2 | 43.7 | 39.8 | 36 | 34.88 | 36.5 | 39.2 | 44.1 | 47.84 | 51.44 | 52.16 | 49.1 | 44.24 | 39.6 | 35.2
TX | VICTORIA REGIONAL AP | 54.9 | 58.4 | 63.9 | 70.4 | 77.2 | 82.5 | 84.1 | 84.7 | 80.3 | 72.4 | 62.7 | 56.1 | 47.1 | 46.58 | 51.1 | 59.54 | 67.5 | 71.96 | 74.48 | 73.04 | 70 | 61.34 | 54 | 45
BC | VICTORIA UNIV | 42.3 | 42.8 | 45.3 | 49.1 | 54.5 | 59.1 | 63.3 | 63.2 | 58.9 | 51.3 | 45.5 | 42.2 | 35.6 | 36.68 | 39.9 | 42.08 | 46.8 | 50.9 | 54.5 | 55.04 | 52.2 | 47.48 | 42.6 | 35.4
VA | VIRGINIA TECH ARPT | 33.8 | 36.5 | 44.4 | 54 | 62.2 | 69.8 | 72.9 | 72.2 | 65.3 | 54.9 | 44.4 | 36.6 | 20.1 | 24.08 | 20.7 | 35.6 | 49.6 | 57.2 | 62.42 | 60.26 | 57 | 44.96 | 37 | 24.4
CA | VISALIA MUNI (AWOS) | 46.6 | 50.4 | 56.2 | 60.3 | 68.4 | 74.8 | 79.7 | 78 | 73.4 | 63.8 | 53.1 | 46 | 38.5 | 30.74 | 43 | 41.54 | 44.6 | 48.56 | 58.1 | 54.5 | 52.2 | 45.32 | 37.6 | 34.9
BC | W VANCOUVER | 39.2 | 40.9 | 43.6 | 48.2 | 54.5 | 59.2 | 64.1 | 64.8 | 59.9 | 50.7 | 42.9 | 38.4 | 31.5 | 32.9 | 36.9 | 39.02 | 45 | 50.18 | 53.96 | 54.32 | 51.1 | 44.42 | 38.7 | 30.6
IL | W. CHICAGO/DU PAGE | 23.2 | 27 | 37.5 | 48.9 | 59.2 | 68.8 | 72.9 | 71.1 | 63.8 | 51.9 | 39.5 | 27.9 | 22.6 | 26.06 | 29.5 | 39.38 | 45.7 | 60.98 | 59.36 | 62.96 | 53.1 | 42.26 | 32.5 | 17.1
TX | WACO REGIONAL AP | 48.3 | 52.1 | 58.9 | 66.8 | 74.7 | 82.2 | 85.5 | 85.7 | 78.7 | 68.6 | 57.6 | 49.4 | 36.7 | 41 | 48.2 | 55.94 | 61.5 | 68 | 67.28 | 68.18 | 67.1 | 53.78 | 47.1 | 34
WA | WALLA WALLA CITY COUNTY AP | 36.6 | 39.7 | 46.8 | 52.4 | 59.8 | 66.5 | 76.3 | 75.2 | 66.9 | 53.8 | 42.4 | 35.1 | 30.6 | 30.56 | 30.9 | 38.12 | 41 | 46.94 | 44.96 | 48.74 | 45.9 | 39.02 | 36 | 30.4
AR | WALNUT RIDGE (AWOS) | 37.6 | 41.2 | 50.1 | 59.9 | 69.2 | 77.8 | 80.3 | 78.8 | 70.9 | 60.7 | 48.9 | 39.8 | 28.8 | 34.52 | 32.2 | 42.8 | 54.3 | 63.14 | 70.34 | 66.2 | 64.2 | 53.6 | 36.3 | 27.7
GA | WARNER ROBINS AFB | 47.5 | 51.2 | 58 | 64.6 | 72.8 | 79.1 | 82 | 80.9 | 75.5 | 65 | 55.6 | 50 | 31.8 | 37.22 | 36.1 | 44.42 | 66.9 | 67.82 | 73.04 | 69.8 | 64.8 | 46.94 | 42.4 | 30.7
IA | WASHINGTON | 25 | 28 | 40 | 52.5 | 63.3 | 72.3 | 75.5 | 73.7 | 64.8 | 53.8 | 40.5 | 28 | 21.2 | 17.78 | 30.2 | 41.36 | 51.4 | 58.64 | 68.18 | 65.66 | 59.5 | 43.88 | 27.5 | 21.6
PA | WASHINGTON (AWOS) | 28.5 | 30.4 | 38.6 | 49.9 | 58.4 | 67.1 | 70.7 | 69 | 62.1 | 51.9 | 41.4 | 32.8 | 30.6 | 22.64 | 19.8 | 36.68 | 46.8 | 57.92 | 60.26 | 60.44 | 55.6 | 38.66 | 32 | 24.8
VA | WASHINGTON DC DULLES INT AR [STERLING - ISIS] | 34.4 | 36.5 | 44.5 | 55 | 63.6 | 72.4 | 76.8 | 75.5 | 68 | 56.3 | 46.1 | 37.6 | 20.7 | 24.08 | 30.4 | 39.92 | 53.6 | 61.16 | 66.56 | 63.86 | 59.7 | 41.18 | 36.7 | 23.4
VA | WASHINGTON DC REAGAN AP | 37.2 | 39.4 | 47.1 | 57.4 | 66.3 | 75.4 | 80 | 78.4 | 71.3 | 59.9 | 49.4 | 40.9 | 23.4 | 20.3 | 27.7 | 42.62 | 53.2 | 63.32 | 65.48 | 63.68 | 60.6 | 49.64 | 39.7 | 32.7
IA | WATERLOO MUNICIPAL AP | 18.5 | 23.3 | 35.6 | 48.4 | 60.1 | 70 | 73 | 70.9 | 62.9 | 50.5 | 36.4 | 23.4 | 9.1 | 13.82 | 25 | 33.44 | 45.7 | 56.12 | 64.22 | 61.34 | 50.7 | 38.12 | 29.7 | 16.3
WI | WATERTOWN | 20.2 | 23.8 | 34.5 | 46.9 | 57.8 | 67.7 | 71.8 | 70 | 62.2 | 50.4 | 37.5 | 25 | 18.7 | 15.98 | 22.1 | 41 | 48.2 | 60.08 | 65.66 | 63.32 | 59.2 | 43.7 | 34 | 27.5
NY | WATERTOWN AP | 20.7 | 21.5 | 31 | 44 | 55.2 | 64.4 | 69 | 67.7 | 60 | 49.3 | 38.6 | 27.6 | 17.2 | 16.7 | 20.3 | 35.24 | 42.8 | 54.14 | 62.24 | 59.54 | 54.1 | 44.06 | 29.1 | 22.5
SD | WATERTOWN MUNICIPAL AP | 13.1 | 16.7 | 28.5 | 43.3 | 55.6 | 65.7 | 71.5 | 69.1 | 60 | 46.3 | 30.9 | 17.8 | 12.7 | 4.28 | 24.3 | 35.06 | 46.4 | 52.7 | 60.98 | 57.38 | 50.5 | 33.44 | 27.5 | 4.1
ME | WATERVILLE (AWOS) | 18.7 | 21.9 | 31.8 | 43.4 | 54.4 | 62.9 | 68.2 | 67 | 59.3 | 47.6 | 37.2 | 26.3 | 16.3 | 11.48 | 17.2 | 21.74 | 36.5 | 42.08 | 59.54 | 57.38 | 42.4 | 31.1 | 28.2 | 19.9
WI | WAUSAU MUNICIPAL ARPT | 15.5 | 19.6 | 30.5 | 44.1 | 56.1 | 65.7 | 69.7 | 68 | 59.3 | 47 | 33.3 | 20.8 | 9.7 | 5.9 | 11.8 | 35.42 | 36.3 | 57.74 | 57.02 | 61.34 | 52 | 38.3 | 26.4 | 17.4
IA | WEBSTER CITY | 20.9 | 24.7 | 36 | 49.5 | 61.2 | 71.1 | 74.7 | 71.8 | 63.3 | 51.6 | 37.6 | 23.9 | 14.5 | 20.48 | 32 | 42.08 | 41.7 | 60.26 | 65.66 | 64.76 | 54.9 | 42.8 | 25.2 | 21.2
WA | WENATCHEE/PANGBORN | 29.3 | 35 | 43.5 | 51.3 | 59.7 | 66.2 | 75 | 73.8 | 65.5 | 51.2 | 38 | 29.2 | 27.1 | 29.12 | 27.7 | 31.46 | 39.2 | 41.36 | 47.3 | 50.72 | 44.8 | 35.6 | 31.6 | 26.2
UT | WENDOVER USAF AUXILIARY FIELD | 27.5 | 33.4 | 43.2 | 50.5 | 60.6 | 70.4 | 79.9 | 77.1 | 66.5 | 51.5 | 37.4 | 27.9 | 18.3 | 21.56 | 23.4 | 25.16 | 32.5 | 30.56 | 37.22 | 38.48 | 31.5 | 31.28 | 17.6 | 18.3
MA | WESTFIELD BARNES MUNI AP | 24.5 | 27.6 | 36.2 | 48.6 | 58.7 | 67.4 | 72.6 | 70.7 | 63.2 | 51.2 | 41.2 | 31 | 5.9 | 14.72 | 28.4 | 35.96 | 42.8 | 58.1 | 58.82 | 60.44 | 57.7 | 44.6 | 31.1 | 22.3
NY | WESTHAMPTON GABRESKI AP | 29.6 | 31.3 | 37.6 | 46.9 | 56.1 | 66 | 72 | 70.9 | 64 | 53.1 | 44.1 | 35.2 | 22.3 | 25.34 | 32.7 | 33.98 | 49.5 | 57.38 | 60.8 | 64.04 | 59.9 | 48.38 | 34.9 | 26.6
MN | WHEATON NDB (AWOS) | 11.1 | 15.2 | 27.9 | 43.6 | 56.5 | 66.3 | 70.6 | 68.1 | 59.8 | 46.7 | 30.8 | 17.1 | 6.3 | 4.64 | 19 | 35.6 | 42.6 | 51.62 | 60.44 | 59.18 | 54 | 34.52 | 16.5 | 16.2
WV | WHEELING OHIO COUNTY AP | 29.3 | 31.5 | 40.6 | 52.7 | 61.4 | 68.7 | 72.5 | 71.6 | 64.9 | 53.8 | 44 | 33.9 | 30.4 | 19.04 | 25.3 | 42.44 | 45.9 | 57.56 | 63.32 | 60.98 | 52.9 | 44.96 | 31.6 | 21.4
WA | WHIDBEY ISLAND NAS | 41.7 | 42.5 | 45.4 | 48.8 | 52.8 | 56.6 | 59.2 | 59.6 | 56.4 | 50.7 | 45.2 | 40.9 | 37.9 | 37.04 | 36.7 | 43.88 | 46.4 | 49.82 | 52.7 | 51.98 | 51.4 | 44.96 | 43 | 37.8
BC | WHISTLER | 28.6 | 31.1 | 35 | 41 | 50 | 55.3 | 62.7 | 62.1 | 55.4 | 43.9 | 33.3 | 27.3 | 20.8 | 23.54 | 28.2 | 32 | 38.7 | 44.96 | 48.56 | 48.2 | 44.1 | 37.22 | 30 | 20.7
NY | WHITE PLAINS WESTCHESTER CO A | 30.1 | 31.9 | 39.2 | 49.8 | 59.4 | 68.7 | 73.8 | 72.3 | 64.9 | 54.2 | 44.4 | 35.3 | 13.3 | 16.34 | 30.6 | 37.76 | 44.2 | 58.28 | 61.34 | 61.16 | 58.6 | 44.78 | 33.4 | 16.7
YT | WHITEHORSE | 2.6 | 10.8 | 18.8 | 34.1 | 45.4 | 54.5 | 57.6 | 54.8 | 45.1 | 32.5 | 14.9 | 7.3 | 33.1 | 34.7 | 39 | 42.08 | 48 | 52.52 | 56.12 | 56.66 | 53.2 | 46.76 | 40.8 | 32.4
MO | WHITEMAN AFB | 30.4 | 35.8 | 44.9 | 55.2 | 65.1 | 74.4 | 78.8 | 77.2 | 68.6 | 57.4 | 44.8 | 34 | 29.5 | 22.82 | 33.3 | 35.06 | 50.5 | 65.12 | 64.76 | 63.68 | 53.8 | 41 | 30.2 | 27.7
FL | WHITING FIELD NAAS | 51.6 | 55.2 | 60.7 | 66.5 | 74.4 | 80.6 | 81.9 | 81.8 | 78.2 | 68.5 | 58.3 | 54.2 | 45.9 | 45.32 | 44.4 | 55.22 | 64.4 | 69.98 | 73.58 | 71.6 | 67.3 | 56.12 | 53.8 | 41.2
AK | WHITTIER | 28.4 | 29.1 | 32.1 | 39.1 | 46.4 | 54.1 | 56.7 | 55.8 | 48.7 | 39.8 | 32.1 | 29.7 | 23.7 | 26.06 | 25.2 | 23.18 | 35.8 | 45.68 | 49.64 | 47.84 | 37.6 | 30.56 | 21 | 25.5
TX | WICHITA FALLS MUNICIPAL ARPT | 43.2 | 47 | 55.1 | 63.5 | 72.5 | 80.8 | 85.1 | 84.6 | 76.4 | 65.2 | 53.3 | 43.9 | 28.2 | 33.26 | 40.8 | 49.82 | 58.5 | 62.78 | 65.84 | 65.12 | 61.2 | 47.12 | 40.8 | 30.7
KS | WICHITA MID-CONTINENT AP | 33.2 | 37.7 | 46.9 | 56.4 | 66.6 | 76.4 | 81.3 | 80.1 | 71.3 | 59 | 45.8 | 35 | 23 | 26.78 | 32 | 41.72 | 51.8 | 61.88 | 63.68 | 65.12 | 55.6 | 46.94 | 36 | 22.3
KS | WICHITA/COL. JABARA | 33 | 37.1 | 46.3 | 56.6 | 66.4 | 75.1 | 80.6 | 79.5 | 70.3 | 58.7 | 46.1 | 34.6 | 28.6 | 28.76 | 39.2 | 45.68 | 48.2 | 63.5 | 65.3 | 66.92 | 59.4 | 47.3 | 32 | 16.5
PA | WILKES-BARRE SCRANTON INTL AP | 27.2 | 29.3 | 37.6 | 49.4 | 59.5 | 67.9 | 72.2 | 70.4 | 63 | 51.9 | 41.9 | 32.2 | 16.2 | 17.42 | 23.2 | 34.34 | 46.6 | 58.1 | 58.28 | 59.9 | 51.4 | 41.54 | 29.8 | 21.7
WA | WILLIAM R FAIRCHILD | 39.5 | 40.3 | 42.7 | 46.6 | 51.3 | 55.9 | 60 | 60.3 | 57.3 | 49.2 | 43.1 | 39.2 | 35.6 | 36.86 | 37 | 38.12 | 43.3 | 49.46 | 50.9 | 51.26 | 48.4 | 44.24 | 40.1 | 35.6
PA | WILLIAMSPORT REGIONAL AP | 27.9 | 30.1 | 39 | 50.5 | 60.4 | 69.4 | 73.4 | 71.7 | 64 | 52.7 | 42.1 | 32.5 | 17.4 | 18.32 | 29.1 | 37.4 | 49.8 | 58.28 | 61.34 | 61.88 | 56.8 | 43.52 | 33.1 | 21.9
ND | WILLISTON SLOULIN INTL AP | 11.7 | 17.2 | 28.8 | 42.9 | 53.6 | 63 | 70.1 | 69.2 | 58.4 | 43.7 | 27.7 | 15.6 | 5.9 | 13.82 | 22.6 | 28.4 | 41.7 | 51.44 | 50.36 | 53.24 | 42.3 | 35.96 | 18.9 | 11.7
MN | WILLMAR | 12.4 | 18.1 | 29.2 | 45 | 56.8 | 67.1 | 70.6 | 68.4 | 60.7 | 47.6 | 31.4 | 18.7 | 5.5 | 18.14 | 30.9 | 40.28 | 46.4 | 56.3 | 63.5 | 63.14 | 45 | 32.9 | 24.4 | 15.3
PA | WILLOW GROVE NAS | 33 | 34.7 | 42.4 | 52.9 | 62.1 | 71.7 | 75.9 | 73.8 | 66.1 | 55.6 | 45.1 | 37.1 | 24.8 | 24.98 | 28 | 36.86 | 48.6 | 59.54 | 60.98 | 65.66 | 57 | 44.24 | 39.6 | 27.9
NC | WILMINGTON INTERNATIONAL ARPT | 46.9 | 48.9 | 55.1 | 63.4 | 70.6 | 77.6 | 81 | 79.4 | 74.5 | 65.2 | 55.8 | 49.3 | 34.7 | 36.32 | 41.9 | 51.62 | 60.8 | 69.44 | 72.32 | 70.34 | 66 | 55.04 | 48.4 | 40.8
DE | WILMINGTON NEW CASTLE CNTY AP | 33.6 | 35.4 | 43.2 | 53.7 | 63 | 72.3 | 77 | 75.2 | 68.1 | 56.7 | 46.6 | 37.9 | 18.5 | 25.7 | 31.3 | 41.36 | 52.7 | 60.26 | 65.84 | 64.04 | 56.7 | 43.34 | 31.6 | 21.4
VA | WINCHESTER RGNL | 34.8 | 36.7 | 44.7 | 54.9 | 63.6 | 72.3 | 76.5 | 75 | 67.6 | 56.2 | 46.1 | 37.4 | 27.5 | 22.28 | 24.4 | 32.54 | 42.6 | 62.42 | 60.62 | 65.3 | 53.2 | 42.98 | 28.6 | 28.4
ON | WINDSOR | 25.9 | 27.7 | 36.4 | 48.1 | 59.4 | 69.5 | 73.4 | 71.7 | 64.4 | 53 | 41.5 | 31 | 19 | 19.22 | 26.1 | 35.42 | 46.2 | 56.66 | 60.26 | 61.52 | 55.2 | 42.98 | 34.2 | 23
TX | WINK WINKLER COUNTY AP | 45.9 | 50.6 | 58.1 | 66.9 | 75.8 | 84.3 | 84.4 | 83.6 | 76.6 | 66.5 | 54 | 45.9 | 29.1 | 25.7 | 39.2 | 30.38 | 43.2 | 55.04 | 61.52 | 57.2 | 56.7 | 49.64 | 39.7 | 19.6
NV | WINNEMUCCA MUNICIPAL ARPT | 30.6 | 35.3 | 41.6 | 46.4 | 55.1 | 64.1 | 73.5 | 70.3 | 61.6 | 48.6 | 37.4 | 29.2 | 18.3 | 22.82 | 21.4 | 23.72 | 34.5 | 31.64 | 39.2 | 37.22 | 28.6 | 26.6 | 23.4 | 19
MB | WINNIPEG | 2.5 | 7.4 | 21.1 | 39.1 | 51.7 | 62.5 | 66.8 | 65.8 | 55.9 | 41.5 | 24 | 8.6 | -2.6 | -0.58 | 14 | 27.86 | 37.8 | 51.62 | 57.74 | 55.04 | 47.8 | 33.44 | 21.4 | 3.7
MN | WINONA MUNI (AWOS) | 18 | 22.5 | 34.2 | 47.6 | 58.8 | 68.7 | 73 | 70.8 | 62.7 | 50.5 | 36.9 | 23.8 | 10.6 | 10.4 | 28.6 | 38.66 | 44.2 | 56.48 | 62.24 | 61.7 | 54.1 | 38.12 | 28.6 | 3.9
AZ | WINSLOW MUNICIPAL AP | 35.6 | 40.1 | 47.4 | 54 | 63.3 | 72.7 | 78.2 | 75.9 | 69 | 56.3 | 43.7 | 34.4 | 20.7 | 21.38 | 21.4 | 23.18 | 30.6 | 30.56 | 49.28 | 53.78 | 46.8 | 21.2 | 25 | 16.2
NC | WINSTON-SALEM REYNOLDS AP | 40.3 | 43.4 | 50.7 | 59.8 | 67.4 | 75.1 | 78 | 76.9 | 70 | 59.7 | 50.4 | 43.1 | 23.2 | 33.98 | 41.2 | 46.76 | 53.2 | 64.4 | 69.08 | 63.86 | 59.2 | 50.72 | 42.3 | 26.1
ME | WISCASSET | 21.3 | 24.8 | 32.7 | 43.3 | 53.3 | 62.2 | 68.1 | 66.9 | 59.5 | 48.3 | 38.6 | 28.5 | 21.4 | 14 | 25.9 | 33.08 | 42.6 | 53.24 | 60.26 | 58.46 | 56.3 | 44.06 | 33.8 | 28.2
VA | WISE/LONESOME PINE | 33.2 | 36.4 | 44.8 | 54.6 | 62 | 69 | 72.4 | 72 | 65.5 | 55.5 | 45.4 | 37 | 24.4 | 27.68 | 26.8 | 31.28 | 47.3 | 58.82 | 65.3 | 60.62 | 55.6 | 43.34 | 34.7 | 20.1
WI | WITTMAN RGNL | 18.7 | 22.2 | 32.7 | 45.8 | 56.7 | 66.8 | 71.5 | 69.4 | 61.6 | 49.4 | 36.8 | 24.1 | 10.4 | 8.78 | 30.7 | 37.4 | 41.4 | 55.76 | 58.46 | 61.52 | 53.1 | 36.86 | 31.6 | 6.6
MT | WOLF POINT INTL [FORT PECK - SURFRAD] | 13.8 | 16.2 | 29.7 | 43.3 | 53.3 | 62.3 | 71.5 | 69.2 | 58.1 | 44.1 | 28.5 | 15.6 | 13.5 | 2.84 | 15.3 | 28.22 | 41.2 | 50.36 | 53.42 | 53.42 | 39 | 31.28 | 22.6 | 12.4
MA | WORCESTER REGIONAL ARPT | 24.9 | 27 | 34.8 | 46.4 | 56.4 | 65.3 | 70.4 | 69 | 61.6 | 50.6 | 40.5 | 30.6 | 9.3 | 14.36 | 19.9 | 31.64 | 43.9 | 52.52 | 59 | 56.3 | 51.4 | 37.22 | 25.5 | 18.1
WY | WORLAND MUNICIPAL | 18.3 | 22.1 | 37.3 | 46.1 | 55.2 | 65.4 | 74.3 | 71 | 60.9 | 46.3 | 32.3 | 18.2 | 11.1 | 17.06 | 18.7 | 28.4 | 37.6 | 42.8 | 46.58 | 43.88 | 37.4 | 33.44 | 21.9 | 12.7
MN | WORTHINGTON (AWOS) | 15.4 | 20 | 31.5 | 45.5 | 56.6 | 66.9 | 70.8 | 68.3 | 60.6 | 48.6 | 33.3 | 20.4 | 8.1 | 18.68 | 12.2 | 35.96 | 46.6 | 53.96 | 60.26 | 60.44 | 53.4 | 33.44 | 23.4 | 9.5
AK | WRANGELL | 32.1 | 34.3 | 36.8 | 42.9 | 49.6 | 54.6 | 57 | 56.9 | 52.2 | 45.2 | 37.9 | 33.9 | 21.9 | 24.62 | 26.1 | 30.56 | 37.8 | 46.58 | 51.44 | 50.36 | 44.8 | 37.76 | 28.9 | 25.5
WA | YAKIMA AIR TERMINAL | 31.6 | 36.6 | 43.3 | 49.5 | 57.8 | 64.4 | 72.1 | 70.2 | 62.2 | 49.5 | 37.9 | 30 | 26.2 | 28.58 | 30 | 35.6 | 39.7 | 44.78 | 47.48 | 45.32 | 40.6 | 36.68 | 25.9 | 23.9
AK | YAKUTAT STATE ARPT | 27.7 | 29.9 | 31.3 | 37.9 | 44.9 | 51.3 | 54.6 | 54.1 | 49 | 41.2 | 32.6 | 29.6 | 23 | 19.4 | 25 | 33.62 | 40.1 | 45.86 | 50 | 50.9 | 44.8 | 36.86 | 28 | 26.8
NT | YELLOWKNIFE AP | -13.9 | -8.2 | 2 | 22.2 | 40.8 | 56.6 | 62.8 | 57.6 | 45.8 | 30 | 8.8 | -7.4 | -19.7 | -17.68 | -9.6 | 11.66 | 24.6 | 38.66 | 47.84 | 45.68 | 37.8 | 25.34 | 6.4 | -12.3
OH | YOUNGSTOWN REGIONAL AIRPORT | 27 | 28.8 | 37.3 | 49.1 | 58.7 | 67.2 | 70.9 | 69.5 | 62.3 | 51.7 | 41.4 | 31.6 | 16.9 | 18.32 | 28.8 | 34.34 | 47.1 | 54.68 | 63.68 | 60.44 | 54.1 | 40.1 | 33.6 | 22.1
CA | YUBA CO | 46.7 | 50.5 | 55.2 | 58.8 | 67.5 | 73.9 | 78.7 | 76.6 | 72.8 | 63.7 | 53.2 | 47.1 | 42.8 | 39.02 | 46 | 43.52 | 46.8 | 51.62 | 55.22 | 54.14 | 50.7 | 45.86 | 43.2 | 41.9
AZ | YUMA INTL ARPT | 59.2 | 61.8 | 67.6 | 73.2 | 81.2 | 89.4 | 94.8 | 94.6 | 89.8 | 78.1 | 66.3 | 57.7 | 33.4 | 29.84 | 34.5 | 31.28 | 35.6 | 40.64 | 61.34 | 59.36 | 53.1 | 40.1 | 35.6 | 32.9
AZ | YUMA MCAS | 58.9 | 62.1 | 67.6 | 73.6 | 81.2 | 89.3 | 94.7 | 94.3 | 89.2 | 78 | 66 | 57.5 | 32.2 | 29.84 | 34.5 | 37.58 | 38.5 | 40.46 | 54.68 | 66.74 | 52.9 | 46.22 | 38.5 | 40.3
OH | ZANESVILLE MUNICIPAL AP | 29.9 | 32.5 | 41.3 | 52.5 | 61.5 | 69.8 | 73.3 | 72.1 | 64.8 | 53.5 | 43.1 | 34 | 30.4 | 26.6 | 32 | 43.88 | 56.8 | 57.74 | 62.06 | 60.8 | 56.8 | 46.76 | 33.6 | 27.1

## phius_monthly climate data (hidden)
Country | State | City_WUFIp Data Set | Country | Select | Select | Country | State | AB | AE | AK | AL | AR | AZ | BC | BD | CA | CO | CT | DE | FL | GA | HI | IA | ID | IL | IN | KS | KY | LA | MA | MB | MD | ME | MI | MN | MO | MS | MT | NB | NC | ND | NE | NL | NH | NJ | NM | NS | NT | NU | NV | NY | OH | OK | ON | OR | PA | PE | QC | RI | SA | SC | SD | SK | TN | TX | UT | VA | Cartagena | VT | WA | WI | WV | WY | YT | 1 | USA | Canada | Columbia
Canada | AB | CALGARY INT AP | Select | #N/A |  | Canada | AB | CALGARY INT AP | DUBAI INT AP | ADAK NAS | ANNISTON METROPOLITAN AP | BATESVILLE (AWOS) | CASA GRANDE (AWOS) | ABBOTSFORD AP | DHAKA | ALTURAS | AKRON WASHINGTON CO AP | BRIDGEPORT SIKORSKY MEMORIAL | DOVER AFB | CRESTVIEW BOB SIKES AP | ALBANY DOUGHERTY COUNTY AP | BARBERS POINT NAS | ALGONA | BOISE AIR TERMINAL [UO] | AURORA MUNICIPAL | DELAWARE CO JOHNSON | CHANUTE MARTIN JOHNSON AP | BOWLING GREEN WARREN CO AP | ALEXANDRIA ESLER REGIONAL AP | BARNSTABLE MUNI BOA | WINNIPEG | ANDREWS AFB | AUBURN-LEWISTON | ALPENA COUNTY REGIONAL AP | AITKIN NDB(AWOS) | CAPE GIRARDEAU MUNICIPAL AP | COLUMBUS AFB | BILLINGS LOGAN INT ARPT | FREDERICTON | ASHEVILLE REGIONAL ARPT | BISMARCK MUNICIPAL ARPT [ISIS] | AINSWORTH MUNICIPAL | ST JOHNS | BERLIN MUNICIPAL | ATLANTIC CITY INTL AP | ALBUQUERQUE INTL ARPT [ISIS] | GREENWOOD AP | YELLOWKNIFE AP | IQALUIT | ELKO MUNICIPAL ARPT | ADIRONDACK RGNL | AKRON AKRON-CANTON REG AP | ALTUS AFB | BEAUSOLEIL | ASTORIA REGIONAL AIRPORT | ALLENTOWN LEHIGH VALLEY INTL | CHARLOTTETOWN | JONQUIERE | BLOCK ISLAND STATE ARPT | RIYADH | ANDERSON COUNTY AP | ABERDEEN REGIONAL ARPT | MOOSE JAW AP | BRISTOL TRI CITY AIRPORT | ABILENE DYESS AFB | CEDAR CITY MUNICIPAL AP | ABINGDON | CARTAGENA, COLUMBIA | BURLINGTON INTERNATIONAL AP | BELLINGHAM INTL AP | APPLETON/OUTAGAMIE | BECKLEY RALEIGH CO MEM AP | CASPER NATRONA CO INTL AP | WHITEHORSE | 2 | AK | AB | Cartagena
Canada | AB | COP UPPER |  | #N/A |  | United Arab Emirates | AE | COP UPPER |  | AMBLER | AUBURN-OPELIKA APT | BENTONVILLE (AWOS) | DAVIS MONTHAN AFB | AGASSIZ CDA |  | ARCATA AIRPORT | ALAMOSA SAN LUIS VALLEY RGNL | DANBURY MUNICIPAL | WILMINGTON NEW CASTLE CNTY AP | DAYTONA BEACH INTL AP | ALMA BACON COUNTY AP | HILO INTERNATIONAL AP | ATLANTIC | BURLEY MUNICIPAL ARPT | BELLEVILLE SCOTT AFB | EVANSVILLE REGIONAL AP | CONCORDIA BLOSSER MUNI AP | CINCINNATI NORTHERN KY AP | BARKSDALE AFB | BEVERLY MUNI |  | BALTIMORE BLT-WASHNGTN INT | AUGUSTA AIRPORT | ANN ARBOR MUNICIPAL | ALBERT LEA (AWOS) | COLUMBIA REGIONAL AIRPORT | GOLDEN TRI(AWOS) | BOZEMAN GALLATIN FIELD | MONCTON AP | CAPE HATTERAS NWS BLDG | DEVILS LAKE(AWOS) | ALLIANCE MUNICIPAL |  | CONCORD MUNICIPAL ARPT | BELMAR ASC | CARLSBAD CAVERN CITY AIR TERM | HALIFAX |  |  | ELY YELLAND FIELD | ALBANY COUNTY AP | BURKE LAKEFRONT | CLINTON-SHERMAN | BURLINGTON PIERS | AURORA STATE | ALTOONA BLAIR CO ARPT |  | LA BAIE | PAWTUCKET (AWOS) |  | BEAUFORT MCAS | BROOKINGS (AWOS) | PRINCE ALBERT AP | CHATTANOOGA LOVELL FIELD AP | ABILENE REGIONAL AP [UT] | MOAB/CANYONLANDS [UO] | CHARLOTTESVILLE FAA |  | HO CHI MIHN | BREMERTON NATIONAL | EAU CLAIRE COUNTY AP | BLUEFIELD/MERCER CO [NREL] | CHEYENNE MUNICIPAL ARPT |  | 3 | AL | BC
Canada | AB | EDMONTON AP |  | #N/A |  | USA | AK | EDMONTON AP |  | ANAKTUVUK PASS | BIRMINGHAM MUNICIPAL AP | EL DORADO GOODWIN FIELD | DEER VALLEY/PHOENIX | BALLENAS ISLAND |  | BAKERSFIELD MEADOWS FIELD | ASPEN PITKIN CO SAR | GROTON NEW LONDON AP |  | FORT LAUDERDALE | ATHENS BEN EPPS AP | HONOLULU INTL ARPT | BOONE MUNI | CALDWELL (AWOS) | CAHOKIA/ST. LOUIS | FORT WAYNE INTL AP | DODGE CITY REGIONAL AP | FORT CAMPBELL AAF | BATON ROUGE RYAN ARPT | BOSTON LOGAN INT ARPT |  | HAGERSTOWN RGNL RIC | BANGOR INTERNATIONAL AP | BATTLE CREEK KELLOGG AP | ALEXANDRIA MUNICIPAL AP | FARMINGTON | GREENWOOD LEFLORE ARPT | BUTTE BERT MOONEY ARPT |  | CHARLOTTE DOUGLAS INTL ARPT | DICKINSON MUNICIPAL AP | BEATRICE MUNICIPAL |  | DILLANT HOPKINS | CALDWELL/ESSEX CO. | CLAYTON MUNICIPAL AIRPARK | SHEARWATER |  |  | FALLON NAAS | BINGHAMTON EDWIN A LINK FIELD | CINCINNATI MUNICIPAL AP LUNKI | FORT SILL POST FIELD AF | ERIEAU | BAKER MUNICIPAL AP | BRADFORD REGIONAL AP |  | LACADIE | PROVIDENCE T F GREEN STATE AR |  | CHARLESTON INTL ARPT | CHAN GURNEY MUNI | REGINA | CROSSVILLE MEMORIAL AP | ALICE INTL AP | OGDEN HILL AFB | DANVILLE FAA AP |  | MONTPELIER AP | EPHRATA AP FCWOS | GREEN BAY AUSTIN STRAUBEL INT | CHARLESTON YEAGER ARPT | CODY MUNI (AWOS) |  | 4 | AR | MB
Canada | AB | EDMONTON MUN AP |  | #N/A |  | USA | AL | EDMONTON MUN AP |  | ANCHORAGE INTL AP | CAIRNS FIELD FORT RUCKER | FAYETTEVILLE DRAKE FIELD | DOUGLAS BISBEE-DOUGLAS INTL A | COMOX AP |  | BEALE AFB | AURORA BUCKLEY FIELD ANGB | HARTFORD BRADLEY INTL AP |  | FORT LAUDERDALE HOLLYWOOD INT | ATLANTA HARTSFIELD INTL AP | KAHULUI AIRPORT | BURLINGTON MUNICIPAL AP | COEUR D`ALENE(AWOS) | CENTRAL ILLINOIS RG | GRISSOM ARB | EMPORIA MUNICIPAL AP | FORT KNOX GODMAN AAF | ENGLAND AFB | CHICOPEE FALLS WESTO |  | PATUXENT RIVER NAS | BAR HARBOR (AWOS) | BENTON HARBOR/ROSS | AUSTIN MUNI | JEFFERSON CITY MEM | GULFPORT BILOXI INT | CUT BANK MUNI AP |  | CHERRY POINT MCAS | FARGO HECTOR INTERNATIONAL AP | BELLEVUE OFFUTT AFB |  | LACONIA MUNI (AWOS) | CAPE MAY CO | CLOVIS CANNON AFB | SYDNEY AP |  |  | LAS VEGAS MCCARRAN INTL AP | BUFFALO NIAGARA INTL AP | CLEVELAND HOPKINS INTL AP | GAGE AIRPORT | LAGOON CITY | BURNS MUNICIPAL ARPT [UO] | BUTLER CO (AWOS) |  | LASSOMPTION |  |  | COLUMBIA METRO ARPT | ELLSWORTH AFB | SASKATOON | DYERSBURG MUNICIPAL AP | AMARILLO INTERNATIONAL AP [CANYON - UT] | OGDEN HINKLEY AIRPORT | DAVISON AAF |  | RUTLAND STATE | FAIRCHILD AFB | JANESVILLE/ROCK CO. | ELKINS ELKINS-RANDOLPH CO ARP | GILLETTE/GILLETTE-C |  | 5 | AZ | NB
Canada | AB | EDMONTON NAMAO |  | #N/A |  | USA | AR | EDMONTON NAMAO |  | ANCHORAGE MERRILL FIELD | DOTHAN MUNICIPAL AP | FLIPPIN (AWOS) | FLAGSTAFF PULLIAM ARPT | CRANBROOK AP |  | BISHOP AIRPORT | BARRANQUILLA | HARTFORD BRAINARD FD |  | FORT MYERS PAGE FIELD | AUGUSTA BUSH FIELD | KANEOHE BAY MCAS | CARROLL | IDAHO FALLS FANNING FIELD | CHICAGO MIDWAY AP | HUNTINGBURG | FORT RILEY MARSHALL AAF | HENDERSON CITY | FORT POLK AAF | LAWRENCE MUNI |  | SALISBURY WICOMICO CO AP | CARIBOU MUNICIPAL ARPT | CADILLAC WEXFORD CO AP | BAUDETTE INTERNATIONAL AP | JOPLIN MUNICIPAL AP | HATTIESBURG LAUREL | GLASGOW INTL ARPT |  | DARE CO RGNL | GRAND FORKS AF | BREWSTER FIELD ARPT |  | LEBANON MUNICIPAL | MCGUIRE AFB | CLOVIS MUNI (AWOS) |  |  |  | LOVELOCK DERBY FIELD | ELMIRA CORNING REGIONAL AP | COLUMBUS PORT COLUMBUS INTL A | HOBART MUNICIPAL AP | LONDON AP | CORVALLIS MUNI | DUBOIS FAA AP |  | LENNOXVILLE |  |  | FLORENCE REGIONAL AP | HURON REGIONAL ARPT |  | JACKSON MCKELLAR-SIPES REGL A | AUSTIN MUELLER MUNICIPAL AP [UT] | PROVO MUNI (AWOS) | FARMVILLE |  | SPRINGFIELD/HARTNES | FELTS FLD | LA CROSSE MUNICIPAL ARPT | HARRISON MARION RGN | JACKSON HOLE |  | 6 | CA | ON
Canada | AB | FORT MCMURRAY AP |  | #N/A |  | USA | AZ | FORT MCMURRAY AP |  | ANCHORAGE/ELMENDORF | HUNTSVILLE INTL/JONES FIELD | FORT SMITH REGIONAL AP | GRAND CANYON NATL P | DISCOVERY ISLAND |  | BLUE CANYON AP | BROOMFIELD/JEFFCO [BOULDER - SURFRAD] | NEW HAVEN TWEED AIRPORT |  | GAINESVILLE REGIONAL AP | BRUNSWICK GOLDEN IS | KONA INTL AT KEAHOL | CEDAR RAPIDS MUNICIPAL AP | JOSLIN FLD MAGIC VA [TWIN FALLS - UO] | CHICAGO OHARE INTL AP | INDIANAPOLIS INTL AP | GARDEN CITY MUNICIPAL AP | JACKSON JULIAN CARROLL AP | LAFAYETTE REGIONAL AP | MARTHAS VINEYARD |  |  | HOULTON INTL ARPT | CHIPPEWA CO INTL | BEMIDJI MUNICIPAL | KAISER MEM (AWOS) | JACKSON INTERNATIONAL AP | GLENDIVE(AWOS) |  | ELIZABETH CITY COAST GUARD AI [NREL] | GRAND FORKS INTERNATIONAL AP | BROKEN BOW MUNI |  | MANCHESTER AIRPORT | MILLVILLE MUNICIPAL AP | DEMING MUNI |  |  |  | MERCURY DESERT ROCK AP [SURFRAD] | FORT DRUM/WHEELER-S | DAYTON INTERNATIONAL AIRPORT | LAWTON MUNICIPAL | NORTH BAY AP | EUGENE MAHLON SWEET ARPT [UO] | ERIE INTERNATIONAL AP |  | MC TAVISH |  |  | GREENVILLE DOWNTOWN AP | MITCHELL (AWOS) |  | KNOXVILLE MCGHEE TYSON AP | BROWNSVILLE S PADRE ISL INTL | SAINT GEORGE (AWOS) | FRANKLIN NAAS |  |  | GRAY AAF | LONE ROCK FAA AP | HUNTINGTON TRI-STATE ARPT | LANDER HUNT FIELD |  | 7 | CO | PE
Canada | AB | GRAND PRAIRIE |  | #N/A |  | Canada | BC | GRAND PRAIRIE |  | ANIAK AIRPORT | MAXWELL AFB | HARRISON FAA AP | KINGMAN (AMOS) | ENTRANCE ISLAND |  | BLYTHE RIVERSIDE CO ARPT | CALI | OXFORD (AWOS) |  | HOMESTEAD AFB | BRUNSWICK MALCOLM MCKINNON AP | LIHUE AIRPORT | CHARITON | LEWISTON NEZ PERCE CNTY AP | CHICAGO/WAUKEGAN | LAFAYETTE PURDUE UNIV AP | GOODLAND RENNER FIELD | LEXINGTON BLUEGRASS AP | LAKE CHARLES REGIONAL ARPT | NANTUCKET MEMORIAL AP |  |  | MILLINOCKET MUNICIPAL AP | DETROIT CITY AIRPORT | BENSON MUNI | KANSAS CITY DOWNTOWN AP | KEESLER AFB | GREAT FALLS INTL ARPT |  | FAYETTEVILLE POPE AFB | JAMESTOWN MUNICIPAL ARPT | COLUMBUS MUNI |  | MOUNT WASHINGTON | NEWARK INTERNATIONAL ARPT | FARMINGTON FOUR CORNERS REGL |  |  |  | NELLIS AFB | GLENS FALLS AP | FINDLAY AIRPORT | MCALESTER MUNICIPAL AP | OTTAWA | KLAMATH FALLS INTL AP [UO] | FRANKLIN |  | MONT JOLI AB |  |  | GREER GREENV-SPARTANBRG AP | MOBRIDGE |  | MEMPHIS INTERNATIONAL AP | CAMP MABRY | SALT LAKE CITY INT ARPT [ISIS] | HILLSVILLE |  |  | HANFORD | MADISON DANE CO REGIONAL ARPT [ISIS] | LEWISBURG/GREENBRIE | LARAMIE GENERAL BREES FIELD |  | 8 | CT | QC
Canada | AB | LACOMBE |  | #N/A |  | India | BD | LACOMBE |  | ANNETTE ISLAND AP | MOBILE DOWNTOWN AP | JONESBORO MUNI | LUKE AFB | ESQUIMALT HARBOUR |  | BURBANK-GLENDALE-PASADENA AP | CARTAGENA |  |  | JACKSONVILLE INTL ARPT | COLUMBUS METROPOLITAN ARPT | MOLOKAI (AMOS) | CHARLES CITY | MOUNTAIN HOME AFB | DECATUR | MONROE CO | GREAT BEND (AWOS) | LONDON-CORBIN AP | MONROE REGIONAL AP | NEW BEDFORD RGNL |  |  | NORTHERN AROOSTOOK | DETROIT METROPOLITAN ARPT | BRAINERD/WIELAND | KANSAS CITY INT ARPT | MCCOMB PIKE COUNTY AP | HAVRE CITY-COUNTY AP |  | FAYETTEVILLE RGNL G | MINOT AFB | FALLS CITY/BRENNER |  | PEASE INTL TRADEPOR | TETERBORO AIRPORT | GALLUP SEN CLARKE FLD |  |  |  | RENO TAHOE INTERNATIONAL AP | ISLIP LONG ISL MACARTHUR AP | MANSFIELD LAHM MUNICIPAL ARPT | OKLAHOMA CITY TINKER AFB | PETERBOROUGH AP | LA GRANDE MUNI AP | HARRISBURG CAPITAL CITY ARPT |  | MONT-ORFORD |  |  | MYRTLE BEACH AFB | PIERRE MUNICIPAL AP |  | NASHVILLE INTERNATIONAL AP | CHILDRESS MUNICIPAL AP | VERNAL | HOT SPRINGS/INGALLS |  |  | HOQUIAM AP | MANITOWOC MUNI AWOS | MARTINSBURG EASTERN WV REG AP | RAWLINS MUNICIPAL AP |  | 9 | DE | SK
Canada | AB | LETHBRIDGE |  | #N/A |  | USA | CA | LETHBRIDGE |  | ANVIK | MOBILE REGIONAL AP | LITTLE ROCK ADAMS FIELD | PAGE MUNI (AMOS) | FORT NELSON |  | CAMARILLO (AWOS) | COLORADO SPRINGS MUNI AP |  |  | JACKSONVILLE NAS | DEKALB PEACHTREE |  | CLARINDA | POCATELLO REGIONAL AP | MARION REGIONAL | NEW DELHI SAFDARJUNG AP | HAYS MUNI (AWOS) | LOUISVILLE BOWMAN FIELD | NEW IBERIA NAAS | NORTH ADAMS |  |  | PORTLAND INTL JETPORT | DETROIT WILLOW RUN AP | CAMBRIDGE MUNI | KIRKSVILLE REGIONAL AP | MERIDIAN KEY FIELD | HELENA REGIONAL AIRPORT |  | FORT BRAGG SIMMONS AAF | MINOT FAA AP | FREMONT MUNI ARPT |  |  | TRENTON MERCER COUNTY AP | HOLLOMAN AFB |  |  |  | TONOPAH AIRPORT | JAMESTOWN (AWOS) | OHIO STATE UNIVERSI | OKLAHOMA CITY WILL ROGERS WOR | PORT WELLER | LAKEVIEW (AWOS) | JOHNSTOWN CAMBRIA COUNTY AP |  | MONTREAL |  |  | SUMTER SHAW AFB | RAPID CITY REGIONAL ARPT |  |  | COLLEGE STATION EASTERWOOD FL | WENDOVER USAF AUXILIARY FIELD | LANGLEY AFB |  |  | KELSO WB AP | MARSHFIELD MUNI | MORGANTOWN HART FIELD | RIVERTON MUNICIPL AP |  | 10 | FL | YT
Canada | AB | MEDICINE AP |  | #N/A |  | USA | CO | MEDICINE AP |  | BARROW W POST-W ROGERS ARPT [NSA - ARM] | MONTGOMERY DANNELLY FIELD | LITTLE ROCK AFB | PHOENIX SKY HARBOR INTL AP | FORT SAINT JOHN |  | CAMP PENDLETON MCAS | CORTEZ/MONTEZUMA |  |  | JACKSONVILLE/CRAIG | FORT BENNING LAWSON |  | CLINTON MUNI (AWOS) | SALMON/LEMHI (AWOS) | MOLINE QUAD CITY INTL AP | PATNA | HILL CITY MUNICIPAL AP | LOUISVILLE STANDIFORD FIELD | NEW ORLEANS ALVIN CALLENDER F | NORWOOD MEMORIAL |  |  | PRESQUE ISLE MUNICIP | ESCANABA (AWOS) | CLOQUET (AWOS) | POPLAR BLUFF(AMOS) | MERIDIAN NAAS | KALISPELL GLACIER PK INT AR |  | GOLDSBORO SEYMOUR JOHNSON AFB | WILLISTON SLOULIN INTL AP | GRAND ISLAND CENTRAL NE REGIO |  |  |  | LAS VEGAS MUNICIPAL ARPT |  |  |  | WINNEMUCCA MUNICIPAL ARPT | MASSENA AP | TOLEDO EXPRESS AIRPORT | OKLAHOMA CITY/WILEY | SAULT STE MARIE | MEDFORD ROGUE VALLEY INTL AP [ASHLAND - UO] | LANCASTER |  | MONTREAL-MIRABEL |  |  |  | SIOUX FALLS FOSS FIELD |  |  | CORPUS CHRISTI INTL ARPT [UT] |  | LEESBURG/GODFREY |  |  | MOSES LAKE GRANT COUNTY AP | MILWAUKEE MITCHELL INTL AP | PARKERSBURG WOOD COUNTY AP | SHERIDAN COUNTY ARPT |  | 11 | GA | -
Canada | AB | RED DEER AP |  | #N/A |  | Colombia | CO | RED DEER AP |  | BETHEL AIRPORT | MUSCLE SHOALS REGIONAL AP | PINE BLUFF FAA AP | PRESCOTT LOVE FIELD | KAMLOOPS AP |  | CARLSBAD/PALOMAR | CRAIG-MOFFAT |  |  | KEY WEST INTL ARPT | FULTON CO ARPT BROW |  | COUNCIL BLUFFS |  | MOUNT VERNON (AWOS) | SOUTH BEND MICHIANA RGNL AP | HUTCHINSON MUNICIPAL AP | PADUCAH BARKLEY REGIONAL AP | NEW ORLEANS INTL ARPT | OTIS ANGB |  |  | ROCKLAND/KNOX(AWOS) | FLINT BISHOP INTL ARPT | CRANE LAKE (AWOS) | SPRINGFIELD REGIONAL ARPT | NATCHEZ/HARDY(AWOS) | LEWISTOWN MUNICIPAL ARPT |  | GREENSBORO PIEDMONT TRIAD INT |  | HASTINGS MUNICIPAL |  |  |  | ROSWELL INDUSTRIAL AIR PARK |  |  |  |  | MONTICELLO(AWOS) | YOUNGSTOWN REGIONAL AIRPORT | PONCA CITY MUNICIPAL AP [SGP - ARM] | SUDBURY AP | NORTH BEND MUNI AIRPORT | MIDDLETOWN HARRISBURG INTL AP |  | NICOLET |  |  |  | WATERTOWN MUNICIPAL AP |  |  | CORPUS CHRISTI NAS |  | LYNCHBURG REGIONAL ARPT |  |  | OLYMPIA AIRPORT | MINOCQUA/WOODRUFF | WHEELING OHIO COUNTY AP | WORLAND MUNICIPAL |  | 12 | HI | -
Canada | AB | SPRINGBANK |  | #N/A |  | USA | CT | SPRINGBANK |  | BETTLES FIELD | TUSCALOOSA MUNICIPAL AP | ROGERS (AWOS) | SAFFORD (AMOS) | KELOWNA AP |  | CHINO AIRPORT | DENVER INTL AP |  |  | KEY WEST NAS | HUNTER AAF |  | CRESTON |  | PEORIA GREATER PEORIA AP | TERRE HAUTE HULMAN REGIONAL A | LIBERAL MUNI | SOMERSET(AWOS) | NEW ORLEANS LAKEFRONT AP | PLYMOUTH MUNICIPAL |  |  | SANFORD MUNI (AWOS) | GRAND RAPIDS KENT COUNTY INT | CROOKSTON MUNI FLD | ST JOSEPH ROSECRANS MEMORIAL | TUPELO C D LEMONS ARPT | LIVINGSTON MISSION FIELD |  | HICKORY REGIONAL AP |  | KEARNEY MUNI (AWOS) |  |  |  | SANTA FE COUNTY MUNICIPAL AP |  |  |  |  | NEW YORK CENTRAL PRK OBS BELV | ZANESVILLE MUNICIPAL AP | STILLWATER RGNL | THUNDER BAY AP | PENDLETON E OR REGIONAL AP | PHILADELPHIA INTERNATIONAL AP |  | POINT-AU-PERE | [6 empty] | COTULLA FAA AP |  | MANASSAS MUNI(AWOS) |  |  | PASCO | MOSINEE/CENTRAL WI |  |  |  | 13 | IA | -
United Arab Emirates | AE | DUBAI INT AP |  | #N/A |  | USA | DE |  |  | BIG DELTA ALLEN AAF |  | SILOAM SPRING(AWOS) | SCOTTSDALE MUNI | MALAHAT |  | CHULA VISTA BROWN FIELD NAAS | DENVER/CENTENNIAL [GOLDEN - NREL] |  |  | MACDILL AFB | MACON MIDDLE GA REGIONAL AP |  | DECORAH |  | QUINCY MUNI BALDWIN FLD |  | MANHATTAN RGNL |  | PATTERSON MEMORIAL | PROVINCETOWN (AWOS) |  |  | WATERVILLE (AWOS) | HANCOCK HOUGHTON CO AP | DETROIT LAKES(AWOS) | ST LOUIS LAMBERT INT ARPT |  | MILES CITY MUNICIPAL ARPT |  | JACKSONVILLE (AWOS) |  | LINCOLN MUNICIPAL ARPT |  |  |  | SIERRA BLANCA RGNL |  |  |  |  | NEW YORK J F KENNEDY INT AR |  | TULSA INTERNATIONAL AIRPORT | TIMMINS AP | PORTLAND INTERNATIONAL AP | PHILADELPHIA NE PHILADELPHIA |  | QUEBEC AP | [6 empty] | COX FLD |  | MARION / WYTHEVILLE |  |  | PULLMAN/MOSCOW RGNL | PHILLIPS/PRICE CO. |  |  |  | 14 | ID | -
USA | AK | ADAK NAS |  | #N/A |  | USA | FL |  |  | BIG RIVER LAKE |  | SPRINGDALE MUNI | TUCSON INTERNATIONAL AP | NORTH VANCOUVER |  | CONCORD CONCORD-BUCHANAN FIEL | DURANGO/LA PLATA CO |  |  | MARATHON AIRPORT | MARIETTA DOBBINS AFB |  | DENISON |  | ROCKFORD GREATER ROCKFORD AP |  | MCCONNELL AFB |  | SHREVEPORT DOWNTOWN | WESTFIELD BARNES MUNI AP |  |  | WISCASSET | HOUGHTON LAKE ROSCOMMON CO AR | DULUTH INTERNATIONAL ARPT | ST LOUIS SPIRIT OF ST LOUIS A |  | MISSOULA INTERNATIONAL AP |  | NEW BERN CRAVEN CO REGL AP |  | MCCOOK MUNICIPAL |  |  |  | TAOS MUNI APT(AWOS) |  |  |  |  | NEW YORK LAGUARDIA ARPT |  | VANCE AFB | TORONTO AP | PORTLAND/HILLSBORO | PITTSBURGH ALLEGHENY CO AP |  | SHERBROOKE AP | [6 empty] | DALHART MUNICIPAL AP |  | MARTINSVILLE |  |  | QUILLAYUTE STATE AIRPORT | RHINELANDER ONEIDA |  |  |  | 15 | IL | -
USA | AK | AMBLER |  | #N/A |  | USA | GA |  |  | BIRCHWOOD |  | STUTTGART (AWOS) | WINSLOW MUNICIPAL AP | PENTICTON AP |  | CRESCENT CITY FAA AI | EAGLE COUNTY AP |  |  | MAYPORT NS | MOODY AFB/VALDOSTA |  | DES MOINES INTL AP |  | SOUTHERN ILLINOIS |  | NEWTON (AWOS) |  | SHREVEPORT REGIONAL ARPT | WORCESTER REGIONAL ARPT |  |  |  | HOWELL | ELY MUNI | VICHY ROLLA NATL ARPT |  | SIDNEY-RICHLAND |  | NEW RIVER MCAF |  | NORFOLK KARL STEFAN MEM ARPT |  |  |  | TRUTH OR CONSEQUENCES MUNI AP |  |  |  |  | NIAGARA FALLS AF |  |  | TORONTO ISLAND AP | PORTLAND/TROUTDALE | PITTSBURGH INTERNATIONAL AP |  | ST ANICET | [6 empty] | DALLAS-FORT WORTH INTL AP |  | MELFA/ACCOMACK ARPT |  |  | RENTON MUNI | RICE LAKE MUNICIPAL |  |  |  | 16 | IN | -
USA | AK | ANAKTUVUK PASS |  | #N/A |  | USA | HI |  |  | COLD BAY ARPT |  | TEXARKANA WEBB FIELD | YUMA INTL ARPT | PITT MEADOWS |  | DAGGETT BARSTOW-DAGGETT AP | FORT COLLINS (AWOS) |  |  | MELBOURNE REGIONAL AP | ROME R B RUSSELL AP |  | DUBUQUE REGIONAL AP |  | SPRINGFIELD CAPITAL AP |  | OLATHE/JOHNSON CO. | [6 empty] | IRON MOUNTAIN/FORD | EVELETH MUNI (AWOS) | WHITEMAN AFB |  | WOLF POINT INTL [FORT PECK - SURFRAD] |  | PITT GREENVILLE ARP |  | NORTH PLATTE REGIONAL AP | [8 empty] | POUGHKEEPSIE DUTCHESS CO AP |  |  | TORONTO | REDMOND ROBERTS FIELD | READING SPAATZ FIELD |  | STE ANNE DE BELLEVUE | [6 empty] | DALLAS/ADDISON ARPT |  | NEWPORT NEWS |  |  | SEATTLE BOEING FIELD [ISIS] | STURGEON BAY |  |  |  | 17 | KS | -
USA | AK | ANCHORAGE INTL AP |  | #N/A |  | USA | IA |  |  | CORDOVA |  | WALNUT RIDGE (AWOS) | YUMA MCAS | PRINCE GEORGE |  | EDWARDS AFB | GRAND JUNCTION WALKER FIELD |  |  | MIAMI INTL AP | SAVANNAH INTL AP |  | ESTHERVILLE MUNI |  | STERLING ROCKFALLS |  | RUSSELL MUNICIPAL AP | [6 empty] | IRONWOOD (AWOS) | FAIRMONT MUNI(AWOS) |  |  |  |  | RALEIGH DURHAM INTERNATIONAL |  | OMAHA EPPLEY AIRFIELD | [8 empty] | REPUBLIC |  |  | TRENTON AP | ROSEBURG REGIONAL AP | STATE COLLEGE [PENN STATE - SURFRAD] |  | STE FOY | [6 empty] | DALLAS/REDBIRD ARPT |  | NORFOLK INTERNATIONAL AP |  |  | SEATTLE SEATTLE-TACOMA INTL A | WATERTOWN |  |  |  | 18 | KY | -
USA | AK | ANCHORAGE MERRILL FIELD |  | #N/A |  | USA | ID |  |  | DEADHORSE |  |  |  | SMITHERS AP |  | FRESNO YOSEMITE INTL AP | GREELEY/WELD (AWOS) |  |  | MIAMI/KENDALL-TAMIA | VALDOSTA WB AIRPORT |  | FAIR FIELD |  | UNIV OF ILLINOIS WI [BONDVILLE - SURFRAD] |  | SALINA MUNICIPAL AP | [6 empty] | JACKSON REYNOLDS FIELD | FARIBAULT MUNI AWOS |  |  |  |  | ROCKY MOUNT WILSON |  | OMAHA WSFO | [8 empty] | ROCHESTER GREATER ROCHESTER I |  |  | WINDSOR | SALEM MCNARY FIELD | WASHINGTON (AWOS) |  | TROIS RIVIERES | [6 empty] | DEL RIO [UT] |  | NORFOLK NAS |  |  | SNOHOMISH CO | WAUSAU MUNICIPAL ARPT |  |  |  | 19 | LA | -
USA | AK | ANCHORAGE/ELMENDORF |  | #N/A |  | USA | IL |  |  | DILLINGHAM (AMOS) |  |  |  | SUMMERLAND |  | FULLERTON MUNICIPAL | GUNNISON CO. (AWOS) |  |  | MIAMI/OPA LOCKA | WARNER ROBINS AFB |  | FORT DODGE (AWOS) |  | W. CHICAGO/DU PAGE |  | TOPEKA FORBES FIELD | [6 empty] | KALAMAZOO BATTLE CR | FLYING CLOUD |  |  |  |  | SOUTHERN PINES AWOS |  | SCOTTSBLUFF W B HEILIG FIELD | [8 empty] | STEWART FIELD |  |  |  | SEXTON SUMMIT | WILKES-BARRE SCRANTON INTL AP |  | VARENNES | [6 empty] | DEL RIO LAUGHLIN AFB |  | OCEANA NAS |  |  | SPOKANE INTERNATIONAL AP [CHENEY - UO] | WITTMAN RGNL |  |  |  | 20 | MA | -
USA | AK | ANIAK AIRPORT |  | #N/A |  | USA | IN |  |  | DUTCH HARBOR |  |  |  | VANCOUVER |  | HAYWARD AIR TERM | HAYDEN/YAMPA (AWOS) |  |  | NAPLES MUNICIPAL |  |  | FORT MADISON |  |  |  | TOPEKA MUNICIPAL AP | [6 empty] | LANSING CAPITAL CITY ARPT | FOSSTON(AWOS) |  |  |  |  | WILMINGTON INTERNATIONAL ARPT |  | SIDNEY MUNICIPAL AP | [8 empty] | SYRACUSE HANCOCK INT ARPT |  |  |  |  | WILLIAMSPORT REGIONAL AP | [8 empty] | DRAUGHON MILLER CEN |  | QUANTICO MCAS |  |  | STAMPEDE PASS |  |  |  |  | 21 | MD | -
USA | AK | ANNETTE ISLAND AP |  | #N/A |  | India | IN |  |  | EMMONAK |  |  |  | VERNON |  | IMPERIAL | LA JUNTA MUNICIPAL AP |  |  | NASA SHUTTLE FCLTY |  |  | KEOKUK MUNI |  |  |  | WICHITA MID-CONTINENT AP | [6 empty] | MANISTEE (AWOS) | GLENWOOD (ASOS) |  |  |  |  | WINSTON-SALEM REYNOLDS AP |  | TEKAMAH (ASOS) | [8 empty] | UTICA ONEIDA COUNTY AP |  |  |  |  | WILLOW GROVE NAS | [8 empty] | EL PASO INTERNATIONAL AP [UT] |  | RICHMOND INTERNATIONAL AP |  |  | TACOMA MCCHORD AFB |  |  |  |  | 22 | ME | -
USA | AK | ANVIK |  | #N/A |  | USA | KS |  |  | FAIRBANKS INTL ARPT |  |  |  | VICTORIA AP |  | JACK NORTHROP FLD H | LAMAR MUNICIPAL |  |  | OCALA MUNI (AWOS) |  |  | KNOXVILLE |  |  |  | WICHITA/COL. JABARA | [6 empty] | MENOMINEE (AWOS) | GRAND RAPIDS(AWOS) | [6 empty] | VALENTINE MILLER FIELD | [8 empty] | WATERTOWN AP | [13 empty] | FORT HOOD |  | ROANOKE REGIONAL AP |  |  | TACOMA NARROWS |  |  |  |  | 23 | MI | -
USA | AK | BARROW W POST-W ROGERS ARPT [NSA - ARM] |  | #N/A |  | USA | KY |  |  | FAIRBANKS/EIELSON A |  |  |  | VICTORIA |  | LANCASTER GEN WM FOX FIELD | LEADVILLE/LAKE CO. |  |  | ORLANDO EXECUTIVE AP |  |  | LE MARS | [10 empty] | MOUNT CLEMENS SELFRIDGE FLD | HALLOCK | [15 empty] | WESTHAMPTON GABRESKI AP | [13 empty] | FORT WORTH ALLIANCE |  | SHANNON ARPT |  |  | THE DALLES MUNICIPAL ARPT |  |  |  |  | 24 | MN | -
USA | AK | BETHEL AIRPORT |  | #N/A |  | USA | LA |  |  | FORT YUKON |  |  |  | VICTORIA UNIV |  | LEMOORE REEVES NAS | LIMON |  |  | ORLANDO INTL ARPT |  |  | MASON CITY MUNICIPAL ARPT | [10 empty] | MUSKEGON COUNTY ARPT | HIBBING CHISHOLM-HIBBING AP | [15 empty] | WHITE PLAINS WESTCHESTER CO A | [13 empty] | FORT WORTH MEACHAM |  | STAUNTON/SHENANDOAH |  |  | WALLA WALLA CITY COUNTY AP |  |  |  |  | 25 | MO | -
USA | AK | BETTLES FIELD |  | #N/A |  | USA | MA |  |  | GAMBELL |  |  |  | W VANCOUVER |  | LIVERMORE MUNICIPAL | MONTROSE CO. ARPT |  |  | ORLANDO SANFORD AIRPORT |  |  | MONTICELLO MUNI | [10 empty] | OAKLAND CO INTL | HUTCHINSON (AWOS) | [29 empty] | FORT WORTH NAS |  | VIRGINIA TECH ARPT |  |  | WENATCHEE/PANGBORN |  |  |  |  | 26 | MS | -
USA | AK | BIG DELTA ALLEN AAF |  | #N/A |  | USA | MB |  |  | GULKANA INTERMEDIATE FIELD |  |  |  | WHISTLER |  | LOMPOC (AWOS) | PUEBLO MEMORIAL AP |  |  | PANAMA CITY BAY CO |  |  | MUSCATINE | [10 empty] | OSCODA WURTSMITH AFB | INTERNATIONAL FALLS INTL AP | [29 empty] | GALVESTON/SCHOLES |  | WASHINGTON DC DULLES INT AR [STERLING - ISIS] |  |  | WHIDBEY ISLAND NAS |  |  |  |  | 27 | MT | -
USA | AK | BIG RIVER LAKE |  | #N/A |  | USA | MD |  |  | GUSTAVUS |  |  |  | WHITE ROCK |  | LONG BEACH DAUGHERTY FLD | RIFLE/GARFIELD RGNL |  |  | PENSACOLA FOREST SHERMAN NAS |  |  | NEWTON MUNI | [10 empty] | PELLSTON EMMET COUNTY AP | LITCHFIELD MUNI | [29 empty] | GEORGETOWN (AWOS) |  | WASHINGTON DC REAGAN AP |  |  | WILLIAM R FAIRCHILD |  |  |  |  | 28 | NC | -
USA | AK | BIRCHWOOD |  | #N/A |  | USA | ME |  |  | HOMER ARPT | [5 empty] | LOS ANGELES INTL ARPT | TRINIDAD LAS ANIMAS COUNTY AP |  |  | PENSACOLA REGIONAL AP |  |  | OELWEN | [10 empty] | SAGINAW TRI CITY INTL AP | LITTLE FALLS (AWOS) | [29 empty] | HARLINGEN RIO GRANDE VALLEY I |  | WINCHESTER RGNL |  |  | YAKIMA AIR TERMINAL |  |  |  |  | 29 | ND | -
USA | AK | COLD BAY ARPT |  | #N/A |  | USA | MI |  |  | HOOPER BAY | [5 empty] | MARCH AFB |  |  |  | SARASOTA BRADENTON |  |  | ORANGE CITY | [10 empty] | SAULT STE MARIE SANDERSON FIE | MANKATO(AWOS) | [29 empty] | HONDO MUNICIPAL AP |  | WISE/LONESOME PINE | [7 empty] | 30 | NE | -
USA | AK | CORDOVA |  | #N/A |  | USA | MN |  |  | HYDABURG SEAPLANE | [5 empty] | MERCED/MACREADY FLD |  |  |  | SOUTHWEST FLORIDA I |  |  | OTTUMWA INDUSTRIAL AP | [10 empty] | ST.CLAIR COUNTY INT | MINNEAPOLIS-ST PAUL INT ARP | [29 empty] | HOUSTON BUSH INTERCONTINENTAL | [9 empty] | 31 | NL | -
USA | AK | DEADHORSE |  | #N/A |  | USA | MO |  |  | ILIAMNA ARPT | [5 empty] | MODESTO CITY-COUNTY AP |  |  |  | ST LUCIE CO INTL |  |  | RED OAK | [10 empty] | TRAVERSE CITY CHERRY CAPITAL | MINNEAPOLIS/CRYSTAL | [29 empty] | HOUSTON ELLINGTON AFB [CLEAR LAKE - UT] | [9 empty] | 32 | NH | -
USA | AK | DILLINGHAM (AMOS) |  | #N/A |  | USA | MS |  |  | JUNEAU INT ARPT | [5 empty] | MONTAGUE SISKIYOU COUNTY AP |  |  |  | ST PETERSBURG ALBERT WHITTED |  |  | SHELDON | [11 empty] | MORA MUNI (AWOS) | [29 empty] | HOUSTON WILLIAM P HOBBY AP | [9 empty] | 33 | NJ | -
USA | AK | DUTCH HARBOR |  | #N/A |  | USA | MT |  |  | KAKE SEAPLANE BASE | [5 empty] | MONTEREY NAF |  |  |  | ST PETERSBURG CLEAR |  |  | SHENANDOAH MUNI | [11 empty] | MORRIS MUNI (AWOS) | [29 empty] | HOUSTON/D.W. HOOKS | [9 empty] | 34 | NM | -
USA | AK | EMMONAK |  | #N/A |  | Canada | NB |  |  | KENAI MUNICIPAL AP | [5 empty] | MOUNTAIN VIEW MOFFETT FLD NAS |  |  |  | TALLAHASSEE REGIONAL AP [ISIS] |  |  | SIOUX CITY SIOUX GATEWAY AP | [11 empty] | NEW ULM MUNI (AWOS) | [29 empty] | KINGSVILLE | [9 empty] | 35 | NS | -
USA | AK | FAIRBANKS INTL ARPT |  | #N/A |  | USA | NC |  |  | KETCHIKAN INTL AP | [5 empty] | NAPA CO. AIRPORT |  |  |  | TAMPA INTERNATIONAL AP |  |  | SPENCER | [11 empty] | ORR | [29 empty] | LAREDO INTL AP [UT] | [9 empty] | 36 | NT | -
USA | AK | FAIRBANKS/EIELSON A |  | #N/A |  | USA | ND |  |  | KING SALMON ARPT | [5 empty] | NEEDLES AIRPORT |  |  |  | TYNDALL AFB |  |  | STORM LAKE | [11 empty] | OWATONNA (AWOS) | [29 empty] | LONGVIEW GREGG COUNTY AP [OVERTON - UT] | [9 empty] | 37 | NU | -
USA | AK | FORT YUKON |  | #N/A |  | USA | NE |  |  | KODIAK AIRPORT | [5 empty] | OAKLAND METROPOLITAN ARPT |  |  |  | VALPARAISO EGLIN AFB |  |  | WASHINGTON | [11 empty] | PARK RAPIDS MUNICIPAL AP | [29 empty] | LUBBOCK INTERNATIONAL AP | [9 empty] | 38 | NV | -
USA | AK | GAMBELL |  | #N/A |  | USA | NL |  |  | KOTZEBUE RALPH WEIN MEMORIAL | [5 empty] | OXNARD AIRPORT |  |  |  | VALPARAISO HURLBURT |  |  | WATERLOO MUNICIPAL AP | [11 empty] | PIPESTONE (AWOS) | [29 empty] | LUFKIN ANGELINA CO | [9 empty] | 39 | NY | -
USA | AK | GULKANA INTERMEDIATE FIELD |  | #N/A |  | USA | NH |  |  | LAKE HOOD SEAPLANE | [5 empty] | PALM SPRINGS INTL |  |  |  | VERO BEACH MUNICIPAL ARPT |  |  | WEBSTER CITY | [11 empty] | RED WING | [29 empty] | MARFA AP | [9 empty] | 40 | OH | -
USA | AK | GUSTAVUS |  | #N/A |  | USA | NJ |  |  | MCGRATH ARPT | [5 empty] | PALM SPRINGS THERMAL AP |  |  |  | WHITING FIELD NAAS | [14 empty] | REDWOOD FALLS MUNI | [29 empty] | MC GREGOR (AWOS) | [9 empty] | 41 | OK | -
USA | AK | HOMER ARPT |  | #N/A |  | USA | NM |  |  | MEKORYUK | [5 empty] | PALMDALE AIRPORT | [18 empty] | ROCHESTER INTERNATIONAL ARPT | [29 empty] | MCALLEN MILLER INTL AP [EDINBURG - UT] | [9 empty] | 42 | OR | -
USA | AK | HOOPER BAY |  | #N/A |  | USA | NS |  |  | MIDDLETON ISLAND AUT | [5 empty] | PASO ROBLES MUNICIPAL ARPT | [18 empty] | ROSEAU MUNI (AWOS) | [29 empty] | MIDLAND INTERNATIONAL AP | [9 empty] | 43 | PA | -
USA | AK | HYDABURG SEAPLANE |  | #N/A |  | USA | NT |  |  | NENANA MUNICIPAL AP | [5 empty] | POINT MUGU NF | [18 empty] | SILVER BAY | [29 empty] | MINERAL WELLS MUNICIPAL AP | [9 empty] | 44 | RI | -
USA | AK | ILIAMNA ARPT |  | #N/A |  | USA | NU |  |  | NOME MUNICIPAL ARPT | [5 empty] | PORTERVILLE (AWOS) | [18 empty] | SOUTH ST PAUL MUNI | [29 empty] | NACOGDOCHES (AWOS) | [9 empty] | 45 | SC | -
USA | AK | JUNEAU INT ARPT |  | #N/A |  | USA | NV |  |  | NORTHWAY AIRPORT | [5 empty] | RED BLUFF MUNICIPAL ARPT | [18 empty] | ST CLOUD REGIONAL ARPT | [29 empty] | PALACIOS MUNICIPAL AP | [9 empty] | 46 | SD | -
USA | AK | KAKE SEAPLANE BASE |  | #N/A |  | USA | NY |  |  | PALMER MUNICIPAL | [5 empty] | REDDING MUNICIPAL ARPT | [18 empty] | ST PAUL DOWNTOWN AP | [29 empty] | PORT ARTHUR JEFFERSON COUNTY | [9 empty] | 47 | TN | -
USA | AK | KENAI MUNICIPAL AP |  | #N/A |  | USA | OH |  |  | PETERSBURG | [5 empty] | RIVERSIDE MUNI | [18 empty] | THIEF RIVER(AWOS) | [29 empty] | RANDOLPH AFB | [9 empty] | 48 | TX | -
USA | AK | KETCHIKAN INTL AP |  | #N/A |  | USA | OK |  |  | POINT HOPE (AWOS) | [5 empty] | SACRAMENTO EXECUTIVE ARPT | [18 empty] | WHEATON NDB (AWOS) | [29 empty] | ROCKPORT/ARANSAS CO | [9 empty] | 49 | UT | -
USA | AK | KING SALMON ARPT |  | #N/A |  | Canada | ON |  |  | PORT HEIDEN | [5 empty] | SACRAMENTO METROPOLITAN AP | [18 empty] | WILLMAR | [29 empty] | SAN ANGELO MATHIS FIELD | [9 empty] | 50 | VA | -
USA | AK | KODIAK AIRPORT |  | #N/A |  | USA | OR |  |  | SAINT MARY`S (AWOS) | [5 empty] | SALINAS MUNICIPAL AP | [18 empty] | WINONA MUNI (AWOS) | [29 empty] | SAN ANTONIO INTL AP | [9 empty] | 51 | VT | -
USA | AK | KOTZEBUE RALPH WEIN MEMORIAL |  | #N/A |  | USA | PA |  |  | SAND POINT | [5 empty] | SAN DIEGO LINDBERGH FIELD | [18 empty] | WORTHINGTON (AWOS) | [29 empty] | SAN ANTONIO KELLY FIELD AFB | [9 empty] | 52 | WA | -
USA | AK | LAKE HOOD SEAPLANE |  | #N/A |  | Canada | PE |  |  | SAVOONGA | [5 empty] | SAN DIEGO MIRAMAR NAS | [48 empty] | SAN ANTONIO/STINSON | [9 empty] | 53 | WI | -
USA | AK | MCGRATH ARPT |  | #N/A |  | Canada | QC |  |  | SELAWIK | [5 empty] | SAN DIEGO NORTH ISLAND NAS | [48 empty] | TYLER/POUNDS FLD | [9 empty] | 54 | WV | -
USA | AK | MEKORYUK |  | #N/A |  | USA | RI |  |  | SEWARD | [5 empty] | SAN DIEGO/MONTGOMER | [48 empty] | VICTORIA REGIONAL AP | [9 empty] | 55 | WY | -
USA | AK | MIDDLETON ISLAND AUT |  |  |  | Saudi Arabia | SA |  |  | SHEMYA AFB | [5 empty] | SAN FRANCISCO INTL AP | [48 empty] | WACO REGIONAL AP | [9 empty] | 56
USA | AK | NENANA MUNICIPAL AP |  |  |  | USA | SC |  |  | SHISHMAREF (AWOS) | [5 empty] | SAN JOSE INTL AP | [48 empty] | WICHITA FALLS MUNICIPAL ARPT | [9 empty] | 57
USA | AK | NOME MUNICIPAL ARPT |  |  |  | USA | SD |  |  | SITKA JAPONSKI AP | [5 empty] | SAN LUIS CO RGNL | [48 empty] | WINK WINKLER COUNTY AP | [9 empty] | 58
USA | AK | NORTHWAY AIRPORT |  |  |  | Canada | SK |  |  | SKAGWAY AIRPORT | [5 empty] | SANDBERG | [58 empty] | 59
USA | AK | PALMER MUNICIPAL |  |  |  | USA | TN |  |  | SLEETMUTE | [5 empty] | SANTA BARBARA MUNICIPAL AP | [58 empty] | 60
USA | AK | PETERSBURG |  |  |  | USA | TX |  |  | SOLDOTNA | [5 empty] | SANTA MARIA PUBLIC ARPT | [58 empty] | 61
USA | AK | POINT HOPE (AWOS) |  |  |  | USA | UT |  |  | ST PAUL ISLAND ARPT | [5 empty] | SANTA MONICA MUNI | [58 empty] | 62
USA | AK | PORT HEIDEN |  |  |  | USA | VA |  |  | TALKEETNA STATE ARPT | [5 empty] | SANTA ROSA (AWOS) | [58 empty] | 63
USA | AK | SAINT MARY`S (AWOS) |  |  |  | USA | VT |  |  | TANANA RALPH M CALHOUN MEM AP | [5 empty] | STOCKTON METROPOLITAN ARPT | [58 empty] | 64
USA | AK | SAND POINT |  |  |  | USA | WA |  |  | TOGIAK VILLAGE AWOS | [5 empty] | TRAVIS FIELD AFB | [58 empty] | 65
USA | AK | SAVOONGA |  |  |  | USA | WI |  |  | UNALAKLEET FIELD | [5 empty] | TRUCKEE-TAHOE | [58 empty] | 66
USA | AK | SELAWIK |  |  |  | USA | WV |  |  | VALDEZ PIONEER FIEL | [5 empty] | UKIAH MUNICIPAL AP | [58 empty] | 67
USA | AK | SEWARD |  |  |  | USA | WY |  |  | VALDEZ WSO | [5 empty] | VAN NUYS AIRPORT | [58 empty] | 68
USA | AK | SHEMYA AFB |  |  |  | Canada | YT |  |  | WHITTIER | [5 empty] | VISALIA MUNI (AWOS) | [58 empty] | 69
USA | AK | SHISHMAREF (AWOS) |  |  |  | Colombia | Cartagena |  |  | WRANGELL | [5 empty] | YUBA CO | [58 empty] | 70
USA | AK | SITKA JAPONSKI AP | [7 empty] | YAKUTAT STATE ARPT | [64 empty] | 71
USA | AK | SKAGWAY AIRPORT | [72 empty] | 72
USA | AK | SLEETMUTE | [72 empty] | 73
USA | AK | SOLDOTNA | [72 empty] | 74
USA | AK | ST PAUL ISLAND ARPT | [72 empty] | 75
USA | AK | TALKEETNA STATE ARPT | [72 empty] | 76
USA | AK | TANANA RALPH M CALHOUN MEM AP | [72 empty] | 77
USA | AK | TOGIAK VILLAGE AWOS | [72 empty] | 78
USA | AK | UNALAKLEET FIELD | [72 empty] | 79
USA | AK | VALDEZ PIONEER FIEL | [72 empty] | 80
USA | AK | VALDEZ WSO | [72 empty] | 81
USA | AK | WHITTIER | [72 empty] | 82
USA | AK | WRANGELL | [72 empty] | 83
USA | AK | YAKUTAT STATE ARPT | [72 empty] | 84
USA | AL | ANNISTON METROPOLITAN AP | [72 empty] | 85
USA | AL | AUBURN-OPELIKA APT | [72 empty] | 86
USA | AL | BIRMINGHAM MUNICIPAL AP | [72 empty] | 87
USA | AL | CAIRNS FIELD FORT RUCKER | [72 empty] | 88
USA | AL | DOTHAN MUNICIPAL AP | [72 empty] | 89
USA | AL | HUNTSVILLE INTL/JONES FIELD | [72 empty] | 90
USA | AL | MAXWELL AFB | [72 empty] | 91
USA | AL | MOBILE DOWNTOWN AP | [72 empty] | 92
USA | AL | MOBILE REGIONAL AP | [72 empty] | 93
USA | AL | MONTGOMERY DANNELLY FIELD | [72 empty] | 94
USA | AL | MUSCLE SHOALS REGIONAL AP | [72 empty] | 95
USA | AL | TUSCALOOSA MUNICIPAL AP | [72 empty] | 96
USA | AR | BATESVILLE (AWOS) | [72 empty] | 97
USA | AR | BENTONVILLE (AWOS) | [72 empty] | 98
USA | AR | EL DORADO GOODWIN FIELD | [72 empty] | 99
USA | AR | FAYETTEVILLE DRAKE FIELD | [72 empty] | 100
USA | AR | FLIPPIN (AWOS) | [72 empty] | 101
USA | AR | FORT SMITH REGIONAL AP | [72 empty] | 102
USA | AR | HARRISON FAA AP | [72 empty] | 103
USA | AR | JONESBORO MUNI | [72 empty] | 104
USA | AR | LITTLE ROCK ADAMS FIELD | [72 empty] | 105
USA | AR | LITTLE ROCK AFB | [72 empty] | 106
USA | AR | PINE BLUFF FAA AP | [72 empty] | 107
USA | AR | ROGERS (AWOS) | [72 empty] | 108
USA | AR | SILOAM SPRING(AWOS) | [72 empty] | 109
USA | AR | SPRINGDALE MUNI | [72 empty] | 110
USA | AR | STUTTGART (AWOS) | [72 empty] | 111
USA | AR | TEXARKANA WEBB FIELD | [72 empty] | 112
USA | AR | WALNUT RIDGE (AWOS) | [72 empty] | 113
USA | AZ | CASA GRANDE (AWOS) | [72 empty] | 114
USA | AZ | DAVIS MONTHAN AFB | [72 empty] | 115
USA | AZ | DEER VALLEY/PHOENIX | [72 empty] | 116
USA | AZ | DOUGLAS BISBEE-DOUGLAS INTL A | [72 empty] | 117
USA | AZ | FLAGSTAFF PULLIAM ARPT | [72 empty] | 118
USA | AZ | GRAND CANYON NATL P | [72 empty] | 119
USA | AZ | KINGMAN (AMOS) | [72 empty] | 120
USA | AZ | LUKE AFB | [72 empty] | 121
USA | AZ | PAGE MUNI (AMOS) | [72 empty] | 122
USA | AZ | PHOENIX SKY HARBOR INTL AP | [72 empty] | 123
USA | AZ | PRESCOTT LOVE FIELD | [72 empty] | 124
USA | AZ | SAFFORD (AMOS) | [72 empty] | 125
USA | AZ | SCOTTSDALE MUNI | [72 empty] | 126
USA | AZ | TUCSON INTERNATIONAL AP | [72 empty] | 127
USA | AZ | WINSLOW MUNICIPAL AP | [72 empty] | 128
USA | AZ | YUMA INTL ARPT | [72 empty] | 129
USA | AZ | YUMA MCAS | [72 empty] | 130
Canada | BC | ABBOTSFORD AP | [72 empty] | 131
Canada | BC | AGASSIZ CDA | [72 empty] | 132
Canada | BC | BALLENAS ISLAND | [72 empty] | 133
Canada | BC | COMOX AP | [72 empty] | 134
Canada | BC | CRANBROOK AP | [72 empty] | 135
Canada | BC | DISCOVERY ISLAND | [72 empty] | 136
Canada | BC | ENTRANCE ISLAND | [72 empty] | 137
Canada | BC | ESQUIMALT HARBOUR | [72 empty] | 138
Canada | BC | FORT NELSON | [72 empty] | 139
Canada | BC | FORT SAINT JOHN | [72 empty] | 140
Canada | BC | KAMLOOPS AP | [72 empty] | 141
Canada | BC | KELOWNA AP | [72 empty] | 142
Canada | BC | MALAHAT | [72 empty] | 143
Canada | BC | NORTH VANCOUVER | [72 empty] | 144
Canada | BC | PENTICTON AP | [72 empty] | 145
Canada | BC | PITT MEADOWS | [72 empty] | 146
Canada | BC | PRINCE GEORGE | [72 empty] | 147
Canada | BC | SMITHERS AP | [72 empty] | 148
Canada | BC | SUMMERLAND | [72 empty] | 149
Canada | BC | VANCOUVER | [72 empty] | 150
Canada | BC | VERNON | [72 empty] | 151
Canada | BC | VICTORIA AP | [72 empty] | 152
Canada | BC | VICTORIA | [72 empty] | 153
Canada | BC | VICTORIA UNIV | [72 empty] | 154
Canada | BC | W VANCOUVER | [72 empty] | 155
Canada | BC | WHISTLER | [72 empty] | 156
Canada | BC | WHITE ROCK | [72 empty] | 157
India | BD | DHAKA | [72 empty] | 158
USA | CA | ALTURAS | [72 empty] | 159
USA | CA | ARCATA AIRPORT | [72 empty] | 160
USA | CA | BAKERSFIELD MEADOWS FIELD | [72 empty] | 161
USA | CA | BEALE AFB | [72 empty] | 162
USA | CA | BISHOP AIRPORT | [72 empty] | 163
USA | CA | BLUE CANYON AP | [72 empty] | 164
USA | CA | BLYTHE RIVERSIDE CO ARPT | [72 empty] | 165
USA | CA | BURBANK-GLENDALE-PASADENA AP | [72 empty] | 166
USA | CA | CAMARILLO (AWOS) | [72 empty] | 167
USA | CA | CAMP PENDLETON MCAS | [72 empty] | 168
USA | CA | CARLSBAD/PALOMAR | [72 empty] | 169
USA | CA | CHINO AIRPORT | [72 empty] | 170
USA | CA | CHULA VISTA BROWN FIELD NAAS | [72 empty] | 171
USA | CA | CONCORD CONCORD-BUCHANAN FIEL | [72 empty] | 172
USA | CA | CRESCENT CITY FAA AI | [72 empty] | 173
USA | CA | DAGGETT BARSTOW-DAGGETT AP | [72 empty] | 174
USA | CA | EDWARDS AFB | [72 empty] | 175
USA | CA | FRESNO YOSEMITE INTL AP | [72 empty] | 176
USA | CA | FULLERTON MUNICIPAL | [72 empty] | 177
USA | CA | HAYWARD AIR TERM | [72 empty] | 178
USA | CA | IMPERIAL | [72 empty] | 179
USA | CA | JACK NORTHROP FLD H | [72 empty] | 180
USA | CA | LANCASTER GEN WM FOX FIELD | [72 empty] | 181
USA | CA | LEMOORE REEVES NAS | [72 empty] | 182
USA | CA | LIVERMORE MUNICIPAL | [72 empty] | 183
USA | CA | LOMPOC (AWOS) | [72 empty] | 184
USA | CA | LONG BEACH DAUGHERTY FLD | [72 empty] | 185
USA | CA | LOS ANGELES INTL ARPT | [72 empty] | 186
USA | CA | MARCH AFB | [72 empty] | 187
USA | CA | MERCED/MACREADY FLD | [72 empty] | 188
USA | CA | MODESTO CITY-COUNTY AP | [72 empty] | 189
USA | CA | MONTAGUE SISKIYOU COUNTY AP | [72 empty] | 190
USA | CA | MONTEREY NAF | [72 empty] | 191
USA | CA | MOUNTAIN VIEW MOFFETT FLD NAS | [72 empty] | 192
USA | CA | NAPA CO. AIRPORT | [72 empty] | 193
USA | CA | NEEDLES AIRPORT | [72 empty] | 194
USA | CA | OAKLAND METROPOLITAN ARPT | [72 empty] | 195
USA | CA | OXNARD AIRPORT | [72 empty] | 196
USA | CA | PALM SPRINGS INTL | [72 empty] | 197
USA | CA | PALM SPRINGS THERMAL AP | [72 empty] | 198
USA | CA | PALMDALE AIRPORT | [72 empty] | 199
USA | CA | PASO ROBLES MUNICIPAL ARPT | [72 empty] | 200
USA | CA | POINT MUGU NF | [72 empty] | 201
USA | CA | PORTERVILLE (AWOS) | [72 empty] | 202
USA | CA | RED BLUFF MUNICIPAL ARPT | [72 empty] | 203
USA | CA | REDDING MUNICIPAL ARPT | [72 empty] | 204
USA | CA | RIVERSIDE MUNI | [72 empty] | 205
USA | CA | SACRAMENTO EXECUTIVE ARPT | [72 empty] | 206
USA | CA | SACRAMENTO METROPOLITAN AP | [72 empty] | 207
USA | CA | SALINAS MUNICIPAL AP | [72 empty] | 208
USA | CA | SAN DIEGO LINDBERGH FIELD | [72 empty] | 209
USA | CA | SAN DIEGO MIRAMAR NAS | [72 empty] | 210
USA | CA | SAN DIEGO NORTH ISLAND NAS | [72 empty] | 211
USA | CA | SAN DIEGO/MONTGOMER | [72 empty] | 212
USA | CA | SAN FRANCISCO INTL AP | [72 empty] | 213
USA | CA | SAN JOSE INTL AP | [72 empty] | 214
USA | CA | SAN LUIS CO RGNL | [72 empty] | 215
USA | CA | SANDBERG | [72 empty] | 216
USA | CA | SANTA BARBARA MUNICIPAL AP | [72 empty] | 217
USA | CA | SANTA MARIA PUBLIC ARPT | [72 empty] | 218
USA | CA | SANTA MONICA MUNI | [72 empty] | 219
USA | CA | SANTA ROSA (AWOS) | [72 empty] | 220
USA | CA | STOCKTON METROPOLITAN ARPT | [72 empty] | 221
USA | CA | TRAVIS FIELD AFB | [72 empty] | 222
USA | CA | TRUCKEE-TAHOE | [72 empty] | 223
USA | CA | UKIAH MUNICIPAL AP | [72 empty] | 224
USA | CA | VAN NUYS AIRPORT | [72 empty] | 225
USA | CA | VISALIA MUNI (AWOS) | [72 empty] | 226
USA | CA | YUBA CO | [72 empty] | 227
USA | CO | AKRON WASHINGTON CO AP | [72 empty] | 228
USA | CO | ALAMOSA SAN LUIS VALLEY RGNL | [72 empty] | 229
USA | CO | ASPEN PITKIN CO SAR | [72 empty] | 230
USA | CO | AURORA BUCKLEY FIELD ANGB | [72 empty] | 231
Colombia | CO | BARRANQUILLA | [72 empty] | 232
USA | CO | BROOMFIELD/JEFFCO [BOULDER - SURFRAD] | [72 empty] | 233
Colombia | CO | CALI | [72 empty] | 234
Colombia | CO | CARTAGENA | [72 empty] | 235
USA | CO | COLORADO SPRINGS MUNI AP | [72 empty] | 236
Colombia | CO | CORTEZ/MONTEZUMA | [72 empty] | 237
USA | CO | CRAIG-MOFFAT | [72 empty] | 238
USA | CO | DENVER INTL AP | [72 empty] | 239
USA | CO | DENVER/CENTENNIAL [GOLDEN - NREL] | [72 empty] | 240
USA | CO | DURANGO/LA PLATA CO | [72 empty] | 241
USA | CO | EAGLE COUNTY AP | [72 empty] | 242
USA | CO | FORT COLLINS (AWOS) | [72 empty] | 243
USA | CO | GRAND JUNCTION WALKER FIELD | [72 empty] | 244
USA | CO | GREELEY/WELD (AWOS) | [72 empty] | 245
USA | CO | GUNNISON CO. (AWOS) | [72 empty] | 246
USA | CO | HAYDEN/YAMPA (AWOS) | [72 empty] | 247
USA | CO | LA JUNTA MUNICIPAL AP | [72 empty] | 248
USA | CO | LAMAR MUNICIPAL | [72 empty] | 249
USA | CO | LEADVILLE/LAKE CO. | [72 empty] | 250
USA | CO | LIMON | [72 empty] | 251
USA | CO | MONTROSE CO. ARPT | [72 empty] | 252
USA | CO | PUEBLO MEMORIAL AP | [72 empty] | 253
USA | CO | RIFLE/GARFIELD RGNL | [72 empty] | 254
USA | CO | TRINIDAD LAS ANIMAS COUNTY AP | [72 empty] | 255
USA | CT | BRIDGEPORT SIKORSKY MEMORIAL | [72 empty] | 256
USA | CT | DANBURY MUNICIPAL | [72 empty] | 257
USA | CT | GROTON NEW LONDON AP | [72 empty] | 258
USA | CT | HARTFORD BRADLEY INTL AP | [72 empty] | 259
USA | CT | HARTFORD BRAINARD FD | [72 empty] | 260
USA | CT | NEW HAVEN TWEED AIRPORT | [72 empty] | 261
USA | CT | OXFORD (AWOS) | [72 empty] | 262
USA | DE | DOVER AFB | [72 empty] | 263
USA | DE | WILMINGTON NEW CASTLE CNTY AP | [72 empty] | 264
USA | FL | CRESTVIEW BOB SIKES AP | [72 empty] | 265
USA | FL | DAYTONA BEACH INTL AP | [72 empty] | 266
USA | FL | FORT LAUDERDALE | [72 empty] | 267
USA | FL | FORT LAUDERDALE HOLLYWOOD INT | [72 empty] | 268
USA | FL | FORT MYERS PAGE FIELD | [72 empty] | 269
USA | FL | GAINESVILLE REGIONAL AP | [72 empty] | 270
USA | FL | HOMESTEAD AFB | [72 empty] | 271
USA | FL | JACKSONVILLE INTL ARPT | [72 empty] | 272
USA | FL | JACKSONVILLE NAS | [72 empty] | 273
USA | FL | JACKSONVILLE/CRAIG | [72 empty] | 274
USA | FL | KEY WEST INTL ARPT | [72 empty] | 275
USA | FL | KEY WEST NAS | [72 empty] | 276
USA | FL | MACDILL AFB | [72 empty] | 277
USA | FL | MARATHON AIRPORT | [72 empty] | 278
USA | FL | MAYPORT NS | [72 empty] | 279
USA | FL | MELBOURNE REGIONAL AP | [72 empty] | 280
USA | FL | MIAMI INTL AP | [72 empty] | 281
USA | FL | MIAMI/KENDALL-TAMIA | [72 empty] | 282
USA | FL | MIAMI/OPA LOCKA | [72 empty] | 283
USA | FL | NAPLES MUNICIPAL | [72 empty] | 284
USA | FL | NASA SHUTTLE FCLTY | [72 empty] | 285
USA | FL | OCALA MUNI (AWOS) | [72 empty] | 286
USA | FL | ORLANDO EXECUTIVE AP | [72 empty] | 287
USA | FL | ORLANDO INTL ARPT | [72 empty] | 288
USA | FL | ORLANDO SANFORD AIRPORT | [72 empty] | 289
USA | FL | PANAMA CITY BAY CO | [72 empty] | 290
USA | FL | PENSACOLA FOREST SHERMAN NAS | [72 empty] | 291
USA | FL | PENSACOLA REGIONAL AP | [72 empty] | 292
USA | FL | SARASOTA BRADENTON | [72 empty] | 293
USA | FL | SOUTHWEST FLORIDA I | [72 empty] | 294
USA | FL | ST LUCIE CO INTL | [72 empty] | 295
USA | FL | ST PETERSBURG ALBERT WHITTED | [72 empty] | 296
USA | FL | ST PETERSBURG CLEAR | [72 empty] | 297
USA | FL | TALLAHASSEE REGIONAL AP [ISIS] | [72 empty] | 298
USA | FL | TAMPA INTERNATIONAL AP | [72 empty] | 299
USA | FL | TYNDALL AFB | [72 empty] | 300
USA | FL | VALPARAISO EGLIN AFB | [72 empty] | 301
USA | FL | VALPARAISO HURLBURT | [72 empty] | 302
USA | FL | VERO BEACH MUNICIPAL ARPT | [72 empty] | 303
USA | FL | WHITING FIELD NAAS | [72 empty] | 304
USA | GA | ALBANY DOUGHERTY COUNTY AP | [72 empty] | 305
USA | GA | ALMA BACON COUNTY AP | [72 empty] | 306
USA | GA | ATHENS BEN EPPS AP | [72 empty] | 307
USA | GA | ATLANTA HARTSFIELD INTL AP | [72 empty] | 308
USA | GA | AUGUSTA BUSH FIELD | [72 empty] | 309
USA | GA | BRUNSWICK GOLDEN IS | [72 empty] | 310
USA | GA | BRUNSWICK MALCOLM MCKINNON AP | [72 empty] | 311
USA | GA | COLUMBUS METROPOLITAN ARPT | [72 empty] | 312
USA | GA | DEKALB PEACHTREE | [72 empty] | 313
USA | GA | FORT BENNING LAWSON | [72 empty] | 314
USA | GA | FULTON CO ARPT BROW | [72 empty] | 315
USA | GA | HUNTER AAF | [72 empty] | 316
USA | GA | MACON MIDDLE GA REGIONAL AP | [72 empty] | 317
USA | GA | MARIETTA DOBBINS AFB | [72 empty] | 318
USA | GA | MOODY AFB/VALDOSTA | [72 empty] | 319
USA | GA | ROME R B RUSSELL AP | [72 empty] | 320
USA | GA | SAVANNAH INTL AP | [72 empty] | 321
USA | GA | VALDOSTA WB AIRPORT | [72 empty] | 322
USA | GA | WARNER ROBINS AFB | [72 empty] | 323
USA | HI | BARBERS POINT NAS | [72 empty] | 324
USA | HI | HILO INTERNATIONAL AP | [72 empty] | 325
USA | HI | HONOLULU INTL ARPT | [72 empty] | 326
USA | HI | KAHULUI AIRPORT | [72 empty] | 327
USA | HI | KANEOHE BAY MCAS | [72 empty] | 328
USA | HI | KONA INTL AT KEAHOL | [72 empty] | 329
USA | HI | LIHUE AIRPORT | [72 empty] | 330
USA | HI | MOLOKAI (AMOS) | [72 empty] | 331
USA | IA | ALGONA | [72 empty] | 332
USA | IA | ATLANTIC | [72 empty] | 333
USA | IA | BOONE MUNI | [72 empty] | 334
USA | IA | BURLINGTON MUNICIPAL AP | [72 empty] | 335
USA | IA | CARROLL | [72 empty] | 336
USA | IA | CEDAR RAPIDS MUNICIPAL AP | [72 empty] | 337
USA | IA | CHARITON | [72 empty] | 338
USA | IA | CHARLES CITY | [72 empty] | 339
USA | IA | CLARINDA | [72 empty] | 340
USA | IA | CLINTON MUNI (AWOS) | [72 empty] | 341
USA | IA | COUNCIL BLUFFS | [72 empty] | 342
USA | IA | CRESTON | [72 empty] | 343
USA | IA | DECORAH | [72 empty] | 344
USA | IA | DENISON | [72 empty] | 345
USA | IA | DES MOINES INTL AP | [72 empty] | 346
USA | IA | DUBUQUE REGIONAL AP | [72 empty] | 347
USA | IA | ESTHERVILLE MUNI | [72 empty] | 348
USA | IA | FAIR FIELD | [72 empty] | 349
USA | IA | FORT DODGE (AWOS) | [72 empty] | 350
USA | IA | FORT MADISON | [72 empty] | 351
USA | IA | KEOKUK MUNI | [72 empty] | 352
USA | IA | KNOXVILLE | [72 empty] | 353
USA | IA | LE MARS | [72 empty] | 354
USA | IA | MASON CITY MUNICIPAL ARPT | [72 empty] | 355
USA | IA | MONTICELLO MUNI | [72 empty] | 356
USA | IA | MUSCATINE | [72 empty] | 357
USA | IA | NEWTON MUNI | [72 empty] | 358
USA | IA | OELWEN | [72 empty] | 359
USA | IA | ORANGE CITY | [72 empty] | 360
USA | IA | OTTUMWA INDUSTRIAL AP | [72 empty] | 361
USA | IA | RED OAK | [72 empty] | 362
USA | IA | SHELDON | [72 empty] | 363
USA | IA | SHENANDOAH MUNI | [72 empty] | 364
USA | IA | SIOUX CITY SIOUX GATEWAY AP | [72 empty] | 365
USA | IA | SPENCER | [72 empty] | 366
USA | IA | STORM LAKE | [72 empty] | 367
USA | IA | WASHINGTON | [72 empty] | 368
USA | IA | WATERLOO MUNICIPAL AP | [72 empty] | 369
USA | IA | WEBSTER CITY | [72 empty] | 370
USA | ID | BOISE AIR TERMINAL [UO] | [72 empty] | 371
USA | ID | BURLEY MUNICIPAL ARPT | [72 empty] | 372
USA | ID | CALDWELL (AWOS) | [72 empty] | 373
USA | ID | COEUR D`ALENE(AWOS) | [72 empty] | 374
USA | ID | IDAHO FALLS FANNING FIELD | [72 empty] | 375
USA | ID | JOSLIN FLD MAGIC VA [TWIN FALLS - UO] | [72 empty] | 376
USA | ID | LEWISTON NEZ PERCE CNTY AP | [72 empty] | 377
USA | ID | MOUNTAIN HOME AFB | [72 empty] | 378
USA | ID | POCATELLO REGIONAL AP | [72 empty] | 379
USA | ID | SALMON/LEMHI (AWOS) | [72 empty] | 380
USA | IL | AURORA MUNICIPAL | [72 empty] | 381
USA | IL | BELLEVILLE SCOTT AFB | [72 empty] | 382
USA | IL | CAHOKIA/ST. LOUIS | [72 empty] | 383
USA | IL | CENTRAL ILLINOIS RG | [72 empty] | 384
USA | IL | CHICAGO MIDWAY AP | [72 empty] | 385
USA | IL | CHICAGO OHARE INTL AP | [72 empty] | 386
USA | IL | CHICAGO/WAUKEGAN | [72 empty] | 387
USA | IL | DECATUR | [72 empty] | 388
USA | IL | MARION REGIONAL | [72 empty] | 389
USA | IL | MOLINE QUAD CITY INTL AP | [72 empty] | 390
USA | IL | MOUNT VERNON (AWOS) | [72 empty] | 391
USA | IL | PEORIA GREATER PEORIA AP | [72 empty] | 392
USA | IL | QUINCY MUNI BALDWIN FLD | [72 empty] | 393
USA | IL | ROCKFORD GREATER ROCKFORD AP | [72 empty] | 394
USA | IL | SOUTHERN ILLINOIS | [72 empty] | 395
USA | IL | SPRINGFIELD CAPITAL AP | [72 empty] | 396
USA | IL | STERLING ROCKFALLS | [72 empty] | 397
USA | IL | UNIV OF ILLINOIS WI [BONDVILLE - SURFRAD] | [72 empty] | 398
USA | IL | W. CHICAGO/DU PAGE | [72 empty] | 399
USA | IN | DELAWARE CO JOHNSON | [72 empty] | 400
USA | IN | EVANSVILLE REGIONAL AP | [72 empty] | 401
USA | IN | FORT WAYNE INTL AP | [72 empty] | 402
USA | IN | GRISSOM ARB | [72 empty] | 403
USA | IN | HUNTINGBURG | [72 empty] | 404
USA | IN | INDIANAPOLIS INTL AP | [72 empty] | 405
USA | IN | LAFAYETTE PURDUE UNIV AP | [72 empty] | 406
USA | IN | MONROE CO | [72 empty] | 407
India | IN | NEW DELHI SAFDARJUNG AP | [72 empty] | 408
India | IN | PATNA | [72 empty] | 409
USA | IN | SOUTH BEND MICHIANA RGNL AP | [72 empty] | 410
USA | IN | TERRE HAUTE HULMAN REGIONAL A | [72 empty] | 411
USA | KS | CHANUTE MARTIN JOHNSON AP | [72 empty] | 412
USA | KS | CONCORDIA BLOSSER MUNI AP | [72 empty] | 413
USA | KS | DODGE CITY REGIONAL AP | [72 empty] | 414
USA | KS | EMPORIA MUNICIPAL AP | [72 empty] | 415
USA | KS | FORT RILEY MARSHALL AAF | [72 empty] | 416
USA | KS | GARDEN CITY MUNICIPAL AP | [72 empty] | 417
USA | KS | GOODLAND RENNER FIELD | [72 empty] | 418
USA | KS | GREAT BEND (AWOS) | [72 empty] | 419
USA | KS | HAYS MUNI (AWOS) | [72 empty] | 420
USA | KS | HILL CITY MUNICIPAL AP | [72 empty] | 421
USA | KS | HUTCHINSON MUNICIPAL AP | [72 empty] | 422
USA | KS | LIBERAL MUNI | [72 empty] | 423
USA | KS | MANHATTAN RGNL | [72 empty] | 424
USA | KS | MCCONNELL AFB | [72 empty] | 425
USA | KS | NEWTON (AWOS) | [72 empty] | 426
USA | KS | OLATHE/JOHNSON CO. | [72 empty] | 427
USA | KS | RUSSELL MUNICIPAL AP | [72 empty] | 428
USA | KS | SALINA MUNICIPAL AP | [72 empty] | 429
USA | KS | TOPEKA FORBES FIELD | [72 empty] | 430
USA | KS | TOPEKA MUNICIPAL AP | [72 empty] | 431
USA | KS | WICHITA MID-CONTINENT AP | [72 empty] | 432
USA | KS | WICHITA/COL. JABARA | [72 empty] | 433
USA | KY | BOWLING GREEN WARREN CO AP | [72 empty] | 434
USA | KY | CINCINNATI NORTHERN KY AP | [72 empty] | 435
USA | KY | FORT CAMPBELL AAF | [72 empty] | 436
USA | KY | FORT KNOX GODMAN AAF | [72 empty] | 437
USA | KY | HENDERSON CITY | [72 empty] | 438
USA | KY | JACKSON JULIAN CARROLL AP | [72 empty] | 439
USA | KY | LEXINGTON BLUEGRASS AP | [72 empty] | 440
USA | KY | LONDON-CORBIN AP | [72 empty] | 441
USA | KY | LOUISVILLE BOWMAN FIELD | [72 empty] | 442
USA | KY | LOUISVILLE STANDIFORD FIELD | [72 empty] | 443
USA | KY | PADUCAH BARKLEY REGIONAL AP | [72 empty] | 444
USA | KY | SOMERSET(AWOS) | [72 empty] | 445
USA | LA | ALEXANDRIA ESLER REGIONAL AP | [72 empty] | 446
USA | LA | BARKSDALE AFB | [72 empty] | 447
USA | LA | BATON ROUGE RYAN ARPT | [72 empty] | 448
USA | LA | ENGLAND AFB | [72 empty] | 449
USA | LA | FORT POLK AAF | [72 empty] | 450
USA | LA | LAFAYETTE REGIONAL AP | [72 empty] | 451
USA | LA | LAKE CHARLES REGIONAL ARPT | [72 empty] | 452
USA | LA | MONROE REGIONAL AP | [72 empty] | 453
USA | LA | NEW IBERIA NAAS | [72 empty] | 454
USA | LA | NEW ORLEANS ALVIN CALLENDER F | [72 empty] | 455
USA | LA | NEW ORLEANS INTL ARPT | [72 empty] | 456
USA | LA | NEW ORLEANS LAKEFRONT AP | [72 empty] | 457
USA | LA | PATTERSON MEMORIAL | [72 empty] | 458
USA | LA | SHREVEPORT DOWNTOWN | [72 empty] | 459
USA | LA | SHREVEPORT REGIONAL ARPT | [72 empty] | 460
USA | MA | BARNSTABLE MUNI BOA | [72 empty] | 461
USA | MA | BEVERLY MUNI | [72 empty] | 462
USA | MA | BOSTON LOGAN INT ARPT | [72 empty] | 463
USA | MA | CHICOPEE FALLS WESTO | [72 empty] | 464
USA | MA | LAWRENCE MUNI | [72 empty] | 465
USA | MA | MARTHAS VINEYARD | [72 empty] | 466
USA | MA | NANTUCKET MEMORIAL AP | [72 empty] | 467
USA | MA | NEW BEDFORD RGNL | [72 empty] | 468
USA | MA | NORTH ADAMS | [72 empty] | 469
USA | MA | NORWOOD MEMORIAL | [72 empty] | 470
USA | MA | OTIS ANGB | [72 empty] | 471
USA | MA | PLYMOUTH MUNICIPAL | [72 empty] | 472
USA | MA | PROVINCETOWN (AWOS) | [72 empty] | 473
USA | MA | WESTFIELD BARNES MUNI AP | [72 empty] | 474
USA | MA | WORCESTER REGIONAL ARPT | [72 empty] | 475
USA | MB | WINNIPEG | [72 empty] | 476
USA | MD | ANDREWS AFB | [72 empty] | 477
USA | MD | BALTIMORE BLT-WASHNGTN INT | [72 empty] | 478
USA | MD | HAGERSTOWN RGNL RIC | [72 empty] | 479
USA | MD | PATUXENT RIVER NAS | [72 empty] | 480
USA | MD | SALISBURY WICOMICO CO AP | [72 empty] | 481
USA | ME | AUBURN-LEWISTON | [72 empty] | 482
USA | ME | AUGUSTA AIRPORT | [72 empty] | 483
USA | ME | BANGOR INTERNATIONAL AP | [72 empty] | 484
USA | ME | BAR HARBOR (AWOS) | [72 empty] | 485
USA | ME | CARIBOU MUNICIPAL ARPT | [72 empty] | 486
USA | ME | HOULTON INTL ARPT | [72 empty] | 487
USA | ME | MILLINOCKET MUNICIPAL AP | [72 empty] | 488
USA | ME | NORTHERN AROOSTOOK | [72 empty] | 489
USA | ME | PORTLAND INTL JETPORT | [72 empty] | 490
USA | ME | PRESQUE ISLE MUNICIP | [72 empty] | 491
USA | ME | ROCKLAND/KNOX(AWOS) | [72 empty] | 492
USA | ME | SANFORD MUNI (AWOS) | [72 empty] | 493
USA | ME | WATERVILLE (AWOS) | [72 empty] | 494
USA | ME | WISCASSET | [72 empty] | 495
USA | MI | ALPENA COUNTY REGIONAL AP | [72 empty] | 496
USA | MI | ANN ARBOR MUNICIPAL | [72 empty] | 497
USA | MI | BATTLE CREEK KELLOGG AP | [72 empty] | 498
USA | MI | BENTON HARBOR/ROSS | [72 empty] | 499
USA | MI | CADILLAC WEXFORD CO AP | [72 empty] | 500
USA | MI | CHIPPEWA CO INTL | [72 empty] | 501
USA | MI | DETROIT CITY AIRPORT | [72 empty] | 502
USA | MI | DETROIT METROPOLITAN ARPT | [72 empty] | 503
USA | MI | DETROIT WILLOW RUN AP | [72 empty] | 504
USA | MI | ESCANABA (AWOS) | [72 empty] | 505
USA | MI | FLINT BISHOP INTL ARPT | [72 empty] | 506
USA | MI | GRAND RAPIDS KENT COUNTY INT | [72 empty] | 507
USA | MI | HANCOCK HOUGHTON CO AP | [72 empty] | 508
USA | MI | HOUGHTON LAKE ROSCOMMON CO AR | [72 empty] | 509
USA | MI | HOWELL | [72 empty] | 510
USA | MI | IRON MOUNTAIN/FORD | [72 empty] | 511
USA | MI | IRONWOOD (AWOS) | [72 empty] | 512
USA | MI | JACKSON REYNOLDS FIELD | [72 empty] | 513
USA | MI | KALAMAZOO BATTLE CR | [72 empty] | 514
USA | MI | LANSING CAPITAL CITY ARPT | [72 empty] | 515
USA | MI | MANISTEE (AWOS) | [72 empty] | 516
USA | MI | MENOMINEE (AWOS) | [72 empty] | 517
USA | MI | MOUNT CLEMENS SELFRIDGE FLD | [72 empty] | 518
USA | MI | MUSKEGON COUNTY ARPT | [72 empty] | 519
USA | MI | OAKLAND CO INTL | [72 empty] | 520
USA | MI | OSCODA WURTSMITH AFB | [72 empty] | 521
USA | MI | PELLSTON EMMET COUNTY AP | [72 empty] | 522
USA | MI | SAGINAW TRI CITY INTL AP | [72 empty] | 523
USA | MI | SAULT STE MARIE SANDERSON FIE | [72 empty] | 524
USA | MI | ST.CLAIR COUNTY INT | [72 empty] | 525
USA | MI | TRAVERSE CITY CHERRY CAPITAL | [72 empty] | 526
USA | MN | AITKIN NDB(AWOS) | [72 empty] | 527
USA | MN | ALBERT LEA (AWOS) | [72 empty] | 528
USA | MN | ALEXANDRIA MUNICIPAL AP | [72 empty] | 529
USA | MN | AUSTIN MUNI | [72 empty] | 530
USA | MN | BAUDETTE INTERNATIONAL AP | [72 empty] | 531
USA | MN | BEMIDJI MUNICIPAL | [72 empty] | 532
USA | MN | BENSON MUNI | [72 empty] | 533
USA | MN | BRAINERD/WIELAND | [72 empty] | 534
USA | MN | CAMBRIDGE MUNI | [72 empty] | 535
USA | MN | CLOQUET (AWOS) | [72 empty] | 536
USA | MN | CRANE LAKE (AWOS) | [72 empty] | 537
USA | MN | CROOKSTON MUNI FLD | [72 empty] | 538
USA | MN | DETROIT LAKES(AWOS) | [72 empty] | 539
USA | MN | DULUTH INTERNATIONAL ARPT | [72 empty] | 540
USA | MN | ELY MUNI | [72 empty] | 541
USA | MN | EVELETH MUNI (AWOS) | [72 empty] | 542
USA | MN | FAIRMONT MUNI(AWOS) | [72 empty] | 543
USA | MN | FARIBAULT MUNI AWOS | [72 empty] | 544
USA | MN | FLYING CLOUD | [72 empty] | 545
USA | MN | FOSSTON(AWOS) | [72 empty] | 546
USA | MN | GLENWOOD (ASOS) | [72 empty] | 547
USA | MN | GRAND RAPIDS(AWOS) | [72 empty] | 548
USA | MN | HALLOCK | [72 empty] | 549
USA | MN | HIBBING CHISHOLM-HIBBING AP | [72 empty] | 550
USA | MN | HUTCHINSON (AWOS) | [72 empty] | 551
USA | MN | INTERNATIONAL FALLS INTL AP | [72 empty] | 552
USA | MN | LITCHFIELD MUNI | [72 empty] | 553
USA | MN | LITTLE FALLS (AWOS) | [72 empty] | 554
USA | MN | MANKATO(AWOS) | [72 empty] | 555
USA | MN | MINNEAPOLIS-ST PAUL INT ARP | [72 empty] | 556
USA | MN | MINNEAPOLIS/CRYSTAL | [72 empty] | 557
USA | MN | MORA MUNI (AWOS) | [72 empty] | 558
USA | MN | MORRIS MUNI (AWOS) | [72 empty] | 559
USA | MN | NEW ULM MUNI (AWOS) | [72 empty] | 560
USA | MN | ORR | [72 empty] | 561
USA | MN | OWATONNA (AWOS) | [72 empty] | 562
USA | MN | PARK RAPIDS MUNICIPAL AP | [72 empty] | 563
USA | MN | PIPESTONE (AWOS) | [72 empty] | 564
USA | MN | RED WING | [72 empty] | 565
USA | MN | REDWOOD FALLS MUNI | [72 empty] | 566
USA | MN | ROCHESTER INTERNATIONAL ARPT | [72 empty] | 567
USA | MN | ROSEAU MUNI (AWOS) | [72 empty] | 568
USA | MN | SILVER BAY | [72 empty] | 569
USA | MN | SOUTH ST PAUL MUNI | [72 empty] | 570
USA | MN | ST CLOUD REGIONAL ARPT | [72 empty] | 571
USA | MN | ST PAUL DOWNTOWN AP | [72 empty] | 572
USA | MN | THIEF RIVER(AWOS) | [72 empty] | 573
USA | MN | WHEATON NDB (AWOS) | [72 empty] | 574
USA | MN | WILLMAR | [72 empty] | 575
USA | MN | WINONA MUNI (AWOS) | [72 empty] | 576
USA | MN | WORTHINGTON (AWOS) | [72 empty] | 577
USA | MO | CAPE GIRARDEAU MUNICIPAL AP | [72 empty] | 578
USA | MO | COLUMBIA REGIONAL AIRPORT | [72 empty] | 579
USA | MO | FARMINGTON | [72 empty] | 580
USA | MO | JEFFERSON CITY MEM | [72 empty] | 581
USA | MO | JOPLIN MUNICIPAL AP | [72 empty] | 582
USA | MO | KAISER MEM (AWOS) | [72 empty] | 583
USA | MO | KANSAS CITY DOWNTOWN AP | [72 empty] | 584
USA | MO | KANSAS CITY INT ARPT | [72 empty] | 585
USA | MO | KIRKSVILLE REGIONAL AP | [72 empty] | 586
USA | MO | POPLAR BLUFF(AMOS) | [72 empty] | 587
USA | MO | SPRINGFIELD REGIONAL ARPT | [72 empty] | 588
USA | MO | ST JOSEPH ROSECRANS MEMORIAL | [72 empty] | 589
USA | MO | ST LOUIS LAMBERT INT ARPT | [72 empty] | 590
USA | MO | ST LOUIS SPIRIT OF ST LOUIS A | [72 empty] | 591
USA | MO | VICHY ROLLA NATL ARPT | [72 empty] | 592
USA | MO | WHITEMAN AFB | [72 empty] | 593
USA | MS | COLUMBUS AFB | [72 empty] | 594
USA | MS | GOLDEN TRI(AWOS) | [72 empty] | 595
USA | MS | GREENWOOD LEFLORE ARPT | [72 empty] | 596
USA | MS | GULFPORT BILOXI INT | [72 empty] | 597
USA | MS | HATTIESBURG LAUREL | [72 empty] | 598
USA | MS | JACKSON INTERNATIONAL AP | [72 empty] | 599
USA | MS | KEESLER AFB | [72 empty] | 600
USA | MS | MCCOMB PIKE COUNTY AP | [72 empty] | 601
USA | MS | MERIDIAN KEY FIELD | [72 empty] | 602
USA | MS | MERIDIAN NAAS | [72 empty] | 603
USA | MS | NATCHEZ/HARDY(AWOS) | [72 empty] | 604
USA | MS | TUPELO C D LEMONS ARPT | [72 empty] | 605
USA | MT | BILLINGS LOGAN INT ARPT | [72 empty] | 606
USA | MT | BOZEMAN GALLATIN FIELD | [72 empty] | 607
USA | MT | BUTTE BERT MOONEY ARPT | [72 empty] | 608
USA | MT | CUT BANK MUNI AP | [72 empty] | 609
USA | MT | GLASGOW INTL ARPT | [72 empty] | 610
USA | MT | GLENDIVE(AWOS) | [72 empty] | 611
USA | MT | GREAT FALLS INTL ARPT | [72 empty] | 612
USA | MT | HAVRE CITY-COUNTY AP | [72 empty] | 613
USA | MT | HELENA REGIONAL AIRPORT | [72 empty] | 614
USA | MT | KALISPELL GLACIER PK INT AR | [72 empty] | 615
USA | MT | LEWISTOWN MUNICIPAL ARPT | [72 empty] | 616
USA | MT | LIVINGSTON MISSION FIELD | [72 empty] | 617
USA | MT | MILES CITY MUNICIPAL ARPT | [72 empty] | 618
USA | MT | MISSOULA INTERNATIONAL AP | [72 empty] | 619
USA | MT | SIDNEY-RICHLAND | [72 empty] | 620
USA | MT | WOLF POINT INTL [FORT PECK - SURFRAD] | [72 empty] | 621
Canada | NB | FREDERICTON | [72 empty] | 622
Canada | NB | MONCTON AP | [72 empty] | 623
USA | NC | ASHEVILLE REGIONAL ARPT | [72 empty] | 624
USA | NC | CAPE HATTERAS NWS BLDG | [72 empty] | 625
USA | NC | CHARLOTTE DOUGLAS INTL ARPT | [72 empty] | 626
USA | NC | CHERRY POINT MCAS | [72 empty] | 627
USA | NC | DARE CO RGNL | [72 empty] | 628
USA | NC | ELIZABETH CITY COAST GUARD AI [NREL] | [72 empty] | 629
USA | NC | FAYETTEVILLE POPE AFB | [72 empty] | 630
USA | NC | FAYETTEVILLE RGNL G | [72 empty] | 631
USA | NC | FORT BRAGG SIMMONS AAF | [72 empty] | 632
USA | NC | GOLDSBORO SEYMOUR JOHNSON AFB | [72 empty] | 633
USA | NC | GREENSBORO PIEDMONT TRIAD INT | [72 empty] | 634
USA | NC | HICKORY REGIONAL AP | [72 empty] | 635
USA | NC | JACKSONVILLE (AWOS) | [72 empty] | 636
USA | NC | NEW BERN CRAVEN CO REGL AP | [72 empty] | 637
USA | NC | NEW RIVER MCAF | [72 empty] | 638
USA | NC | PITT GREENVILLE ARP | [72 empty] | 639
USA | NC | RALEIGH DURHAM INTERNATIONAL | [72 empty] | 640
USA | NC | ROCKY MOUNT WILSON | [72 empty] | 641
USA | NC | SOUTHERN PINES AWOS | [72 empty] | 642
USA | NC | WILMINGTON INTERNATIONAL ARPT | [72 empty] | 643
USA | NC | WINSTON-SALEM REYNOLDS AP | [72 empty] | 644
USA | ND | BISMARCK MUNICIPAL ARPT [ISIS] | [72 empty] | 645
USA | ND | DEVILS LAKE(AWOS) | [72 empty] | 646
USA | ND | DICKINSON MUNICIPAL AP | [72 empty] | 647
USA | ND | FARGO HECTOR INTERNATIONAL AP | [72 empty] | 648
USA | ND | GRAND FORKS AF | [72 empty] | 649
USA | ND | GRAND FORKS INTERNATIONAL AP | [72 empty] | 650
USA | ND | JAMESTOWN MUNICIPAL ARPT | [72 empty] | 651
USA | ND | MINOT AFB | [72 empty] | 652
USA | ND | MINOT FAA AP | [72 empty] | 653
USA | ND | WILLISTON SLOULIN INTL AP | [72 empty] | 654
USA | NE | AINSWORTH MUNICIPAL | [72 empty] | 655
USA | NE | ALLIANCE MUNICIPAL | [72 empty] | 656
USA | NE | BEATRICE MUNICIPAL | [72 empty] | 657
USA | NE | BELLEVUE OFFUTT AFB | [72 empty] | 658
USA | NE | BREWSTER FIELD ARPT | [72 empty] | 659
USA | NE | BROKEN BOW MUNI | [72 empty] | 660
USA | NE | COLUMBUS MUNI | [72 empty] | 661
USA | NE | FALLS CITY/BRENNER | [72 empty] | 662
USA | NE | FREMONT MUNI ARPT | [72 empty] | 663
USA | NE | GRAND ISLAND CENTRAL NE REGIO | [72 empty] | 664
USA | NE | HASTINGS MUNICIPAL | [72 empty] | 665
USA | NE | KEARNEY MUNI (AWOS) | [72 empty] | 666
USA | NE | LINCOLN MUNICIPAL ARPT | [72 empty] | 667
USA | NE | MCCOOK MUNICIPAL | [72 empty] | 668
USA | NE | NORFOLK KARL STEFAN MEM ARPT | [72 empty] | 669
USA | NE | NORTH PLATTE REGIONAL AP | [72 empty] | 670
USA | NE | OMAHA EPPLEY AIRFIELD | [72 empty] | 671
USA | NE | OMAHA WSFO | [72 empty] | 672
USA | NE | SCOTTSBLUFF W B HEILIG FIELD | [72 empty] | 673
USA | NE | SIDNEY MUNICIPAL AP | [72 empty] | 674
USA | NE | TEKAMAH (ASOS) | [72 empty] | 675
USA | NE | VALENTINE MILLER FIELD | [72 empty] | 676
USA | NL | ST JOHNS | [72 empty] | 677
USA | NH | BERLIN MUNICIPAL | [72 empty] | 678
USA | NH | CONCORD MUNICIPAL ARPT | [72 empty] | 679
USA | NH | DILLANT HOPKINS | [72 empty] | 680
USA | NH | LACONIA MUNI (AWOS) | [72 empty] | 681
USA | NH | LEBANON MUNICIPAL | [72 empty] | 682
USA | NH | MANCHESTER AIRPORT | [72 empty] | 683
USA | NH | MOUNT WASHINGTON | [72 empty] | 684
USA | NH | PEASE INTL TRADEPOR | [72 empty] | 685
USA | NJ | ATLANTIC CITY INTL AP | [72 empty] | 686
USA | NJ | BELMAR ASC | [72 empty] | 687
USA | NJ | CALDWELL/ESSEX CO. | [72 empty] | 688
USA | NJ | CAPE MAY CO | [72 empty] | 689
USA | NJ | MCGUIRE AFB | [72 empty] | 690
USA | NJ | MILLVILLE MUNICIPAL AP | [72 empty] | 691
USA | NJ | NEWARK INTERNATIONAL ARPT | [72 empty] | 692
USA | NJ | TETERBORO AIRPORT | [72 empty] | 693
USA | NJ | TRENTON MERCER COUNTY AP | [72 empty] | 694
USA | NM | ALBUQUERQUE INTL ARPT [ISIS] | [72 empty] | 695
USA | NM | CARLSBAD CAVERN CITY AIR TERM | [72 empty] | 696
USA | NM | CLAYTON MUNICIPAL AIRPARK | [72 empty] | 697
USA | NM | CLOVIS CANNON AFB | [72 empty] | 698
USA | NM | CLOVIS MUNI (AWOS) | [72 empty] | 699
USA | NM | DEMING MUNI | [72 empty] | 700
USA | NM | FARMINGTON FOUR CORNERS REGL | [72 empty] | 701
USA | NM | GALLUP SEN CLARKE FLD | [72 empty] | 702
USA | NM | HOLLOMAN AFB | [72 empty] | 703
USA | NM | LAS VEGAS MUNICIPAL ARPT | [72 empty] | 704
USA | NM | ROSWELL INDUSTRIAL AIR PARK | [72 empty] | 705
USA | NM | SANTA FE COUNTY MUNICIPAL AP | [72 empty] | 706
USA | NM | SIERRA BLANCA RGNL | [72 empty] | 707
USA | NM | TAOS MUNI APT(AWOS) | [72 empty] | 708
USA | NM | TRUTH OR CONSEQUENCES MUNI AP | [72 empty] | 709
USA | NS | GREENWOOD AP | [72 empty] | 710
USA | NS | HALIFAX | [72 empty] | 711
USA | NS | SHEARWATER | [72 empty] | 712
USA | NS | SYDNEY AP | [72 empty] | 713
USA | NT | YELLOWKNIFE AP | [72 empty] | 714
USA | NU | IQALUIT | [72 empty] | 715
USA | NV | ELKO MUNICIPAL ARPT | [72 empty] | 716
USA | NV | ELY YELLAND FIELD | [72 empty] | 717
USA | NV | FALLON NAAS | [72 empty] | 718
USA | NV | LAS VEGAS MCCARRAN INTL AP | [72 empty] | 719
USA | NV | LOVELOCK DERBY FIELD | [72 empty] | 720
USA | NV | MERCURY DESERT ROCK AP [SURFRAD] | [72 empty] | 721
USA | NV | NELLIS AFB | [72 empty] | 722
USA | NV | RENO TAHOE INTERNATIONAL AP | [72 empty] | 723
USA | NV | TONOPAH AIRPORT | [72 empty] | 724
USA | NV | WINNEMUCCA MUNICIPAL ARPT | [72 empty] | 725
USA | NY | ADIRONDACK RGNL | [72 empty] | 726
USA | NY | ALBANY COUNTY AP | [72 empty] | 727
USA | NY | BINGHAMTON EDWIN A LINK FIELD | [72 empty] | 728
USA | NY | BUFFALO NIAGARA INTL AP | [72 empty] | 729
USA | NY | ELMIRA CORNING REGIONAL AP | [72 empty] | 730
USA | NY | FORT DRUM/WHEELER-S | [72 empty] | 731
USA | NY | GLENS FALLS AP | [72 empty] | 732
USA | NY | ISLIP LONG ISL MACARTHUR AP | [72 empty] | 733
USA | NY | JAMESTOWN (AWOS) | [72 empty] | 734
USA | NY | MASSENA AP | [72 empty] | 735
USA | NY | MONTICELLO(AWOS) | [72 empty] | 736
USA | NY | NEW YORK CENTRAL PRK OBS BELV | [72 empty] | 737
USA | NY | NEW YORK J F KENNEDY INT AR | [72 empty] | 738
USA | NY | NEW YORK LAGUARDIA ARPT | [72 empty] | 739
USA | NY | NIAGARA FALLS AF | [72 empty] | 740
USA | NY | POUGHKEEPSIE DUTCHESS CO AP | [72 empty] | 741
USA | NY | REPUBLIC | [72 empty] | 742
USA | NY | ROCHESTER GREATER ROCHESTER I | [72 empty] | 743
USA | NY | STEWART FIELD | [72 empty] | 744
USA | NY | SYRACUSE HANCOCK INT ARPT | [72 empty] | 745
USA | NY | UTICA ONEIDA COUNTY AP | [72 empty] | 746
USA | NY | WATERTOWN AP | [72 empty] | 747
USA | NY | WESTHAMPTON GABRESKI AP | [72 empty] | 748
USA | NY | WHITE PLAINS WESTCHESTER CO A | [72 empty] | 749
USA | OH | AKRON AKRON-CANTON REG AP | [72 empty] | 750
USA | OH | BURKE LAKEFRONT | [72 empty] | 751
USA | OH | CINCINNATI MUNICIPAL AP LUNKI | [72 empty] | 752
USA | OH | CLEVELAND HOPKINS INTL AP | [72 empty] | 753
USA | OH | COLUMBUS PORT COLUMBUS INTL A | [72 empty] | 754
USA | OH | DAYTON INTERNATIONAL AIRPORT | [72 empty] | 755
USA | OH | FINDLAY AIRPORT | [72 empty] | 756
USA | OH | MANSFIELD LAHM MUNICIPAL ARPT | [72 empty] | 757
USA | OH | OHIO STATE UNIVERSI | [72 empty] | 758
USA | OH | TOLEDO EXPRESS AIRPORT | [72 empty] | 759
USA | OH | YOUNGSTOWN REGIONAL AIRPORT | [72 empty] | 760
USA | OH | ZANESVILLE MUNICIPAL AP | [72 empty] | 761
USA | OK | ALTUS AFB | [72 empty] | 762
USA | OK | CLINTON-SHERMAN | [72 empty] | 763
USA | OK | FORT SILL POST FIELD AF | [72 empty] | 764
USA | OK | GAGE AIRPORT | [72 empty] | 765
USA | OK | HOBART MUNICIPAL AP | [72 empty] | 766
USA | OK | LAWTON MUNICIPAL | [72 empty] | 767
USA | OK | MCALESTER MUNICIPAL AP | [72 empty] | 768
USA | OK | OKLAHOMA CITY TINKER AFB | [72 empty] | 769
USA | OK | OKLAHOMA CITY WILL ROGERS WOR | [72 empty] | 770
USA | OK | OKLAHOMA CITY/WILEY | [72 empty] | 771
USA | OK | PONCA CITY MUNICIPAL AP [SGP - ARM] | [72 empty] | 772
USA | OK | STILLWATER RGNL | [72 empty] | 773
USA | OK | TULSA INTERNATIONAL AIRPORT | [72 empty] | 774
USA | OK | VANCE AFB | [72 empty] | 775
Canada | ON | BEAUSOLEIL | [72 empty] | 776
Canada | ON | BURLINGTON PIERS | [72 empty] | 777
Canada | ON | ERIEAU | [72 empty] | 778
Canada | ON | LAGOON CITY | [72 empty] | 779
Canada | ON | LONDON AP | [72 empty] | 780
Canada | ON | NORTH BAY AP | [72 empty] | 781
Canada | ON | OTTAWA | [72 empty] | 782
Canada | ON | PETERBOROUGH AP | [72 empty] | 783
Canada | ON | PORT WELLER | [72 empty] | 784
Canada | ON | SAULT STE MARIE | [72 empty] | 785
Canada | ON | SUDBURY AP | [72 empty] | 786
Canada | ON | THUNDER BAY AP | [72 empty] | 787
Canada | ON | TIMMINS AP | [72 empty] | 788
Canada | ON | TORONTO AP | [72 empty] | 789
Canada | ON | TORONTO ISLAND AP | [72 empty] | 790
Canada | ON | TORONTO | [72 empty] | 791
Canada | ON | TRENTON AP | [72 empty] | 792
Canada | ON | WINDSOR | [72 empty] | 793
USA | OR | ASTORIA REGIONAL AIRPORT | [72 empty] | 794
USA | OR | AURORA STATE | [72 empty] | 795
USA | OR | BAKER MUNICIPAL AP | [72 empty] | 796
USA | OR | BURNS MUNICIPAL ARPT [UO] | [72 empty] | 797
USA | OR | CORVALLIS MUNI | [72 empty] | 798
USA | OR | EUGENE MAHLON SWEET ARPT [UO] | [72 empty] | 799
USA | OR | KLAMATH FALLS INTL AP [UO] | [72 empty] | 800
USA | OR | LA GRANDE MUNI AP | [72 empty] | 801
USA | OR | LAKEVIEW (AWOS) | [72 empty] | 802
USA | OR | MEDFORD ROGUE VALLEY INTL AP [ASHLAND - UO] | [72 empty] | 803
USA | OR | NORTH BEND MUNI AIRPORT | [72 empty] | 804
USA | OR | PENDLETON E OR REGIONAL AP | [72 empty] | 805
USA | OR | PORTLAND INTERNATIONAL AP | [72 empty] | 806
USA | OR | PORTLAND/HILLSBORO | [72 empty] | 807
USA | OR | PORTLAND/TROUTDALE | [72 empty] | 808
USA | OR | REDMOND ROBERTS FIELD | [72 empty] | 809
USA | OR | ROSEBURG REGIONAL AP | [72 empty] | 810
USA | OR | SALEM MCNARY FIELD | [72 empty] | 811
USA | OR | SEXTON SUMMIT | [72 empty] | 812
USA | PA | ALLENTOWN LEHIGH VALLEY INTL | [72 empty] | 813
USA | PA | ALTOONA BLAIR CO ARPT | [72 empty] | 814
USA | PA | BRADFORD REGIONAL AP | [72 empty] | 815
USA | PA | BUTLER CO (AWOS) | [72 empty] | 816
USA | PA | DUBOIS FAA AP | [72 empty] | 817
USA | PA | ERIE INTERNATIONAL AP | [72 empty] | 818
USA | PA | FRANKLIN | [72 empty] | 819
USA | PA | HARRISBURG CAPITAL CITY ARPT | [72 empty] | 820
USA | PA | JOHNSTOWN CAMBRIA COUNTY AP | [72 empty] | 821
USA | PA | LANCASTER | [72 empty] | 822
USA | PA | MIDDLETOWN HARRISBURG INTL AP | [72 empty] | 823
USA | PA | PHILADELPHIA INTERNATIONAL AP | [72 empty] | 824
USA | PA | PHILADELPHIA NE PHILADELPHIA | [72 empty] | 825
USA | PA | PITTSBURGH ALLEGHENY CO AP | [72 empty] | 826
USA | PA | PITTSBURGH INTERNATIONAL AP | [72 empty] | 827
USA | PA | READING SPAATZ FIELD | [72 empty] | 828
USA | PA | STATE COLLEGE [PENN STATE - SURFRAD] | [72 empty] | 829
USA | PA | WASHINGTON (AWOS) | [72 empty] | 830
USA | PA | WILKES-BARRE SCRANTON INTL AP | [72 empty] | 831
USA | PA | WILLIAMSPORT REGIONAL AP | [72 empty] | 832
USA | PA | WILLOW GROVE NAS | [72 empty] | 833
Canada | PE | CHARLOTTETOWN | [72 empty] | 834
Canada | QC | JONQUIERE | [72 empty] | 835
Canada | QC | LA BAIE | [72 empty] | 836
Canada | QC | LACADIE | [72 empty] | 837
Canada | QC | LASSOMPTION | [72 empty] | 838
Canada | QC | LENNOXVILLE | [72 empty] | 839
Canada | QC | MC TAVISH | [72 empty] | 840
Canada | QC | MONT JOLI AB | [72 empty] | 841
Canada | QC | MONT-ORFORD | [72 empty] | 842
Canada | QC | MONTREAL | [72 empty] | 843
Canada | QC | MONTREAL-MIRABEL | [72 empty] | 844
Canada | QC | NICOLET | [72 empty] | 845
Canada | QC | POINT-AU-PERE | [72 empty] | 846
Canada | QC | QUEBEC AP | [72 empty] | 847
Canada | QC | SHERBROOKE AP | [72 empty] | 848
Canada | QC | ST ANICET | [72 empty] | 849
Canada | QC | STE ANNE DE BELLEVUE | [72 empty] | 850
Canada | QC | STE FOY | [72 empty] | 851
Canada | QC | TROIS RIVIERES | [72 empty] | 852
Canada | QC | VARENNES | [72 empty] | 853
USA | RI | BLOCK ISLAND STATE ARPT | [72 empty] | 854
USA | RI | PAWTUCKET (AWOS) | [72 empty] | 855
USA | RI | PROVIDENCE T F GREEN STATE AR | [72 empty] | 856
Saudi Arabia | SA | RIYADH | [72 empty] | 857
USA | SC | ANDERSON COUNTY AP | [72 empty] | 858
USA | SC | BEAUFORT MCAS | [72 empty] | 859
USA | SC | CHARLESTON INTL ARPT | [72 empty] | 860
USA | SC | COLUMBIA METRO ARPT | [72 empty] | 861
USA | SC | FLORENCE REGIONAL AP | [72 empty] | 862
USA | SC | GREENVILLE DOWNTOWN AP | [72 empty] | 863
USA | SC | GREER GREENV-SPARTANBRG AP | [72 empty] | 864
USA | SC | MYRTLE BEACH AFB | [72 empty] | 865
USA | SC | SUMTER SHAW AFB | [72 empty] | 866
USA | SD | ABERDEEN REGIONAL ARPT | [72 empty] | 867
USA | SD | BROOKINGS (AWOS) | [72 empty] | 868
USA | SD | CHAN GURNEY MUNI | [72 empty] | 869
USA | SD | ELLSWORTH AFB | [72 empty] | 870
USA | SD | HURON REGIONAL ARPT | [72 empty] | 871
USA | SD | MITCHELL (AWOS) | [72 empty] | 872
USA | SD | MOBRIDGE | [72 empty] | 873
USA | SD | PIERRE MUNICIPAL AP | [72 empty] | 874
USA | SD | RAPID CITY REGIONAL ARPT | [72 empty] | 875
USA | SD | SIOUX FALLS FOSS FIELD | [72 empty] | 876
USA | SD | WATERTOWN MUNICIPAL AP | [72 empty] | 877
Canada | SK | MOOSE JAW AP | [72 empty] | 878
Canada | SK | PRINCE ALBERT AP | [72 empty] | 879
Canada | SK | REGINA | [72 empty] | 880
Canada | SK | SASKATOON | [72 empty] | 881
USA | TN | BRISTOL TRI CITY AIRPORT | [72 empty] | 882
USA | TN | CHATTANOOGA LOVELL FIELD AP | [72 empty] | 883
USA | TN | CROSSVILLE MEMORIAL AP | [72 empty] | 884
USA | TN | DYERSBURG MUNICIPAL AP | [72 empty] | 885
USA | TN | JACKSON MCKELLAR-SIPES REGL A | [72 empty] | 886
USA | TN | KNOXVILLE MCGHEE TYSON AP | [72 empty] | 887
USA | TN | MEMPHIS INTERNATIONAL AP | [72 empty] | 888
USA | TN | NASHVILLE INTERNATIONAL AP | [72 empty] | 889
USA | TX | ABILENE DYESS AFB | [72 empty] | 890
USA | TX | ABILENE REGIONAL AP [UT] | [72 empty] | 891
USA | TX | ALICE INTL AP | [72 empty] | 892
USA | TX | AMARILLO INTERNATIONAL AP [CANYON - UT] | [72 empty] | 893
USA | TX | AUSTIN MUELLER MUNICIPAL AP [UT] | [72 empty] | 894
USA | TX | BROWNSVILLE S PADRE ISL INTL | [72 empty] | 895
USA | TX | CAMP MABRY | [72 empty] | 896
USA | TX | CHILDRESS MUNICIPAL AP | [72 empty] | 897
USA | TX | COLLEGE STATION EASTERWOOD FL | [72 empty] | 898
USA | TX | CORPUS CHRISTI INTL ARPT [UT] | [72 empty] | 899
USA | TX | CORPUS CHRISTI NAS | [72 empty] | 900
USA | TX | COTULLA FAA AP | [72 empty] | 901
USA | TX | COX FLD | [72 empty] | 902
USA | TX | DALHART MUNICIPAL AP | [72 empty] | 903
USA | TX | DALLAS-FORT WORTH INTL AP | [72 empty] | 904
USA | TX | DALLAS/ADDISON ARPT | [72 empty] | 905
USA | TX | DALLAS/REDBIRD ARPT | [72 empty] | 906
USA | TX | DEL RIO [UT] | [72 empty] | 907
USA | TX | DEL RIO LAUGHLIN AFB | [72 empty] | 908
USA | TX | DRAUGHON MILLER CEN | [72 empty] | 909
USA | TX | EL PASO INTERNATIONAL AP [UT] | [72 empty] | 910
USA | TX | FORT HOOD | [72 empty] | 911
USA | TX | FORT WORTH ALLIANCE | [72 empty] | 912
USA | TX | FORT WORTH MEACHAM | [72 empty] | 913
USA | TX | FORT WORTH NAS | [72 empty] | 914
USA | TX | GALVESTON/SCHOLES | [72 empty] | 915
USA | TX | GEORGETOWN (AWOS) | [72 empty] | 916
USA | TX | HARLINGEN RIO GRANDE VALLEY I | [72 empty] | 917
USA | TX | HONDO MUNICIPAL AP | [72 empty] | 918
USA | TX | HOUSTON BUSH INTERCONTINENTAL | [72 empty] | 919
USA | TX | HOUSTON ELLINGTON AFB [CLEAR LAKE - UT] | [72 empty] | 920
USA | TX | HOUSTON WILLIAM P HOBBY AP | [72 empty] | 921
USA | TX | HOUSTON/D.W. HOOKS | [72 empty] | 922
USA | TX | KINGSVILLE | [72 empty] | 923
USA | TX | LAREDO INTL AP [UT] | [72 empty] | 924
USA | TX | LONGVIEW GREGG COUNTY AP [OVERTON - UT] | [72 empty] | 925
USA | TX | LUBBOCK INTERNATIONAL AP | [72 empty] | 926
USA | TX | LUFKIN ANGELINA CO | [72 empty] | 927
USA | TX | MARFA AP | [72 empty] | 928
USA | TX | MC GREGOR (AWOS) | [72 empty] | 929
USA | TX | MCALLEN MILLER INTL AP [EDINBURG - UT] | [72 empty] | 930
USA | TX | MIDLAND INTERNATIONAL AP | [72 empty] | 931
USA | TX | MINERAL WELLS MUNICIPAL AP | [72 empty] | 932
USA | TX | NACOGDOCHES (AWOS) | [72 empty] | 933
USA | TX | PALACIOS MUNICIPAL AP | [72 empty] | 934
USA | TX | PORT ARTHUR JEFFERSON COUNTY | [72 empty] | 935
USA | TX | RANDOLPH AFB | [72 empty] | 936
USA | TX | ROCKPORT/ARANSAS CO | [72 empty] | 937
USA | TX | SAN ANGELO MATHIS FIELD | [72 empty] | 938
USA | TX | SAN ANTONIO INTL AP | [72 empty] | 939
USA | TX | SAN ANTONIO KELLY FIELD AFB | [72 empty] | 940
USA | TX | SAN ANTONIO/STINSON | [72 empty] | 941
USA | TX | TYLER/POUNDS FLD | [72 empty] | 942
USA | TX | VICTORIA REGIONAL AP | [72 empty] | 943
USA | TX | WACO REGIONAL AP | [72 empty] | 944
USA | TX | WICHITA FALLS MUNICIPAL ARPT | [72 empty] | 945
USA | TX | WINK WINKLER COUNTY AP | [72 empty] | 946
USA | UT | CEDAR CITY MUNICIPAL AP | [72 empty] | 947
USA | UT | MOAB/CANYONLANDS [UO] | [72 empty] | 948
USA | UT | OGDEN HILL AFB | [72 empty] | 949
USA | UT | OGDEN HINKLEY AIRPORT | [72 empty] | 950
USA | UT | PROVO MUNI (AWOS) | [72 empty] | 951
USA | UT | SAINT GEORGE (AWOS) | [72 empty] | 952
USA | UT | SALT LAKE CITY INT ARPT [ISIS] | [72 empty] | 953
USA | UT | VERNAL | [72 empty] | 954
USA | UT | WENDOVER USAF AUXILIARY FIELD | [72 empty] | 955
USA | VA | ABINGDON | [72 empty] | 956
USA | VA | CHARLOTTESVILLE FAA | [72 empty] | 957
USA | VA | DANVILLE FAA AP | [72 empty] | 958
USA | VA | DAVISON AAF | [72 empty] | 959
USA | VA | FARMVILLE | [72 empty] | 960
USA | VA | FRANKLIN NAAS | [72 empty] | 961
USA | VA | HILLSVILLE | [72 empty] | 962
USA | VA | HOT SPRINGS/INGALLS | [72 empty] | 963
USA | VA | LANGLEY AFB | [72 empty] | 964
USA | VA | LEESBURG/GODFREY | [72 empty] | 965
USA | VA | LYNCHBURG REGIONAL ARPT | [72 empty] | 966
USA | VA | MANASSAS MUNI(AWOS) | [72 empty] | 967
USA | VA | MARION / WYTHEVILLE | [72 empty] | 968
USA | VA | MARTINSVILLE | [72 empty] | 969
USA | VA | MELFA/ACCOMACK ARPT | [72 empty] | 970
USA | VA | NEWPORT NEWS | [72 empty] | 971
USA | VA | NORFOLK INTERNATIONAL AP | [72 empty] | 972
USA | VA | NORFOLK NAS | [72 empty] | 973
USA | VA | OCEANA NAS | [72 empty] | 974
USA | VA | QUANTICO MCAS | [72 empty] | 975
USA | VA | RICHMOND INTERNATIONAL AP | [72 empty] | 976
USA | VA | ROANOKE REGIONAL AP | [72 empty] | 977
USA | VA | SHANNON ARPT | [72 empty] | 978
USA | VA | STAUNTON/SHENANDOAH | [72 empty] | 979
USA | VA | VIRGINIA TECH ARPT | [72 empty] | 980
USA | VA | WASHINGTON DC DULLES INT AR [STERLING - ISIS] | [72 empty] | 981
USA | VA | WASHINGTON DC REAGAN AP | [72 empty] | 982
USA | VA | WINCHESTER RGNL | [72 empty] | 983
USA | VA | WISE/LONESOME PINE | [72 empty] | 984
USA | VT | BURLINGTON INTERNATIONAL AP | [72 empty] | 985
USA | VT | HO CHI MIHN | [72 empty] | 986
USA | VT | MONTPELIER AP | [72 empty] | 987
USA | VT | RUTLAND STATE | [72 empty] | 988
USA | VT | SPRINGFIELD/HARTNES | [72 empty] | 989
USA | WA | BELLINGHAM INTL AP | [72 empty] | 990
USA | WA | BREMERTON NATIONAL | [72 empty] | 991
USA | WA | EPHRATA AP FCWOS | [72 empty] | 992
USA | WA | FAIRCHILD AFB | [72 empty] | 993
USA | WA | FELTS FLD | [72 empty] | 994
USA | WA | GRAY AAF | [72 empty] | 995
USA | WA | HANFORD | [72 empty] | 996
USA | WA | HOQUIAM AP | [72 empty] | 997
USA | WA | KELSO WB AP | [72 empty] | 998
USA | WA | MOSES LAKE GRANT COUNTY AP | [72 empty] | 999
USA | WA | OLYMPIA AIRPORT | [72 empty] | 1000
USA | WA | PASCO | [72 empty] | 1001
USA | WA | PULLMAN/MOSCOW RGNL | [72 empty] | 1002
USA | WA | QUILLAYUTE STATE AIRPORT | [72 empty] | 1003
USA | WA | RENTON MUNI | [72 empty] | 1004
USA | WA | SEATTLE BOEING FIELD [ISIS] | [72 empty] | 1005
USA | WA | SEATTLE SEATTLE-TACOMA INTL A | [72 empty] | 1006
USA | WA | SNOHOMISH CO | [72 empty] | 1007
USA | WA | SPOKANE INTERNATIONAL AP [CHENEY - UO] | [72 empty] | 1008
USA | WA | STAMPEDE PASS | [72 empty] | 1009
USA | WA | TACOMA MCCHORD AFB | [72 empty] | 1010
USA | WA | TACOMA NARROWS | [72 empty] | 1011
USA | WA | THE DALLES MUNICIPAL ARPT | [72 empty] | 1012
USA | WA | WALLA WALLA CITY COUNTY AP | [72 empty] | 1013
USA | WA | WENATCHEE/PANGBORN | [72 empty] | 1014
USA | WA | WHIDBEY ISLAND NAS | [72 empty] | 1015
USA | WA | WILLIAM R FAIRCHILD | [72 empty] | 1016
USA | WA | YAKIMA AIR TERMINAL | [72 empty] | 1017
USA | WI | APPLETON/OUTAGAMIE | [72 empty] | 1018
USA | WI | EAU CLAIRE COUNTY AP | [72 empty] | 1019
USA | WI | GREEN BAY AUSTIN STRAUBEL INT | [72 empty] | 1020
USA | WI | JANESVILLE/ROCK CO. | [72 empty] | 1021
USA | WI | LA CROSSE MUNICIPAL ARPT | [72 empty] | 1022
USA | WI | LONE ROCK FAA AP | [72 empty] | 1023
USA | WI | MADISON DANE CO REGIONAL ARPT [ISIS] | [72 empty] | 1024
USA | WI | MANITOWOC MUNI AWOS | [72 empty] | 1025
USA | WI | MARSHFIELD MUNI | [72 empty] | 1026
USA | WI | MILWAUKEE MITCHELL INTL AP | [72 empty] | 1027
USA | WI | MINOCQUA/WOODRUFF | [72 empty] | 1028
USA | WI | MOSINEE/CENTRAL WI | [72 empty] | 1029
USA | WI | PHILLIPS/PRICE CO. | [72 empty] | 1030
USA | WI | RHINELANDER ONEIDA | [72 empty] | 1031
USA | WI | RICE LAKE MUNICIPAL | [72 empty] | 1032
USA | WI | STURGEON BAY | [72 empty] | 1033
USA | WI | WATERTOWN | [72 empty] | 1034
USA | WI | WAUSAU MUNICIPAL ARPT | [72 empty] | 1035
USA | WI | WITTMAN RGNL | [72 empty] | 1036
USA | WV | BECKLEY RALEIGH CO MEM AP | [72 empty] | 1037
USA | WV | BLUEFIELD/MERCER CO [NREL] | [72 empty] | 1038
USA | WV | CHARLESTON YEAGER ARPT | [72 empty] | 1039
USA | WV | ELKINS ELKINS-RANDOLPH CO ARP | [72 empty] | 1040
USA | WV | HARRISON MARION RGN | [72 empty] | 1041
USA | WV | HUNTINGTON TRI-STATE ARPT | [72 empty] | 1042
USA | WV | LEWISBURG/GREENBRIE | [72 empty] | 1043
USA | WV | MARTINSBURG EASTERN WV REG AP | [72 empty] | 1044
USA | WV | MORGANTOWN HART FIELD | [72 empty] | 1045
USA | WV | PARKERSBURG WOOD COUNTY AP | [72 empty] | 1046
USA | WV | WHEELING OHIO COUNTY AP | [72 empty] | 1047
USA | WY | CASPER NATRONA CO INTL AP | [72 empty] | 1048
USA | WY | CHEYENNE MUNICIPAL ARPT | [72 empty] | 1049
USA | WY | CODY MUNI (AWOS) | [72 empty] | 1050
USA | WY | GILLETTE/GILLETTE-C | [72 empty] | 1051
USA | WY | JACKSON HOLE | [72 empty] | 1052
USA | WY | LANDER HUNT FIELD | [72 empty] | 1053
USA | WY | LARAMIE GENERAL BREES FIELD | [72 empty] | 1054
USA | WY | RAWLINS MUNICIPAL AP | [72 empty] | 1055
USA | WY | RIVERTON MUNICIPL AP | [72 empty] | 1056
USA | WY | SHERIDAN COUNTY ARPT | [72 empty] | 1057
USA | WY | WORLAND MUNICIPAL | [72 empty] | 1058
Canada | YT | WHITEHORSE | [72 empty] | 1059