## QAHV-N136
v26.1.0 - 2026.03
Phius - Mitsubishi QAHV CO2: HPWH COP Estimator
Climate Data | [9 empty] | Required input cells.
Type of Phius Climate Data | Country | State | Phius Climate Location | [6 empty] | Required dropdown menu inputs.
Select | Select | Select | Select
Outputs for Energy Model (WUFI Passive or METr) | [9 empty] | Calculated.
Leaving Water Temperature (°F): |  | Select | Round up to the nearest leaving water tempature. | [6 empty] | Calculated from another sheet.
Heat Exchanger Efficiency (%): |  | 85% | If a heat exchanger is used, input the efficiency from the datasheet or use a default of 85%. If no heat exchanger is used, input 100%. | [6 empty] | Output for WUFI Passive or METr
Annual Heating Coefficient of Performance (COP): |  | 0 | System 1 > Device/Equipment > Add line item for 'Heat Pump'. Set coverage to 'DHW'. Under Device > Set 'Type' to 'Heat Pump'. Water storage must be modeled as a separate device. | [6 empty] | Constants & Instructions
Total System Performance Ratio of Heat Generator: |  | -
-
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31
Ambient Temp (°F) | - | - | - | - | - | - | - | - | - | - | - | -
Dew Point (°F) | - | - | - | - | - | - | - | - | - | - | - | -
Capacity Correction Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Weighted COP @130 (°F) | - | - | - | - | - | - | - | - | - | - | - | -
Weighted COP @150 (°F) | - | - | - | - | - | - | - | - | - | - | - | -
Weighted COP @170 (°F) | - | - | - | - | - | - | - | - | - | - | - | -
Leaving Water Temperature (°F) | V3 | V2 | V1 | Intercept |  | Select
130 | -8e-06 | 0.0011 | -0.0027 | 1.1846 |  | 130 | 0
150 | -8e-06 | 0.0011 | -0.0017 | 1.2438 |  | 150 | 0
170 | -4e-06 | 0.0005 | 0.0035 | 1.2602 |  | 170 | 0
Outside Air Temp (°F) | COP @ 130F | COP @ 150F | COP @ 170F
-10 | 1.2377 | 1.2877 | 1.2485
0 | 1.2826 | 1.3343 | 1.2839
10 | 1.377 | 1.4341 | 1.3777
20 | 1.5673 | 1.6282 | 1.5565
30 | 1.7216 | 1.7817 | 1.6995
40 | 2.066 | 2.1298 | 1.9369
50 | 2.8054 | 2.8797 | 2.3455
60 | 3.5321 | 3.5228 | 2.5509
70 | 3.6437 | 3.6901 | 2.8785
80 | 3.6981 | 3.7767 | 3.0756
90 | 3.6684 | 3.8059 | 3.2188
100 | 3.7273 | 3.8716 | 3.2346

## Custom Climate Data
Passive House Planning
OFFICIAL CLIMATE DATA SET
METRIC:
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Heating Load |  | Cooling Load
Days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 | Weather 1 | Weather 2 | Radiation
ALGONA IA | Latitude: | 43.083 | Longitude ° East: | -94.267 | Altitude (m): | 372 | 0 |  | Daily temperature variation summer (K) | 10.5 | Radiation Data: | kWh/(m²*month) | Radiation: W/m² |  | W/m²
Ambient Temp (°C) | -8.1 | -6.2 | 6.1 | 9.3 | 13.1 | 20.7 | 24 | 21.8 | 15.5 | 11.6 | 1.7 | -2.9 | -15.8 | -12.3 | 25.9
North | 19 | 32 | 36 | 42 | 51 | 56 | 56 | 46 | 32 | 25 | 19 | 17 | 20 | 20 | 71
East | 27 | 56 | 83 | 106 | 91 | 93 | 98 | 95 | 71 | 57 | 36 | 30 | 32 | 32 | 149
South | 47 | 106 | 123 | 116 | 79 | 73 | 84 | 95 | 99 | 98 | 90 | 72 | 40 | 40 | 148
West | 33 | 62 | 80 | 100 | 94 | 94 | 108 | 100 | 77 | 56 | 43 | 30 | 28 | 28 | 156
Global | 33 | 70 | 115 | 166 | 158 | 165 | 182 | 162 | 117 | 85 | 54 | 35 | 32 | 32 | 285
Dewpoint | -11.4 | -13.3 | -1.3 | -0.5 | 6.8 | 14.2 | 17.8 | 16.2 | 11.1 | 4.4 | -5.7 | -4.9
Sky temperature | -23.1 | -24.3 | -9.5 | -8.4 | 0.9 | 9.1 | 13.4 | 11.4 | 5.7 | -1.5 | -13.5 | -14.3
US CUSTOMARY:
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Heating Load |  | Cooling Load
Days | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 | Weather 1 | Weather 2 | Radiation
ALGONA IA | Latitude: | 43.083 | Longitude ° East: | -94.267 | Altitude (ft): | 1220.4724 | 0 |  | Daily temperature variation summer (F) | 18.9 | Radiation Data: | kBTU/(ft².month) | Radiation: BTU/hr.ft² |  | BTU/hr.ft²
Ambient Temp (°F) | 17.42 | 20.84 | 42.98 | 48.74 | 55.58 | 69.26 | 75.2 | 71.24 | 59.9 | 52.88 | 35.06 | 26.78 | 3.56 | 9.86 | 78.62
North | 6.023 | 10.144 | 11.4119 | 13.3139 | 16.1669 | 17.7519 | 17.7519 | 14.5819 | 10.144 | 7.925 | 6.023 | 5.389 | 6.34 | 6.34 | 22.5069
East | 8.559 | 17.7519 | 26.3109 | 33.6018 | 28.8469 | 29.4809 | 31.0659 | 30.1149 | 22.5069 | 18.0689 | 11.4119 | 9.51 | 10.144 | 10.144 | 47.2328
South | 14.8989 | 33.6018 | 38.9908 | 36.7718 | 25.0429 | 23.1409 | 26.6279 | 30.1149 | 31.3829 | 31.0659 | 28.5299 | 22.8239 | 12.6799 | 12.6799 | 46.9158
West | 10.461 | 19.6539 | 25.3599 | 31.6998 | 29.7979 | 29.7979 | 34.2358 | 31.6998 | 24.4089 | 17.7519 | 13.6309 | 9.51 | 8.876 | 8.876 | 49.4518
Global | 10.461 | 22.1899 | 36.4548 | 52.6217 | 50.0858 | 52.3048 | 57.6937 | 51.3538 | 37.0888 | 26.9449 | 17.1179 | 11.0949 | 10.144 | 10.144 | 90.3446
Dewpoint | 11.48 | 8.06 | 29.66 | 31.1 | 44.24 | 57.56 | 64.04 | 61.16 | 51.98 | 39.92 | 21.74 | 23.18
Sky temperature | -9.58 | -11.74 | 14.9 | 16.88 | 33.62 | 48.38 | 56.12 | 52.52 | 42.26 | 29.3 | 7.7 | 6.26
Note on H6: Altitude of Weather Station
Note on I6: Input of building site altitude only required if highly different from weather station altitude. For empty input no temperature correction is applied.
Note on H21: Altitude of Weather Station
Note on I21: Input of building site altitude only required if highly different from weather station altitude. For empty input no temperature correction is applied.

## Update Tracker
Version | Update | Date | Description
v26.1.0 | 1 | 2026-03-24 | Calculation line added to account for heat exchangers which are typically used in tandem with this system.

## Climate Data (hidden)
|  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49
Current Location |  | 2: Temperature (F); 14: Dewpoint (F); 26: Relative Humidity; 38: Capacity Correction Factor
Select | Select | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
State | City_WUFIp Data Set | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
BC | ABBOTSFORD AP | Jan: 38.4; Feb: 41.2; Mar: 44.6; Apr: 49.6; May: 55.6; Jun: 60.1; Jul: 65.1; Aug: 65.2; Sep: 60.1; Oct: 51.1; Nov: 43.1; Dec: 37.8; Jan: 32.4; Feb: 32.18; Mar: 35.4; Apr: 38.48; May: 44.2; Jun: 49.1; Jul: 53.06; Aug: 53.06; Sep: 49.8; Oct: 43.52; Nov: 37.4; Dec: 31.5; Mar: Outside Air Temp (F)
SD | ABERDEEN REGIONAL ARPT | 12.5 | 17.6 | 30 | 44.2 | 56.7 | 66.5 | 71.4 | 69.3 | 60.2 | 46.2 | 30.2 | 17.5 | 6.4 | 6.26 | 25.9 | 32.36 | 49.6 | 57.2 | 59.72 | 60.98 | 52.5 | 41 | 22.6 | 15.3 |  | RH | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85
TX | ABILENE DYESS AFB | 44.7 | 49.3 | 56.8 | 65.2 | 74.3 | 82.2 | 84.4 | 83.6 | 75.6 | 66.2 | 54.5 | 46.6 | 26.6 | 25.16 | 27.5 | 37.76 | 56.3 | 64.22 | 64.4 | 61.16 | 53.8 | 44.24 | 35.1 | 30.9 |  | 30% | 0.97 | 0.96 | 0.96 | 0.95 | 0.94 | 0.94 | 0.96 | 0.99 | 1.01 | 0.89 | 0.84 | 0.88 | 0.89 | 0.91 | 0.92 | 0.94 | 0.95 | 0.97 | 0.98
TX | ABILENE REGIONAL AP [UT] | 45.8 | 49.6 | 57 | 65.3 | 73.3 | 80.4 | 83.3 | 83 | 75.7 | 66.1 | 54.7 | 46.3 | 24.4 | 29.84 | 39 | 45.32 | 58.1 | 60.62 | 61.7 | 62.78 | 57.4 | 47.66 | 38.1 | 27 |  | 40% | 0.97 | 0.97 | 0.96 | 0.96 | 0.95 | 0.95 | 0.98 | 1 | 1.03 | 0.88 | 0.86 | 0.92 | 0.93 | 0.94 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99
VA | ABINGDON | 36 | 39.4 | 47.1 | 56.1 | 64.2 | 71.6 | 74.1 | 73.9 | 67.9 | 57.2 | 46.7 | 38.9 | 31.8 | 24.62 | 32.2 | 35.42 | 44.2 | 59.18 | 62.6 | 62.42 | 49.3 | 39.92 | 30.2 | 30.9 |  | 50% | 0.98 | 0.97 | 0.97 | 0.97 | 0.96 | 0.97 | 0.99 | 1.02 | 1.02 | 0.88 | 0.89 | 0.95 | 0.96 | 0.97 | 0.97 | 0.98 | 0.98 | 0.99 | 0.99
AK | ADAK NAS | 32.3 | 33.3 | 33.9 | 36.4 | 40.3 | 45.2 | 49.1 | 51.3 | 47.9 | 42.3 | 37.6 | 33.5 | 25.9 | 29.48 | 30.4 | 25.88 | 32.4 | 36.5 | 42.98 | 41.36 | 34.5 | 33.44 | 30.6 | 27.1 |  | 60% | 0.99 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 1 | 1.01 | 1.01 | 0.89 | 0.93 | 0.97 | 0.98 | 0.98 | 0.98 | 0.99 | 0.99 | 1 | 1
NY | ADIRONDACK RGNL | 13.9 | 15.7 | 25 | 39 | 50.8 | 59.7 | 63.6 | 62 | 55 | 43.7 | 33.1 | 20.8 | 12.7 | 12.92 | 22.5 | 25.88 | 41.2 | 53.06 | 54.68 | 56.48 | 47.5 | 33.98 | 25.7 | 14.5 |  | 70% | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 1.01 | 1.01 | 1.01 | 0.9 | 0.96 | 0.99 | 1 | 1.01 | 1.01 | 1 | 1 | 1 | 1
BC | AGASSIZ CDA | 38 | 41.4 | 44.5 | 50.2 | 56.7 | 60.8 | 65.8 | 65.7 | 61.1 | 51.9 | 42.9 | 38.3 | 28.2 | 31.64 | 36.9 | 41.18 | 47.8 | 53.42 | 57.74 | 57.38 | 53.1 | 45.5 | 37.9 | 28.8 |  | 80% | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98 | 0.99 | 1 | 1.02 | 1.03 | 1.02 | 1.01 | 1 | 1 | 1
NE | AINSWORTH MUNICIPAL | 25.4 | 28.1 | 36.9 | 46.8 | 57.2 | 66.8 | 74.8 | 72.3 | 63.2 | 49.5 | 37.1 | 26.8 | 17.1 | 16.34 | 28.8 | 32.36 | 45.7 | 55.04 | 58.46 | 57.74 | 43.5 | 40.46 | 27.9 | 19.6 |  | 90% | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1 | 1.01 | 1.01 | 1.01 | 1.02 | 1.01 | 1.02 | 1.03 | 1.04 | 1.03 | 1.01 | 1.01 | 1 | 1
MN | AITKIN NDB(AWOS) | Jan: 10; Feb: 14.8; Mar: 27.1; Apr: 40.9; May: 52.9; Jun: 62.3; Jul: 67; Aug: 64.5; Sep: 56.3; Oct: 44.4; Nov: 29.7; Dec: 16.5; Jan: 5.2; Feb: 3.02; Mar: 17.1; Apr: 32.9; May: 38.7; Jun: 51.62; Jul: 61.52; Aug: 57.92; Sep: 48.9; Oct: 42.08; Nov: 23; Dec: 16
OH | AKRON AKRON-CANTON REG AP | Jan: 27.1; Feb: 29.2; Mar: 38; Apr: 49.9; May: 59.8; Jun: 68.7; Jul: 72.3; Aug: 70.8; Sep: 63.5; Oct: 52.3; Nov: 41.4; Dec: 31.8; Jan: 15.4; Feb: 18.5; Mar: 27.7; Apr: 38.66; May: 50.2; Jun: 57.74; Jul: 61.7; Aug: 60.62; Sep: 54.3; Oct: 39.2; Nov: 32; Dec: 21.9; Feb: RH; Mar: Row
CO | AKRON WASHINGTON CO AP | Jan: 29.3; Feb: 31.5; Mar: 40.2; Apr: 47.3; May: 57.5; Jun: 67.9; Jul: 74.3; Aug: 72.4; Sep: 63.7; Oct: 50.6; Nov: 38.2; Dec: 29.2; Jan: 14.7; Feb: 20.12; Mar: 24.6; Apr: 31.28; May: 40.1; Jun: 54.32; Jul: 57.2; Aug: 51.8; Sep: 44.1; Oct: 26.78; Nov: 26.1; Dec: 17.1; Feb: 30%; Mar: 2
CO | ALAMOSA SAN LUIS VALLEY RGNL | Jan: 16.8; Feb: 23.7; Mar: 34.6; Apr: 42.4; May: 51.7; Jun: 60.3; Jul: 64.9; Aug: 62.9; Sep: 55.5; Oct: 43.7; Nov: 29.8; Dec: 17.8; Jan: 5.2; Feb: 10.58; Mar: 16.3; Apr: 18.68; May: 28.2; Jun: 34.7; Jul: 44.42; Aug: 43.7; Sep: 37.2; Oct: 21.92; Nov: 16.5; Dec: 10.9; Feb: 40%; Mar: 3
NY | ALBANY COUNTY AP | Jan: 24.1; Feb: 26.4; Mar: 35.4; Apr: 47.9; May: 58.7; Jun: 67.9; Jul: 72.3; Aug: 70.6; Sep: 62.6; Oct: 50.9; Nov: 40.3; Dec: 29.9; Jan: 12.6; Feb: 15.8; Mar: 23.5; Apr: 32.72; May: 45.9; Jun: 54.14; Jul: 60.44; Aug: 59.36; Sep: 52.3; Oct: 42.26; Nov: 31.8; Dec: 19.6; Feb: 50%; Mar: 4
GA | ALBANY DOUGHERTY COUNTY AP | Jan: 50.5; Feb: 53.5; Mar: 59.7; Apr: 66.4; May: 74.6; Jun: 80.3; Jul: 82.4; Aug: 81.8; Sep: 77.7; Oct: 68.1; Nov: 58.3; Dec: 52.1; Jan: 46; Feb: 46.76; Mar: 43.5; Apr: 55.4; May: 59; Jun: 69.08; Jul: 71.6; Aug: 70.16; Sep: 66.2; Oct: 64.04; Nov: 48.7; Dec: 37.8; Feb: 60%; Mar: 5
MN | ALBERT LEA (AWOS) | Jan: 15.5; Feb: 19.9; Mar: 32.2; Apr: 46.3; May: 57.9; Jun: 68.1; Jul: 72.1; Aug: 69.4; Sep: 61.7; Oct: 49.3; Nov: 34.5; Dec: 21.2; Jan: 18.7; Feb: 16.7; Mar: 26.2; Apr: 36.32; May: 43; Jun: 59.9; Jul: 63.32; Aug: 66.02; Sep: 53.8; Oct: 37.76; Nov: 27.9; Dec: 17.6; Feb: 70%; Mar: 6
NM | ALBUQUERQUE INTL ARPT [ISIS] | Jan: 37.7; Feb: 42.2; Mar: 49.3; Apr: 57; May: 66.6; Jun: 76.3; Jul: 78.8; Aug: 76.7; Sep: 70.2; Oct: 58.5; Nov: 45.9; Dec: 37.1; Jan: 18.5; Feb: 21.74; Mar: 22.1; Apr: 20.48; May: 30; Jun: 39.56; Jul: 51.26; Aug: 50.72; Sep: 45.9; Oct: 31.82; Nov: 23.2; Dec: 16; Feb: 80%; Mar: 7
LA | ALEXANDRIA ESLER REGIONAL AP | Jan: 49.6; Feb: 52.3; Mar: 59.4; Apr: 66.5; May: 74.2; Jun: 80; Jul: 82.5; Aug: 82.4; Sep: 77; Oct: 66.5; Nov: 56.7; Dec: 50.1; Jan: 41.5; Feb: 48.56; Mar: 50.5; Apr: 52.7; May: 64.4; Jun: 71.24; Jul: 71.96; Aug: 74.48; Sep: 65.3; Oct: 61.88; Nov: 47.7; Dec: 40.6; Feb: 90%; Mar: 8
MN | ALEXANDRIA MUNICIPAL AP | Jan: 10.9; Feb: 15.4; Mar: 27.5; Apr: 42.9; May: 55.9; Jun: 65.5; Jul: 70.4; Aug: 68.5; Sep: 59.7; Oct: 46; Nov: 30.1; Dec: 16.5; Jan: 8.1; Feb: 6.8; Mar: 18; Apr: 34.52; May: 43.9; Jun: 54.5; Jul: 60.62; Aug: 59.72; Sep: 54.3; Oct: 33.98; Nov: 26.1; Dec: -2.4
IA | ALGONA | Jan: 18.2; Feb: 22.5; Mar: 33.9; Apr: 47.6; May: 59.7; Jun: 69.8; Jul: 73.2; Aug: 71; Sep: 62.9; Oct: 50.4; Nov: 36.4; Dec: 23.1; Jan: 11.5; Feb: 8.06; Mar: 29.7; Apr: 31.1; May: 44.2; Jun: 57.56; Jul: 64.04; Aug: 61.16; Sep: 52; Oct: 39.92; Nov: 21.7; Dec: 23.2
TX | ALICE INTL AP | Jan: 58.2; Feb: 61.4; Mar: 67.2; Apr: 73.8; May: 79.7; Jun: 84.2; Jul: 85.6; Aug: 86.1; Sep: 81.6; Oct: 74.8; Nov: 65.6; Dec: 59.2; Jan: 50.5; Feb: 46.04; Mar: 52.5; Apr: 66.38; May: 72; Jun: 70.88; Jul: 71.96; Aug: 72.86; Sep: 66; Oct: 63.14; Nov: 54.5; Dec: 50.7
PA | ALLENTOWN LEHIGH VALLEY INTL | Jan: 29.7; Feb: 31.6; Mar: 40.1; Apr: 51.1; May: 60.9; Jun: 70; Jul: 74.4; Aug: 72.5; Sep: 65; Oct: 53.7; Nov: 43.3; Dec: 34.1; Jan: 15.3; Feb: 19.4; Mar: 26.8; Apr: 35.24; May: 48.9; Jun: 55.76; Jul: 63.32; Aug: 60.98; Sep: 52.5; Oct: 39.56; Nov: 32.7; Dec: 25.5
NE | ALLIANCE MUNICIPAL | Jan: 25.6; Feb: 27.3; Mar: 36.9; Apr: 44.5; May: 54.6; Jun: 65.7; Jul: 73.8; Aug: 71.3; Sep: 60.9; Oct: 46.5; Nov: 34.5; Dec: 24.8; Jan: 12.2; Feb: 10.58; Mar: 26.8; Apr: 32; May: 40.3; Jun: 49.28; Jul: 54.86; Aug: 54.32; Sep: 47.1; Oct: 33.44; Nov: 21.4; Dec: 13.5
GA | ALMA BACON COUNTY AP | Jan: 50.5; Feb: 53; Mar: 59.5; Apr: 66.3; May: 73.7; Jun: 79.8; Jul: 81.6; Aug: 81.6; Sep: 77.3; Oct: 68; Nov: 58.3; Dec: 52.4; Jan: 38.5; Feb: 42.8; Mar: 41.7; Apr: 55.4; May: 63; Jun: 69.26; Jul: 72.68; Aug: 73.4; Sep: 66.2; Oct: 52.88; Nov: 49.1; Dec: 37.6
MI | ALPENA COUNTY REGIONAL AP | Jan: 20; Feb: 20.7; Mar: 29.2; Apr: 41.4; May: 52.9; Jun: 63; Jul: 67.4; Aug: 66; Sep: 58.2; Oct: 47; Nov: 36.2; Dec: 26; Jan: 13.5; Feb: 13.1; Mar: 24.4; Apr: 31.82; May: 39.2; Jun: 48.74; Jul: 55.76; Aug: 57.38; Sep: 53.2; Oct: 37.22; Nov: 25.7; Dec: 19.4
PA | ALTOONA BLAIR CO ARPT | Jan: 28.3; Feb: 30.2; Mar: 38.6; Apr: 50.2; May: 59.5; Jun: 67.9; Jul: 71.6; Aug: 69.9; Sep: 62.8; Oct: 52.3; Nov: 42.1; Dec: 32.4; Jan: 19.9; Feb: 20.84; Mar: 33.1; Apr: 37.58; May: 46.4; Jun: 55.94; Jul: 63.5; Aug: 59.18; Sep: 55.2; Oct: 44.78; Nov: 34.9; Dec: 21.4
CA | ALTURAS | Jan: 31.1; Feb: 33.9; Mar: 38.7; Apr: 43.3; May: 51.8; Jun: 59.9; Jul: 68.4; Aug: 65.5; Sep: 58.5; Oct: 47.4; Nov: 37.7; Dec: 30.8; Jan: 26.1; Feb: 25.52; Mar: 30.2; Apr: 30.38; May: 32; Jun: 37.04; Jul: 41.18; Aug: 36.5; Sep: 41.5; Oct: 29.48; Nov: 29.5; Dec: 24.1
OK | ALTUS AFB | Jan: 40.6; Feb: 45.7; Mar: 53.7; Apr: 61.5; May: 71.7; Jun: 80.9; Jul: 84; Aug: 83.2; Sep: 75; Oct: 63.4; Nov: 51; Dec: 41.3; Jan: 27.7; Feb: 33.26; Mar: 37.4; Apr: 34.34; May: 58.8; Jun: 60.8; Jul: 64.94; Aug: 59.9; Sep: 54.7; Oct: 44.42; Nov: 34.5; Dec: 28.2
TX | AMARILLO INTERNATIONAL AP [CANYON - UT] | Jan: 37.9; Feb: 40.9; Mar: 48.6; Apr: 56.7; May: 66.2; Jun: 75.4; Jul: 78.4; Aug: 77.2; Sep: 69.8; Oct: 58.6; Nov: 46.6; Dec: 37.9; Jan: 20.3; Feb: 24.08; Mar: 28; Apr: 36.86; May: 45.7; Jun: 59.18; Jul: 59.72; Aug: 60.62; Sep: 52; Oct: 40.82; Nov: 27.5; Dec: 20.7
AK | AMBLER | Jan: -3; Feb: 3.1; Mar: 5.4; Apr: 20.9; May: 39.2; Jun: 56.3; Jul: 58.2; Aug: 52.2; Sep: 41.1; Oct: 21.9; Nov: 7; Dec: 1.1; Jan: -15.2; Feb: -3.46; Mar: 6.8; Apr: 15.08; May: 28; Jun: 35.24; Jul: 43.7; Aug: 36.32; Sep: 29.1; Oct: 25.16; Nov: 2.5; Dec: -0.8
AK | ANAKTUVUK PASS | Jan: -8.4; Feb: -6.2; Mar: -4.1; Apr: 10.5; May: 31.6; Jun: 50; Jul: 52.7; Aug: 45.6; Sep: 34.2; Oct: 12.7; Nov: -0.7; Dec: -7; Jan: -14.8; Feb: -11.56; Mar: -4.9; Apr: 7.88; May: 27.9; Jun: 33.98; Jul: 37.94; Aug: 29.12; Sep: 30; Oct: 15.8; Nov: -0.4; Dec: -7.1
AK | ANCHORAGE INTL AP | Jan: 17; Feb: 20.8; Mar: 25.7; Apr: 37.3; May: 48; Jun: 55.6; Jul: 59; Aug: 57.1; Sep: 49; Oct: 35.6; Nov: 22.8; Dec: 18.7; Jan: 10.9; Feb: 11.48; Mar: 13.5; Apr: 25.88; May: 36; Jun: 43.88; Jul: 48.74; Aug: 47.3; Sep: 42.6; Oct: 26.6; Nov: 16.5; Dec: 15.1
AK | ANCHORAGE MERRILL FIELD | Jan: 15.9; Feb: 20.1; Mar: 25.8; Apr: 38.6; May: 49.7; Jun: 57.5; Jul: 60.6; Aug: 58.2; Sep: 49.6; Oct: 35.8; Nov: 22.2; Dec: 17.7; Jan: 23; Feb: 15.26; Mar: 20.7; Apr: 26.24; May: 32.2; Jun: 41.9; Jul: 48.74; Aug: 50.36; Sep: 35.2; Oct: 30.02; Nov: 30.2; Dec: 20.1
AK | ANCHORAGE/ELMENDORF | Jan: 14.6; Feb: 18.8; Mar: 25.3; Apr: 37.6; May: 48.9; Jun: 56.8; Jul: 59.9; Aug: 57.6; Sep: 48.8; Oct: 34.5; Nov: 21.1; Dec: 15.9; Jan: 24.1; Feb: 27.86; Mar: 20.3; Apr: 27.68; May: 32.4; Jun: 39.56; Jul: 51.26; Aug: 49.1; Sep: 33.4; Oct: 26.06; Nov: 31.3; Dec: 20.5
SC | ANDERSON COUNTY AP | Jan: 43.3; Feb: 46.4; Mar: 53.2; Apr: 61.2; May: 69.2; Jun: 76.6; Jul: 79.8; Aug: 78.9; Sep: 72.7; Oct: 62; Nov: 51.9; Dec: 45.1; Jan: 26.6; Feb: 30.38; Mar: 32.7; Apr: 42.98; May: 52.9; Jun: 64.76; Jul: 69.62; Aug: 70.34; Sep: 60.8; Oct: 46.04; Nov: 45.7; Dec: 30.2
MD | ANDREWS AFB | Jan: 35; Feb: 37.6; Mar: 45.4; Apr: 55.6; May: 64.3; Jun: 73; Jul: 77.6; Aug: 75.3; Sep: 68.4; Oct: 57.4; Nov: 47.4; Dec: 39; Jan: 24.6; Feb: 24.8; Mar: 27.9; Apr: 36.14; May: 49.8; Jun: 60.62; Jul: 66.92; Aug: 63.86; Sep: 55.8; Oct: 43.7; Nov: 33.4; Dec: 31.5
AK | ANIAK AIRPORT | Jan: 5; Feb: 13.5; Mar: 13.7; Apr: 30.4; May: 44.7; Jun: 53.9; Jul: 56.6; Aug: 53.3; Sep: 45.2; Oct: 30.5; Nov: 15.3; Dec: 7.8; Jan: 0.9; Feb: 20.3; Mar: 13.6; Apr: 18.5; May: 28; Jun: 35.96; Jul: 43.16; Aug: 41; Sep: 28.2; Oct: 25.16; Nov: 20.5; Dec: 9.1
MI | ANN ARBOR MUNICIPAL | Jan: 23.2; Feb: 24.8; Mar: 35.3; Apr: 48; May: 57.8; Jun: 66.9; Jul: 70.6; Aug: 69; Sep: 61.2; Oct: 49.8; Nov: 39.5; Dec: 28.6; Jan: 14.9; Feb: 15.62; Mar: 30.6; Apr: 37.94; May: 43; Jun: 58.46; Jul: 62.06; Aug: 62.24; Sep: 52.7; Oct: 42.8; Nov: 37.9; Dec: 26.8
AK | ANNETTE ISLAND AP | Jan: 36.9; Feb: 37.4; Mar: 38.6; Apr: 43.7; May: 49.8; Jun: 55.2; Jul: 58.1; Aug: 58.8; Sep: 53.8; Oct: 46.9; Nov: 40.3; Dec: 37.2; Jan: 30.7; Feb: 32.9; Mar: 29.1; Apr: 36.32; May: 41.5; Jun: 46.4; Jul: 50.54; Aug: 51.62; Sep: 49.8; Oct: 42.62; Nov: 36.7; Dec: 32.7
AL | ANNISTON METROPOLITAN AP | Jan: 44.4; Feb: 47.9; Mar: 55; Apr: 62.4; May: 70.2; Jun: 77.1; Jul: 80; Aug: 79.7; Sep: 74; Oct: 63.2; Nov: 52.9; Dec: 46.5; Jan: 39.6; Feb: 42.08; Mar: 41.5; Apr: 55.4; May: 65.3; Jun: 64.22; Jul: 71.24; Aug: 67.28; Sep: 62.4; Oct: 47.66; Nov: 45.1; Dec: 35.8
AK | ANVIK | Jan: 4.2; Feb: 11.1; Mar: 13; Apr: 28.8; May: 44.2; Jun: 54.5; Jul: 56.5; Aug: 52.4; Sep: 45; Oct: 29.2; Nov: 12.9; Dec: 5.4; Jan: -0.6; Feb: 12.2; Mar: 9.1; Apr: 21.56; May: 27.5; Jun: 30.74; Jul: 37.04; Aug: 33.44; Sep: 26.6; Oct: 27.68; Nov: 16.7; Dec: 10.4
WI | APPLETON/OUTAGAMIE | Jan: 19.1; Feb: 24.7; Mar: 32.7; Apr: 46.4; May: 56.3; Jun: 66.9; Jul: 71.8; Aug: 69.4; Sep: 62.7; Oct: 49.7; Nov: 37; Dec: 24.9; Jan: 19.4; Feb: 28.04; Mar: 24.6; Apr: 30.38; May: 39.7; Jun: 58.28; Jul: 59.72; Aug: 60.26; Sep: 50.5; Oct: 40.1; Nov: 29.3; Dec: 23.9
CA | ARCATA AIRPORT | Jan: 47.6; Feb: 48; Mar: 48.4; Apr: 49.4; May: 52.3; Jun: 54.9; Jul: 56.7; Aug: 57.2; Sep: 56.1; Oct: 53.6; Nov: 50.1; Dec: 47.1; Jan: 41.2; Feb: 37.76; Mar: 43.9; Apr: 44.24; May: 46.4; Jun: 49.46; Jul: 51.8; Aug: 52.7; Sep: 50.5; Oct: 48.56; Nov: 45.7; Dec: 40.6
NC | ASHEVILLE REGIONAL ARPT | Jan: 38.1; Feb: 40.9; Mar: 47.3; Apr: 55.9; May: 63.5; Jun: 70.5; Jul: 73.7; Aug: 72.8; Sep: 66.7; Oct: 56.5; Nov: 46.9; Dec: 40.3; Jan: 25.7; Feb: 28.76; Mar: 32.9; Apr: 42.8; May: 53.6; Jun: 62.96; Jul: 63.68; Aug: 65.84; Sep: 60.1; Oct: 47.12; Nov: 35.6; Dec: 25.7
CO | ASPEN PITKIN CO SAR | Jan: 20.4; Feb: 23; Mar: 32.2; Apr: 40.3; May: 48.9; Jun: 58.2; Jul: 64.8; Aug: 61.8; Sep: 54.7; Oct: 43.2; Nov: 31.2; Dec: 20.7; Jan: 14.9; Feb: 13.28; Mar: 21.9; Apr: 22.1; May: 22.6; Jun: 33.26; Jul: 43.52; Aug: 35.06; Sep: 32.7; Oct: 20.3; Nov: 18.1; Dec: 12.6
OR | ASTORIA REGIONAL AIRPORT | Jan: 43.8; Feb: 44.4; Mar: 46.2; Apr: 48.7; May: 53.1; Jun: 57.1; Jul: 60.5; Aug: 61.1; Sep: 59; Oct: 52.8; Nov: 47.1; Dec: 43.1; Jan: 37.6; Feb: 39.92; Mar: 41.4; Apr: 42.44; May: 46.2; Jun: 49.82; Jul: 54.14; Aug: 55.4; Sep: 52.2; Oct: 47.84; Nov: 42.4; Dec: 39
GA | ATHENS BEN EPPS AP | Jan: 44.1; Feb: 47.3; Mar: 54.2; Apr: 61.8; May: 69.7; Jun: 76.9; Jul: 80.1; Aug: 79.1; Sep: 73.1; Oct: 62.7; Nov: 52.8; Dec: 45.9; Jan: 26.2; Feb: 35.6; Mar: 38.1; Apr: 47.48; May: 56.7; Jun: 65.66; Jul: 67.46; Aug: 69.98; Sep: 63.5; Oct: 50; Nov: 45.1; Dec: 32.9
GA | ATLANTA HARTSFIELD INTL AP | Jan: 44.5; Feb: 48; Mar: 54.9; Apr: 62.6; May: 70.5; Jun: 77.3; Jul: 80.1; Aug: 79.5; Sep: 73.9; Oct: 63.6; Nov: 53.5; Dec: 46.4; Jan: 26.6; Feb: 29.66; Mar: 38.8; Apr: 47.84; May: 56.7; Jun: 61.7; Jul: 67.64; Aug: 69.26; Sep: 62.2; Oct: 51.44; Nov: 39.6; Dec: 32.5
IA | ATLANTIC | Jan: 22.8; Feb: 27; Mar: 38.3; Apr: 50.5; May: 61.8; Jun: 71.7; Jul: 75.5; Aug: 72.4; Sep: 64.1; Oct: 51.9; Nov: 38.1; Dec: 26.1; Jan: 19; Feb: 12.02; Mar: 27; Apr: 42.26; May: 52.9; Jun: 61.34; Jul: 66.2; Aug: 66.74; Sep: 54.1; Oct: 43.7; Nov: 26.8; Dec: 16.3
NJ | ATLANTIC CITY INTL AP | Jan: 34.2; Feb: 35.6; Mar: 42.3; Apr: 52; May: 61.1; Jun: 70.7; Jul: 76.1; Aug: 74.2; Sep: 67.2; Oct: 56.5; Nov: 46.5; Dec: 38.4; Jan: 19.2; Feb: 24.98; Mar: 30.7; Apr: 41; May: 50.9; Jun: 60.26; Jul: 65.84; Aug: 64.76; Sep: 57; Oct: 44.96; Nov: 38.1; Dec: 28.8
ME | AUBURN-LEWISTON | Jan: 19.6; Feb: 22.6; Mar: 31.8; Apr: 43.3; May: 53.6; Jun: 63.3; Jul: 68.3; Aug: 66.7; Sep: 59.1; Oct: 47.3; Nov: 37.1; Dec: 26.8; Jan: 17.1; Feb: 10.58; Mar: 25.3; Apr: 28.04; May: 37.2; Jun: 47.66; Jul: 57.2; Aug: 51.98; Sep: 47.1; Oct: 35.24; Nov: 26.8; Dec: 18.7
AL | AUBURN-OPELIKA APT | Jan: 46.3; Feb: 49.3; Mar: 55.8; Apr: 62.8; May: 71.1; Jun: 77.3; Jul: 79.7; Aug: 79.3; Sep: 74.1; Oct: 64.5; Nov: 55; Dec: 47.5; Jan: 28.9; Feb: 34.88; Mar: 36.3; Apr: 43.7; May: 55; Jun: 68.54; Jul: 69.08; Aug: 67.28; Sep: 62.4; Oct: 46.04; Nov: 43; Dec: 36.1
ME | AUGUSTA AIRPORT | Jan: 20.4; Feb: 23.1; Mar: 32.2; Apr: 44.1; May: 55; Jun: 64.4; Jul: 69.9; Aug: 68.6; Sep: 60.5; Oct: 49.2; Nov: 38.3; Dec: 27.3; Jan: 0.1; Feb: 4.1; Mar: 25.7; Apr: 32.54; May: 43; Jun: 53.96; Jul: 57.92; Aug: 59.9; Sep: 57; Oct: 43.34; Nov: 31.6; Dec: 16.7
GA | AUGUSTA BUSH FIELD | Jan: 46.5; Feb: 49.5; Mar: 56.3; Apr: 63.4; May: 71.3; Jun: 78.3; Jul: 81.3; Aug: 80.4; Sep: 74.8; Oct: 64.4; Nov: 54.5; Dec: 48; Jan: 35.2; Feb: 33.44; Mar: 42.3; Apr: 49.28; May: 58.6; Jun: 66.74; Jul: 68.36; Aug: 69.44; Sep: 65.8; Oct: 51.44; Nov: 48; Dec: 34.9
CO | AURORA BUCKLEY FIELD ANGB | Jan: 32.4; Feb: 34.6; Mar: 41.2; Apr: 47.6; May: 57.5; Jun: 66.8; Jul: 73.2; Aug: 71.2; Sep: 63.4; Oct: 51.3; Nov: 38.6; Dec: 33; Jan: 23.9; Feb: 21.02; Mar: 22.1; Apr: 28.4; May: 35.2; Jun: 41.18; Jul: 43.52; Aug: 43.16; Sep: 34.3; Oct: 27.14; Nov: 26.8; Dec: 14.9
IL | AURORA MUNICIPAL | Jan: 22.5; Feb: 25.1; Mar: 37.6; Apr: 49.4; May: 60; Jun: 69.3; Jul: 72.7; Aug: 70.4; Sep: 63; Oct: 51.3; Nov: 39.5; Dec: 27; Jan: 16.9; Feb: 20.3; Mar: 32.7; Apr: 42.62; May: 48; Jun: 58.82; Jul: 61.16; Aug: 62.6; Sep: 57.4; Oct: 38.66; Nov: 34; Dec: 9.7
OR | AURORA STATE | Jan: 41.6; Feb: 43.8; Mar: 47; Apr: 50.9; May: 57.1; Jun: 62; Jul: 68.7; Aug: 68.8; Sep: 64.1; Oct: 54.1; Nov: 46.2; Dec: 40.8; Jan: 37; Feb: 35.96; Mar: 43.2; Apr: 41.18; May: 43.9; Jun: 50.36; Jul: 53.42; Aug: 56.3; Sep: 47.1; Oct: 47.66; Nov: 44.4; Dec: 37.6
TX | AUSTIN MUELLER MUNICIPAL AP [UT] | Jan: 51.2; Feb: 55; Mar: 61.1; Apr: 68.7; May: 76.1; Jun: 82.2; Jul: 84.1; Aug: 84.9; Sep: 79.2; Oct: 70.1; Nov: 59.5; Dec: 52.1; Jan: 41; Feb: 42.08; Mar: 50.2; Apr: 61.34; May: 64.8; Jun: 69.98; Jul: 70.88; Aug: 70.34; Sep: 62.6; Oct: 64.76; Nov: 52.9; Dec: 42.6
MN | AUSTIN MUNI | Jan: 15.3; Feb: 19.5; Mar: 31.9; Apr: 46; May: 57.8; Jun: 67.8; Jul: 71.9; Aug: 69.2; Sep: 60.8; Oct: 48.9; Nov: 34.5; Dec: 21.3; Jan: 19.8; Feb: 8.06; Mar: 29.7; Apr: 41.54; May: 41; Jun: 54.86; Jul: 62.24; Aug: 67.64; Sep: 53.1; Oct: 35.42; Nov: 23.4; Dec: 7.2
OR | BAKER MUNICIPAL AP | Jan: 26.9; Feb: 31.4; Mar: 38.9; Apr: 44.1; May: 52; Jun: 58.5; Jul: 66.9; Aug: 65.9; Sep: 57.8; Oct: 45.3; Nov: 34.2; Dec: 26.7; Jan: 24.3; Feb: 21.38; Mar: 25.5; Apr: 29.66; May: 32.5; Jun: 44.06; Jul: 47.48; Aug: 45.86; Sep: 41; Oct: 32.72; Nov: 23.4; Dec: 26.1
CA | BAKERSFIELD MEADOWS FIELD | Jan: 48.9; Feb: 53.3; Mar: 58.2; Apr: 62.6; May: 70.7; Jun: 77.7; Jul: 84.1; Aug: 82.7; Sep: 77.8; Oct: 67.5; Nov: 55.9; Dec: 48.5; Jan: 39.7; Feb: 40.46; Mar: 40.5; Apr: 42.62; May: 43.7; Jun: 48.2; Jul: 55.76; Aug: 55.58; Sep: 52.9; Oct: 48.2; Nov: 40.6; Dec: 41.5
BC | BALLENAS ISLAND | Jan: 42.3; Feb: 42.6; Mar: 45.2; Apr: 49.1; May: 55.3; Jun: 60.2; Jul: 64.8; Aug: 64.9; Sep: 60; Oct: 52.4; Nov: 45.8; Dec: 43; Jan: 34.7; Feb: 33.8; Mar: 36.1; Apr: 39.2; May: 44.6; Jun: 49.28; Jul: 53.78; Aug: 53.78; Sep: 50.2; Oct: 44.42; Nov: 38.8; Dec: 34
MD | BALTIMORE BLT-WASHNGTN INT | Jan: 34.7; Feb: 36.6; Mar: 44.4; Apr: 54.9; May: 64; Jun: 73.3; Jul: 77.9; Aug: 75.8; Sep: 68.6; Oct: 57.2; Nov: 47; Dec: 38.4; Jan: 20.3; Feb: 22.64; Mar: 26.1; Apr: 40.1; May: 52.3; Jun: 59.72; Jul: 65.12; Aug: 63.5; Sep: 61.2; Oct: 41.54; Nov: 37; Dec: 20.8
ME | BANGOR INTERNATIONAL AP | Jan: 18.5; Feb: 21.1; Mar: 30.9; Apr: 43; May: 54.3; Jun: 63.8; Jul: 69.3; Aug: 67.9; Sep: 59.6; Oct: 48.3; Nov: 37.3; Dec: 26; Jan: 10.9; Feb: 8.24; Mar: 21.7; Apr: 29.84; May: 38.5; Jun: 50; Jul: 61.16; Aug: 58.64; Sep: 48.2; Oct: 37.04; Nov: 26.4; Dec: 18.9
ME | BAR HARBOR (AWOS) | Jan: 21.2; Feb: 23.8; Mar: 31.8; Apr: 41.9; May: 51.3; Jun: 60.1; Jul: 66.2; Aug: 65.4; Sep: 58.6; Oct: 48.1; Nov: 38.3; Dec: 28.7; Jan: 18.7; Feb: 15.62; Mar: 21.6; Apr: 26.06; May: 25.5; Jun: 47.48; Jul: 52.88; Aug: 54.32; Sep: 46.6; Oct: 37.04; Nov: 29.7; Dec: 27.1
HI | BARBERS POINT NAS | Jan: 72.7; Feb: 72.7; Mar: 73.5; Apr: 75; May: 76.4; Jun: 78.7; Jul: 79.9; Aug: 80.4; Sep: 79.9; Oct: 78.6; Nov: 76.4; Dec: 74.2; Jan: 59.9; Feb: 58.64; Mar: 63.7; Apr: 59.9; May: 62.4; Jun: 62.96; Jul: 63.32; Aug: 68.18; Sep: 69.4; Oct: 69.08; Nov: 66.6; Dec: 63.7
LA | BARKSDALE AFB | Jan: 46.9; Feb: 51.4; Mar: 57.7; Apr: 64.7; May: 72.8; Jun: 80.2; Jul: 82.7; Aug: 82.7; Sep: 76.5; Oct: 65.7; Nov: 55; Dec: 49; Jan: 34.2; Feb: 37.04; Mar: 36.3; Apr: 48.92; May: 67.5; Jun: 70.34; Jul: 71.24; Aug: 69.62; Sep: 60.6; Oct: 51.98; Nov: 44.4; Dec: 41.4
MA | BARNSTABLE MUNI BOA | Jan: 30.7; Feb: 32; Mar: 37.6; Apr: 46.1; May: 55.5; Jun: 64.7; Jul: 71.5; Aug: 70.2; Sep: 63.4; Oct: 53.3; Nov: 44.5; Dec: 36.2; Jan: 28.2; Feb: 19.4; Mar: 32; Apr: 38.48; May: 45.1; Jun: 56.48; Jul: 62.96; Aug: 63.68; Sep: 54; Oct: 50.18; Nov: 37.4; Dec: 27.9
AK | BARROW W POST-W ROGERS ARPT [NSA - ARM] | Jan: -13.2; Feb: -13.7; Mar: -11.9; Apr: 3.5; May: 22.2; Jun: 35.8; Jul: 41.1; Aug: 39.6; Sep: 33.3; Oct: 19.9; Nov: 3.7; Dec: -7.5; Jan: -15.7; Feb: -20.02; Mar: -15.3; Apr: -6.52; May: 17.4; Jun: 30.38; Jul: 35.42; Aug: 35.42; Sep: 27.9; Oct: 13.64; Nov: -9.9; Dec: -13.7
OK | BARTLESVILLE-PHILLIPS FIELD | Jan: 36; Feb: 39; Mar: 50; Apr: 59; May: 68; Jun: 76; Jul: 81; Aug: 80; Sep: 72; Oct: 60; Nov: 48; Dec: 38; Jan: 26.1; Feb: 25.16; Mar: 33.1; Apr: 51.8; May: 60.3; Jun: 66.74; Jul: 63.86; Aug: 60.26; Sep: 52.7; Oct: 46.22; Nov: 32.2; Dec: 22.3
AR | BATESVILLE (AWOS) | Jan: 39.4; Feb: 42.8; Mar: 51.1; Apr: 60.7; May: 68.9; Jun: 77.1; Jul: 80.7; Aug: 80; Sep: 72.1; Oct: 61.4; Nov: 50.4; Dec: 41.5; Jan: 33.6; Feb: 26.6; Mar: 29.5; Apr: 39.92; May: 53.1; Jun: 65.12; Jul: 65.66; Aug: 61.16; Sep: 63; Oct: 46.22; Nov: 35.6; Dec: 32.9
LA | BATON ROUGE RYAN ARPT | Jan: 52.1; Feb: 55.3; Mar: 61.3; Apr: 67.8; May: 75.2; Jun: 80.8; Jul: 82.3; Aug: 82.4; Sep: 78.2; Oct: 68.8; Nov: 59.1; Dec: 53.4; Jan: 42.4; Feb: 42.26; Mar: 53.6; Apr: 57.56; May: 66; Jun: 67.46; Jul: 73.04; Aug: 71.24; Sep: 66.4; Oct: 58.46; Nov: 52.5; Dec: 41.4
MI | BATTLE CREEK KELLOGG AP | Jan: 24; Feb: 26; Mar: 36.4; Apr: 48.9; May: 59.8; Jun: 68.8; Jul: 72.5; Aug: 70.7; Sep: 63.3; Oct: 51.4; Nov: 40.7; Dec: 29.3; Jan: 18; Feb: 23.18; Mar: 31.1; Apr: 40.46; May: 41; Jun: 57.74; Jul: 58.28; Aug: 62.6; Sep: 54.3; Oct: 41.36; Nov: 34.2; Dec: 20.1
MN | BAUDETTE INTERNATIONAL AP | Jan: 5.6; Feb: 11.3; Mar: 23.3; Apr: 39.6; May: 51.8; Jun: 62.1; Jul: 67.2; Aug: 65; Sep: 56.1; Oct: 42.9; Nov: 26.8; Dec: 11.5; Jan: 9.7; Feb: 10.4; Mar: 18.5; Apr: 30.2; May: 43; Jun: 53.96; Jul: 55.4; Aug: 56.84; Sep: 47.8; Oct: 33.26; Nov: 23.4; Dec: 14
CA | BEALE AFB | Jan: 47.5; Feb: 51.7; Mar: 55.4; Apr: 60.1; May: 66.8; Jun: 73.3; Jul: 78.5; Aug: 77.4; Sep: 74.3; Oct: 64.8; Nov: 54.6; Dec: 46.9; Jan: 36; Feb: 40.1; Mar: 43.5; Apr: 42.98; May: 47.8; Jun: 46.94; Jul: 53.78; Aug: 54.86; Sep: 52; Oct: 42.98; Nov: 37.2; Dec: 39
NE | BEATRICE MUNICIPAL | Jan: 26; Feb: 30.7; Mar: 41.1; Apr: 52.2; May: 63.1; Jun: 72.8; Jul: 78; Aug: 75.7; Sep: 66.5; Oct: 54.4; Nov: 40.7; Dec: 28.8; Jan: 19.6; Feb: 18.5; Mar: 33.8; Apr: 42.26; May: 45.1; Jun: 56.12; Jul: 62.42; Aug: 64.4; Sep: 55.2; Oct: 42.44; Nov: 30.4; Dec: 25.7
SC | BEAUFORT MCAS | Jan: 50.2; Feb: 53; Mar: 59; Apr: 66.2; May: 73.8; Jun: 79.9; Jul: 82.8; Aug: 81.7; Sep: 77.1; Oct: 68.1; Nov: 58.6; Dec: 52.6; Jan: 34.7; Feb: 41; Mar: 42.8; Apr: 53.24; May: 57.2; Jun: 69.8; Jul: 73.76; Aug: 71.42; Sep: 66; Oct: 54.32; Nov: 51.6; Dec: 37.6
ON | BEAUSOLEIL | Jan: 17.5; Feb: 18.7; Mar: 27.7; Apr: 41; May: 53.1; Jun: 63.8; Jul: 68.7; Aug: 67.6; Sep: 60.9; Oct: 48.2; Nov: 37.4; Dec: 26.3; Jan: 12.9; Feb: 13.28; Mar: 20.3; Apr: 31.1; May: 42.6; Jun: 54.5; Jul: 58.64; Aug: 58.64; Sep: 52.9; Oct: 41.54; Nov: 32.5; Dec: 19.2
WV | BECKLEY RALEIGH CO MEM AP | Jan: 32.3; Feb: 34.8; Mar: 42.2; Apr: 53; May: 60.3; Jun: 67.6; Jul: 70.7; Aug: 69.8; Sep: 63.5; Oct: 53.5; Nov: 43.6; Dec: 35.4; Jan: 27.5; Feb: 26.6; Mar: 33.1; Apr: 41.18; May: 47.8; Jun: 59.9; Jul: 64.22; Aug: 62.96; Sep: 55.6; Oct: 40.82; Nov: 32.2; Dec: 17.6
IL | BELLEVILLE SCOTT AFB | Jan: 31.4; Feb: 37.1; Mar: 45.9; Apr: 56.3; May: 65.9; Jun: 74.7; Jul: 78.2; Aug: 77; Sep: 68.7; Oct: 57.7; Nov: 45.4; Dec: 35.2; Jan: 27; Feb: 26.42; Mar: 27; Apr: 37.22; May: 45.5; Jun: 65.48; Jul: 66.2; Aug: 65.12; Sep: 53.6; Oct: 41.9; Nov: 33.3; Dec: 26.8
NE | BELLEVUE OFFUTT AFB | Jan: 23.9; Feb: 29.7; Mar: 40.5; Apr: 51.9; May: 63; Jun: 72.5; Jul: 77; Aug: 75.1; Sep: 66.3; Oct: 54.1; Nov: 39.5; Dec: 27.8; Jan: 14.5; Feb: 30.92; Mar: 31.3; Apr: 36.14; May: 46.8; Jun: 64.58; Jul: 63.68; Aug: 63.5; Sep: 52.5; Oct: 39.38; Nov: 27.5; Dec: 24.8
WA | BELLINGHAM INTL AP | Jan: 39.7; Feb: 41.4; Mar: 44.6; Apr: 48.9; May: 54.4; Jun: 58.9; Jul: 63.1; Aug: 63.2; Sep: 58.3; Oct: 50.5; Nov: 43.7; Dec: 39.1; Jan: 34.9; Feb: 32.72; Mar: 30.7; Apr: 42.08; May: 45.7; Jun: 50.72; Jul: 53.78; Aug: 54.32; Sep: 50.5; Oct: 42.44; Nov: 37.4; Dec: 36.9
NJ | BELMAR ASC | Jan: 32.6; Feb: 34.1; Mar: 41.3; Apr: 51.1; May: 60; Jun: 70.1; Jul: 75.3; Aug: 73; Sep: 66.7; Oct: 55; Nov: 46.4; Dec: 37.3; Jan: 16; Feb: 22.28; Mar: 24.1; Apr: 33.98; May: 45.7; Jun: 54.86; Jul: 61.34; Aug: 60.44; Sep: 53.4; Oct: 41.18; Nov: 34; Dec: 24.1
MN | BEMIDJI MUNICIPAL | Jan: 7.9; Feb: 12.5; Mar: 25.3; Apr: 39.8; May: 52.4; Jun: 62.7; Jul: 67.1; Aug: 65.5; Sep: 56.3; Oct: 43.4; Nov: 27.6; Dec: 13.8; Jan: 1.6; Feb: 10.4; Mar: 3.9; Apr: 30.2; May: 42.3; Jun: 48.38; Jul: 56.48; Aug: 55.94; Sep: 46.8; Oct: 32.54; Nov: 22.6; Dec: 5.4
MN | BENSON MUNI | Jan: 12.2; Feb: 16.2; Mar: 29.1; Apr: 44.6; May: 56.9; Jun: 66.9; Jul: 71.4; Aug: 68.4; Sep: 60.6; Oct: 47.2; Nov: 31.8; Dec: 17.8; Jan: 11.1; Feb: 16.16; Mar: 28.2; Apr: 32.72; May: 45.1; Jun: 51.98; Jul: 64.04; Aug: 56.84; Sep: 52.7; Oct: 40.64; Nov: 21; Dec: 8.4
MI | BENTON HARBOR/ROSS | Jan: 26.4; Feb: 28.6; Mar: 36.5; Apr: 47.4; May: 57.2; Jun: 66.5; Jul: 70.9; Aug: 69.1; Sep: 62.4; Oct: 51.9; Nov: 41.4; Dec: 31.3; Jan: 22.5; Feb: 24.98; Mar: 32.9; Apr: 39.74; May: 43.3; Jun: 57.38; Jul: 64.22; Aug: 64.94; Sep: 52.9; Oct: 45.86; Nov: 31.1; Dec: 14.9
AR | BENTONVILLE (AWOS) | Jan: 36.3; Feb: 40.2; Mar: 48.4; Apr: 57.2; May: 65.7; Jun: 74.3; Jul: 78.4; Aug: 77.9; Sep: 69.3; Oct: 58.8; Nov: 48.1; Dec: 38.8; Jan: 25.9; Feb: 33.98; Mar: 29.3; Apr: 43.7; May: 58.8; Jun: 62.06; Jul: 66.92; Aug: 66.2; Sep: 58.6; Oct: 47.12; Nov: 32.5; Dec: 23.9
NH | BERLIN MUNICIPAL | Jan: 14.2; Feb: 17.3; Mar: 26.5; Apr: 39.7; May: 51.4; Jun: 60.7; Jul: 64.9; Aug: 63.5; Sep: 56.2; Oct: 44.1; Nov: 33.5; Dec: 21.3; Jan: 8.1; Feb: 9.5; Mar: 12.2; Apr: 28.4; May: 36.1; Jun: 53.6; Jul: 55.4; Aug: 56.48; Sep: 50.9; Oct: 36.32; Nov: 27.5; Dec: 22.1
AK | BETHEL AIRPORT | Jan: 6.1; Feb: 11.5; Mar: 13.4; Apr: 28; May: 42.1; Jun: 52.6; Jul: 55.8; Aug: 53.6; Sep: 45.7; Oct: 30.9; Nov: 17.6; Dec: 9.1; Jan: 10.6; Feb: 7.34; Mar: 9.9; Apr: 24.08; May: 33.8; Jun: 44.24; Jul: 48.74; Aug: 49.1; Sep: 39.2; Oct: 27.5; Nov: 13.1; Dec: 8.4
AK | BETTLES FIELD | Jan: -11.2; Feb: -4.4; Mar: 3.1; Apr: 24.4; May: 45; Jun: 58.4; Jul: 59.4; Aug: 52.9; Sep: 41.6; Oct: 21; Nov: -0.2; Dec: -6.6; Jan: -14.3; Feb: -14.8; Mar: -4.2; Apr: 12.92; May: 30.4; Jun: 40.28; Jul: 47.48; Aug: 46.04; Sep: 30.9; Oct: 15.98; Nov: -1.3; Dec: -15.9
MA | BEVERLY MUNI | Jan: 26.9; Feb: 29.3; Mar: 36.4; Apr: 46.9; May: 55.9; Jun: 65.4; Jul: 71.3; Aug: 70.1; Sep: 63; Oct: 51.9; Nov: 42.8; Dec: 33.2; Jan: 4.6; Feb: 5.54; Mar: 29.1; Apr: 35.78; May: 45.5; Jun: 55.22; Jul: 58.28; Aug: 62.24; Sep: 50.4; Oct: 39.56; Nov: 33.6; Dec: 24.3
AK | BIG DELTA ALLEN AAF | Jan: -0.4; Feb: 6.3; Mar: 14.4; Apr: 33.3; May: 47.8; Jun: 58.1; Jul: 60.1; Aug: 55.6; Sep: 44.5; Oct: 26.1; Nov: 7; Dec: 2; Jan: -3.3; Feb: -3.46; Mar: -0.4; Apr: 16.34; May: 35.4; Jun: 46.58; Jul: 44.96; Aug: 37.94; Sep: 34.3; Oct: 17.24; Nov: -4.7; Dec: -2.4
AK | BIG RIVER LAKE | Jan: 22.5; Feb: 25.6; Mar: 26.5; Apr: 35.8; May: 45.2; Jun: 49.7; Jul: 53.9; Aug: 54.1; Sep: 49.2; Oct: 40.1; Nov: 28.7; Dec: 25.4; Jan: 18; Feb: 13.1; Mar: 21.6; Apr: 31.82; May: 33.3; Jun: 46.58; Jul: 50.54; Aug: 50.18; Sep: 35.6; Oct: 19.58; Nov: 14.5; Dec: 20.7
MT | BILLINGS LOGAN INT ARPT | Jan: 27.1; Feb: 30.2; Mar: 37.9; Apr: 45.7; May: 55.1; Jun: 64; Jul: 73.1; Aug: 71.7; Sep: 61.7; Oct: 48.3; Nov: 36.3; Dec: 27.2; Jan: 9.1; Feb: 13.82; Mar: 23.4; Apr: 30.38; May: 38.7; Jun: 43.7; Jul: 46.04; Aug: 44.96; Sep: 39.6; Oct: 27.14; Nov: 19.9; Dec: 16.3
NY | BINGHAMTON EDWIN A LINK FIELD | Jan: 23.3; Feb: 25; Mar: 33.1; Apr: 45.3; May: 56.3; Jun: 65; Jul: 68.9; Aug: 67.5; Sep: 59.9; Oct: 49.2; Nov: 38.6; Dec: 28.5; Jan: 14.9; Feb: 13.28; Mar: 24.1; Apr: 31.82; May: 45.3; Jun: 56.3; Jul: 57.56; Aug: 55.94; Sep: 49.6; Oct: 40.46; Nov: 31.5; Dec: 20.3
AK | BIRCHWOOD | Jan: 14.5; Feb: 19.7; Mar: 23.9; Apr: 37; May: 47.6; Jun: 55.5; Jul: 58.4; Aug: 55.9; Sep: 48.1; Oct: 34.6; Nov: 21.1; Dec: 15.9; Jan: 11.1; Feb: 24.98; Mar: 21.2; Apr: 28.04; May: 32.4; Jun: 39.38; Jul: 47.66; Aug: 41; Sep: 34.3; Oct: 23.72; Nov: 27.9; Dec: 19.8
AL | BIRMINGHAM MUNICIPAL AP | Jan: 44.6; Feb: 48.3; Mar: 55.4; Apr: 63.1; May: 70.9; Jun: 77.8; Jul: 80.8; Aug: 80.6; Sep: 74.8; Oct: 64; Nov: 53.7; Dec: 46.8; Jan: 31.8; Feb: 32.72; Mar: 39.6; Apr: 50; May: 57.6; Jun: 67.82; Jul: 71.42; Aug: 68.54; Sep: 63.3; Oct: 50.72; Nov: 46.8; Dec: 33.4
CA | BISHOP AIRPORT | Jan: 39.3; Feb: 42.1; Mar: 48.6; Apr: 54.3; May: 62.9; Jun: 71.5; Jul: 77.7; Aug: 75.3; Sep: 68.1; Oct: 56.9; Nov: 45.4; Dec: 37.8; Jan: 18.5; Feb: 29.66; Mar: 10.4; Apr: 18.86; May: 27.3; Jun: 31.82; Jul: 38.12; Aug: 39.2; Sep: 31.3; Oct: 28.4; Nov: 20.8; Dec: 26.6
ND | BISMARCK MUNICIPAL ARPT [ISIS] | Jan: 13.1; Feb: 18.2; Mar: 30; Apr: 43.4; May: 55.3; Jun: 64.9; Jul: 71; Aug: 69.9; Sep: 59.8; Oct: 45.2; Nov: 29.7; Dec: 17.4; Jan: 1.2; Feb: 13.82; Mar: 21.7; Apr: 30.2; May: 45.3; Jun: 50.54; Jul: 55.4; Aug: 53.24; Sep: 44.4; Oct: 32.54; Nov: 22.6; Dec: 9.9
UT | BLANDING MUNI AP | Jan: 30; Feb: 36; Mar: 44; Apr: 50; May: 58; Jun: 72; Jul: 74; Aug: 74; Sep: 65; Oct: 53; Nov: 41; Dec: 32; Jan: 28.2; Feb: 21.56; Mar: 26.8; Apr: 24.8; May: 29.7; Jun: 31.82; Jul: 31.82; Aug: 30.56; Sep: 30.7; Oct: 29.3; Nov: 26.4; Dec: 20.7
RI | BLOCK ISLAND STATE ARPT | Jan: 33.1; Feb: 33.7; Mar: 38.8; Apr: 46.8; May: 55.4; Jun: 64.9; Jul: 71.5; Aug: 70.6; Sep: 65.2; Oct: 55.9; Nov: 46.9; Dec: 38.7; Jan: 27.1; Feb: 24.26; Mar: 27.5; Apr: 35.42; May: 43.9; Jun: 57.56; Jul: 62.6; Aug: 64.04; Sep: 59.4; Oct: 45.14; Nov: 34; Dec: 28.6
CA | BLUE CANYON AP | Jan: 40; Feb: 38.5; Mar: 41.2; Apr: 44.3; May: 52.6; Jun: 60.9; Jul: 69.6; Aug: 68.7; Sep: 64.5; Oct: 54.7; Nov: 44.7; Dec: 38.6; Jan: 23.4; Feb: 21.2; Mar: 31.1; Apr: 28.4; May: 32.9; Jun: 38.84; Jul: 40.64; Aug: 40.82; Sep: 50.7; Oct: 29.12; Nov: 28; Dec: 19
WV | BLUEFIELD/MERCER CO [NREL] | Jan: 34.4; Feb: 36.4; Mar: 44.4; Apr: 55.3; May: 62.3; Jun: 69.3; Jul: 72.3; Aug: 71.5; Sep: 65.4; Oct: 55.3; Nov: 45.7; Dec: 37; Jan: 19.4; Feb: 27.86; Mar: 31.1; Apr: 34.7; May: 47.7; Jun: 59.9; Jul: 63.14; Aug: 62.78; Sep: 52.5; Oct: 47.66; Nov: 30.7; Dec: 28.2
CA | BLYTHE RIVERSIDE CO ARPT | Jan: 55.7; Feb: 59; Mar: 65.4; Apr: 71.9; May: 80.8; Jun: 88.8; Jul: 94.7; Aug: 94.1; Sep: 87.9; Oct: 75.3; Nov: 63; Dec: 54.1; Jan: 24.3; Feb: 32.18; Mar: 35.2; Apr: 31.28; May: 37.9; Jun: 39.2; Jul: 49.46; Aug: 59.9; Sep: 54.1; Oct: 42.26; Nov: 28.2; Dec: 18
ID | BOISE AIR TERMINAL [UO] | Jan: 31.9; Feb: 37.1; Mar: 44.7; Apr: 50.5; May: 59.1; Jun: 67.1; Jul: 77; Aug: 75.4; Sep: 66.4; Oct: 52.9; Nov: 40; Dec: 31.8; Jan: 24.1; Feb: 28.04; Mar: 27.1; Apr: 34.34; May: 38.5; Jun: 39.02; Jul: 42.62; Aug: 39.38; Sep: 38.5; Oct: 31.28; Nov: 28.6; Dec: 26.1
IA | BOONE MUNI | Jan: 21.8; Feb: 26.5; Mar: 36.8; Apr: 49.9; May: 60.9; Jun: 70.2; Jul: 74.1; Aug: 72.8; Sep: 63.8; Oct: 52.3; Nov: 38.7; Dec: 26.6; Jan: 19.2; Feb: 28.22; Mar: 20.3; Apr: 43.7; May: 48.6; Jun: 62.96; Jul: 63.14; Aug: 63.86; Sep: 52.3; Oct: 41; Nov: 27.7; Dec: 17.2
MA | BOSTON LOGAN INT ARPT | Jan: 30.2; Feb: 32; Mar: 38.7; Apr: 48.8; May: 58.1; Jun: 68; Jul: 73.8; Aug: 72.4; Sep: 65.3; Oct: 54.9; Nov: 45.1; Dec: 36; Jan: 13.8; Feb: 17.42; Mar: 24.6; Apr: 35.06; May: 47.1; Jun: 54.14; Jul: 60.62; Aug: 60.98; Sep: 53.2; Oct: 41.72; Nov: 33.4; Dec: 23
KY | BOWLING GREEN WARREN CO AP | Jan: 36.6; Feb: 40.4; Mar: 48.4; Apr: 58; May: 66.6; Jun: 74.8; Jul: 78.3; Aug: 77.3; Sep: 70.3; Oct: 58.7; Nov: 47.8; Dec: 39.3; Jan: 23.5; Feb: 32.4; Mar: 30.4; Apr: 46.6; May: 58.1; Jun: 66.4; Jul: 66.6; Aug: 67.1; Sep: 64; Oct: 53.4; Nov: 35.2; Dec: 32.2
MT | BOZEMAN GALLATIN FIELD | Jan: 21.7; Feb: 24.9; Mar: 34.5; Apr: 42.4; May: 51.3; Jun: 58.6; Jul: 67.6; Aug: 65.8; Sep: 56.6; Oct: 43.7; Nov: 30.3; Dec: 20.6; Jan: 16.3; Feb: 12.74; Mar: 26.1; Apr: 30.92; May: 37; Jun: 44.42; Jul: 48.02; Aug: 40.46; Sep: 32.2; Oct: 29.84; Nov: 20.8; Dec: 18.3
PA | BRADFORD REGIONAL AP | Jan: 23; Feb: 24.5; Mar: 32.4; Apr: 44.4; May: 54.5; Jun: 62.1; Jul: 65.6; Aug: 64.2; Sep: 57.6; Oct: 47.2; Nov: 37.6; Dec: 27.8; Jan: 11.7; Feb: 15.62; Mar: 27.1; Apr: 32; May: 41; Jun: 50.36; Jul: 58.46; Aug: 56.3; Sep: 49.5; Oct: 35.78; Nov: 28.6; Dec: 16.3
MN | BRAINERD/WIELAND | Jan: 11; Feb: 16.4; Mar: 28.2; Apr: 43.2; May: 55; Jun: 64.7; Jul: 70; Aug: 67.4; Sep: 59; Oct: 46; Nov: 30.8; Dec: 16.5; Jan: 7.5; Feb: 5.54; Mar: 24.3; Apr: 34.7; May: 42.3; Jun: 53.42; Jul: 59.36; Aug: 57.2; Sep: 51.3; Oct: 37.58; Nov: 20.7; Dec: 7.2
WA | BREMERTON NATIONAL | Jan: 38.9; Feb: 40.1; Mar: 43.5; Apr: 47.1; May: 53.2; Jun: 57.9; Jul: 63.2; Aug: 63.4; Sep: 58.9; Oct: 50; Nov: 42.6; Dec: 38.2; Jan: 34.2; Feb: 35.42; Mar: 37.4; Apr: 37.58; May: 41.5; Jun: 48.2; Jul: 50.9; Aug: 52.16; Sep: 43.5; Oct: 41.54; Nov: 38.7; Dec: 37.9
NE | BREWSTER FIELD ARPT | Jan: 28.2; Feb: 30.4; Mar: 40.4; Apr: 50.2; May: 61.1; Jun: 71; Jul: 76.3; Aug: 73.5; Sep: 65.1; Oct: 52.6; Nov: 40.7; Dec: 29.4; Jan: 16.9; Feb: 20.3; Mar: 28.4; Apr: 39.02; May: 47.3; Jun: 54.32; Jul: 63.14; Aug: 61.52; Sep: 54.1; Oct: 36.32; Nov: 24.6; Dec: 20.3
CT | BRIDGEPORT SIKORSKY MEMORIAL | Jan: 30.8; Feb: 33.2; Mar: 39.8; Apr: 49.7; May: 59.3; Jun: 68.9; Jul: 74.6; Aug: 73.7; Sep: 67; Oct: 55.7; Nov: 45.7; Dec: 36.6; Jan: 15.4; Feb: 22.1; Mar: 24.4; Apr: 37.04; May: 46.4; Jun: 56.66; Jul: 62.96; Aug: 61.88; Sep: 58.8; Oct: 44.78; Nov: 36.5; Dec: 23.9
TN | BRISTOL TRI CITY AIRPORT | Jan: 36.6; Feb: 39.9; Mar: 47.3; Apr: 56.3; May: 64.3; Jun: 72; Jul: 75; Aug: 74.1; Sep: 67.9; Oct: 56.7; Nov: 46.4; Dec: 39.1; Jan: 26.8; Feb: 24.08; Mar: 31.1; Apr: 39.92; May: 52.3; Jun: 62.6; Jul: 64.76; Aug: 64.04; Sep: 57.9; Oct: 46.22; Nov: 36.7; Dec: 25.5
NE | BROKEN BOW MUNI | Jan: 26.3; Feb: 26.9; Mar: 38.3; Apr: 48.4; May: 58.6; Jun: 68.7; Jul: 74.6; Aug: 72; Sep: 62.4; Oct: 49.6; Nov: 37.1; Dec: 26.5; Jan: 12.9; Feb: 18.86; Mar: 17.8; Apr: 36.32; May: 44.2; Jun: 56.84; Jul: 60.62; Aug: 64.22; Sep: 53.4; Oct: 36.32; Nov: 23; Dec: 19.6
SD | BROOKINGS (AWOS) | Jan: 13.7; Feb: 18.5; Mar: 30; Apr: 43.9; May: 56; Jun: 65.7; Jul: 71; Aug: 68.3; Sep: 59.4; Oct: 47; Nov: 32.3; Dec: 18.9; Jan: 12.2; Feb: 17.78; Mar: 21.4; Apr: 33.8; May: 45.9; Jun: 51.98; Jul: 60.08; Aug: 53.96; Sep: 47.5; Oct: 37.22; Nov: 17.8; Dec: 7.5
CO | BROOMFIELD/JEFFCO [BOULDER - SURFRAD] | Jan: 31.64; Feb: 33.08; Mar: 40.82; Apr: 49.64; May: 57.02; Jun: 66.2; Jul: 73.4; Aug: 71.06; Sep: 62.24; Oct: 50.9; Nov: 40.28; Dec: 29.12; Jan: 15.4; Feb: 18.14; Mar: 24.3; Apr: 30.02; May: 36.5; Jun: 42.8; Jul: 45.32; Aug: 48.92; Sep: 37.9; Oct: 27.32; Nov: 20.3; Dec: 12.9
TX | BROWNSVILLE S PADRE ISL INTL | Jan: 62; Feb: 65; Mar: 69.6; Apr: 75.1; May: 80.4; Jun: 84.2; Jul: 84.8; Aug: 85.3; Sep: 81.8; Oct: 76.4; Nov: 69; Dec: 62.9; Jan: 52.7; Feb: 52.34; Mar: 57.7; Apr: 67.82; May: 70.7; Jun: 74.84; Jul: 74.48; Aug: 73.22; Sep: 73.4; Oct: 66.02; Nov: 60.3; Dec: 53.2
GA | BRUNSWICK GOLDEN IS | Jan: 52.1; Feb: 54.3; Mar: 60.4; Apr: 67.2; May: 74.3; Jun: 80.5; Jul: 82.8; Aug: 82.1; Sep: 77.9; Oct: 69.3; Nov: 60; Dec: 54; Jan: 35.4; Feb: 47.66; Mar: 46.6; Apr: 53.24; May: 71.4; Jun: 72.68; Jul: 75.92; Aug: 71.78; Sep: 68.9; Oct: 56.12; Nov: 48.2; Dec: 44.2
GA | BRUNSWICK MALCOLM MCKINNON AP | Jan: 52.1; Feb: 54.7; Mar: 60.2; Apr: 66.6; May: 74.4; Jun: 79.9; Jul: 82.2; Aug: 81.4; Sep: 78; Oct: 69.9; Nov: 60.7; Dec: 54.5; Jan: 46.6; Feb: 52.34; Mar: 54.7; Apr: 64.4; May: 67.1; Jun: 69.8; Jul: 73.04; Aug: 73.04; Sep: 71.2; Oct: 64.22; Nov: 54.7; Dec: 51.3
UT | BRYCE CANYON AP | Jan: 21; Feb: 24; Mar: 32; Apr: 39; May: 47; Jun: 57; Jul: 64; Aug: 61; Sep: 54; Oct: 43; Nov: 32; Dec: 21; Jan: 9.1; Feb: 13.64; Mar: 19; Apr: 20.3; May: 28.8; Jun: 25.7; Jul: 34.34; Aug: 40.1; Sep: 28.6; Oct: 28.76; Nov: 16; Dec: 14.4
NY | BUFFALO NIAGARA INTL AP | Jan: 25.8; Feb: 26.4; Mar: 34.3; Apr: 46.1; May: 57.5; Jun: 67; Jul: 71.2; Aug: 70.1; Sep: 62.8; Oct: 51.7; Nov: 41.1; Dec: 31.2; Jan: 16.3; Feb: 17.42; Mar: 27; Apr: 35.42; May: 42.4; Jun: 52.7; Jul: 60.98; Aug: 56.66; Sep: 52.2; Oct: 41; Nov: 33.4; Dec: 22.5
CA | BURBANK-GLENDALE-PASADENA AP | Jan: 56.4; Feb: 56.5; Mar: 59.4; Apr: 62.3; May: 66.2; Jun: 70.1; Jul: 75.3; Aug: 76.7; Sep: 74.7; Oct: 67.9; Nov: 61; Dec: 55.2; Jan: 36.1; Feb: 35.6; Mar: 49.6; Apr: 46.4; May: 50.2; Jun: 58.46; Jul: 58.28; Aug: 57.2; Sep: 57.6; Oct: 51.26; Nov: 43.3; Dec: 35.6
OH | BURKE LAKEFRONT | Jan: 29.8; Feb: 31.3; Mar: 38.3; Apr: 50.2; May: 61.3; Jun: 70.6; Jul: 74.6; Aug: 73.4; Sep: 66.9; Oct: 55.7; Nov: 46.3; Dec: 34.9; Jan: 15.3; Feb: 23.72; Mar: 27.1; Apr: 40.46; May: 44.6; Jun: 61.88; Jul: 64.22; Aug: 61.52; Sep: 55.8; Oct: 43.34; Nov: 40.1; Dec: 17.4
ID | BURLEY MUNICIPAL ARPT | Jan: 28.8; Feb: 33; Mar: 41.3; Apr: 47.1; May: 55.4; Jun: 63.2; Jul: 72.2; Aug: 70; Sep: 61.3; Oct: 49.6; Nov: 37.8; Dec: 28.9; Jan: 22.5; Feb: 19.94; Mar: 26.2; Apr: 30.2; May: 33.4; Jun: 42.62; Jul: 51.08; Aug: 46.76; Sep: 39.6; Oct: 33.62; Nov: 27.9; Dec: 26.2
VT | BURLINGTON INTERNATIONAL AP | Jan: 20.1; Feb: 22; Mar: 31.5; Apr: 44.9; May: 57; Jun: 66.5; Jul: 70.9; Aug: 69.3; Sep: 61.1; Oct: 49.2; Nov: 38.5; Dec: 27.1; Jan: 12; Feb: 11.66; Mar: 19.8; Apr: 30.02; May: 42.1; Jun: 55.22; Jul: 57.74; Aug: 57.02; Sep: 50.2; Oct: 38.12; Nov: 27; Dec: 19.2
IA | BURLINGTON MUNICIPAL AP | Jan: 24.8; Feb: 29.5; Mar: 40.9; Apr: 52.9; May: 63.2; Jun: 72.5; Jul: 75.9; Aug: 74.3; Sep: 66.4; Oct: 54.7; Nov: 41.6; Dec: 29.7; Jan: 15.1; Feb: 15.98; Mar: 31.8; Apr: 42.8; May: 53.2; Jun: 64.4; Jul: 68.72; Aug: 66.56; Sep: 58.3; Oct: 41.18; Nov: 36.9; Dec: 18.9
ON | BURLINGTON PIERS | Jan: 26.5; Feb: 27.2; Mar: 34.3; Apr: 44.7; May: 55.1; Jun: 65.6; Jul: 70.9; Aug: 70.4; Sep: 63.6; Oct: 52.1; Nov: 41.8; Dec: 32.4; Jan: 15.8; Feb: 17.06; Mar: 23.9; Apr: 32.54; May: 42.4; Jun: 53.6; Jul: 57.92; Aug: 58.82; Sep: 54.1; Oct: 42.26; Nov: 34; Dec: 20.3
OR | BURNS MUNICIPAL ARPT [UO] | Jan: 26; Feb: 29.3; Mar: 37.6; Apr: 43; May: 51.3; Jun: 58.3; Jul: 67.7; Aug: 65.4; Sep: 57.2; Oct: 44.9; Nov: 33.8; Dec: 25.2; Jan: 19.9; Feb: 22.1; Mar: 27.9; Apr: 25.52; May: 30.2; Jun: 40.64; Jul: 37.76; Aug: 40.64; Sep: 34.9; Oct: 30.74; Nov: 25.3; Dec: 23.5
PA | BUTLER CO (AWOS) | Jan: 27.4; Feb: 28.7; Mar: 37.9; Apr: 49.6; May: 58.3; Jun: 67.4; Jul: 70.9; Aug: 69.4; Sep: 62.1; Oct: 51.3; Nov: 41.4; Dec: 32.2; Jan: 21.9; Feb: 23.18; Mar: 25.2; Apr: 33.26; May: 43.2; Jun: 57.02; Jul: 62.24; Aug: 58.64; Sep: 48.7; Oct: 38.84; Nov: 28; Dec: 23.5
MT | BUTTE BERT MOONEY ARPT | Jan: 20.5; Feb: 22.6; Mar: 31.8; Apr: 38.7; May: 47.3; Jun: 54.8; Jul: 63.7; Aug: 61.8; Sep: 53; Oct: 40.9; Nov: 28.4; Dec: 18.8; Jan: 12.7; Feb: 13.82; Mar: 19.9; Apr: 25.34; May: 29.7; Jun: 36.86; Jul: 41.18; Aug: 42.8; Sep: 34.3; Oct: 28.22; Nov: 17.8; Dec: 14.5
MI | CADILLAC WEXFORD CO AP | Jan: 19.4; Feb: 20.6; Mar: 29.5; Apr: 42.1; May: 53.5; Jun: 63.4; Jul: 67.2; Aug: 65.3; Sep: 57.8; Oct: 46.6; Nov: 35.3; Dec: 25; Jan: 12.6; Feb: 26.42; Mar: 15.4; Apr: 28.58; May: 39.2; Jun: 54.5; Jul: 55.76; Aug: 54.68; Sep: 53.2; Oct: 36.5; Nov: 33.8; Dec: 20.7
IL | CAHOKIA/ST. LOUIS | Jan: 32.5; Feb: 35.8; Mar: 46.1; Apr: 57.2; May: 66.6; Jun: 74.5; Jul: 78.3; Aug: 77; Sep: 68.6; Oct: 57.5; Nov: 46.1; Dec: 35.4; Jan: 27.5; Feb: 29.12; Mar: 37.2; Apr: 47.12; May: 46.9; Jun: 60.98; Jul: 69.26; Aug: 69.08; Sep: 63.1; Oct: 46.76; Nov: 39.4; Dec: 24.3
AL | CAIRNS FIELD FORT RUCKER | Jan: 50.3; Feb: 53.4; Mar: 59.4; Apr: 65.7; May: 73.8; Jun: 79.5; Jul: 81.4; Aug: 80.4; Sep: 76.7; Oct: 67.4; Nov: 57.7; Dec: 52.4; Jan: 35.4; Feb: 41.36; Mar: 42.8; Apr: 47.3; May: 68.9; Jun: 68.9; Jul: 73.76; Aug: 70.52; Sep: 66.6; Oct: 48.92; Nov: 45.7; Dec: 39.6
ID | CALDWELL (AWOS) | Jan: 30.7; Feb: 35.9; Mar: 43.9; Apr: 49.4; May: 58.2; Jun: 65.5; Jul: 74.3; Aug: 72; Sep: 63; Oct: 50.6; Nov: 38.5; Dec: 31; Jan: 28.9; Feb: 25.34; Mar: 27.7; Apr: 33.08; May: 34.7; Jun: 43.88; Jul: 45.32; Aug: 40.64; Sep: 37.6; Oct: 36.86; Nov: 28.6; Dec: 20.8
NJ | CALDWELL/ESSEX CO. | Jan: 29.8; Feb: 32.1; Mar: 40.8; Apr: 51.8; May: 61.3; Jun: 70.4; Jul: 75.3; Aug: 73.5; Sep: 66.2; Oct: 54.5; Nov: 44.9; Dec: 34.9; Jan: 16.5; Feb: 20.84; Mar: 28.6; Apr: 37.4; May: 45; Jun: 57.02; Jul: 58.64; Aug: 60.8; Sep: 58.1; Oct: 44.24; Nov: 33.6; Dec: 29.5
AB | CALGARY INT AP | Jan: 18.9; Feb: 22.3; Mar: 28.4; Apr: 39.5; May: 49; Jun: 55.9; Jul: 61.9; Aug: 60.7; Sep: 53.1; Oct: 41.1; Nov: 28; Dec: 20; Jan: 9.1; Feb: 10.76; Mar: 15.4; Apr: 23.36; May: 32.4; Jun: 43.16; Jul: 48.56; Aug: 45.14; Sep: 36.9; Oct: 26.42; Nov: 17.6; Dec: 9.7
CA | CAMARILLO (AWOS) | Jan: 55.5; Feb: 55.1; Mar: 57; Apr: 58.5; May: 61.8; Jun: 64.7; Jul: 67.7; Aug: 68.2; Sep: 67.3; Oct: 63.9; Nov: 59.3; Dec: 54.7; Jan: 38.8; Feb: 38.3; Mar: 38.5; Apr: 44.6; May: 53.1; Jun: 53.78; Jul: 56.3; Aug: 58.82; Sep: 55; Oct: 53.24; Nov: 43.7; Dec: 42.4
MN | CAMBRIDGE MUNI | Jan: 12.5; Feb: 17.3; Mar: 29.6; Apr: 44.1; May: 56.3; Jun: 66; Jul: 71.3; Aug: 68.3; Sep: 59.8; Oct: 47; Nov: 32.2; Dec: 18.3; Jan: -2.9; Feb: 5.9; Mar: 21.4; Apr: 35.78; May: 37.9; Jun: 53.96; Jul: 61.88; Aug: 61.16; Sep: 52.2; Oct: 37.4; Nov: 18.7; Dec: 16.7
TX | CAMP MABRY | Jan: 52.2; Feb: 55.6; Mar: 61.7; Apr: 69.1; May: 76.5; Jun: 82.1; Jul: 84.7; Aug: 85.2; Sep: 79.9; Oct: 70.9; Nov: 60.8; Dec: 52.8; Jan: 37.2; Feb: 42.44; Mar: 44.2; Apr: 57.74; May: 65.7; Jun: 69.44; Jul: 71.24; Aug: 67.64; Sep: 65.5; Oct: 56.48; Nov: 48.7; Dec: 37.2
CA | CAMP PENDLETON MCAS | Jan: 54.4; Feb: 54.4; Mar: 56.9; Apr: 59.1; May: 63.2; Jun: 66.4; Jul: 70.1; Aug: 71.4; Sep: 69.8; Oct: 64.4; Nov: 58.6; Dec: 53.5; Jan: 41.4; Feb: 48.02; Mar: 42.3; Apr: 49.1; May: 54.7; Jun: 55.76; Jul: 59.36; Aug: 59.36; Sep: 56.8; Oct: 54.5; Nov: 44.2; Dec: 39.7
MO | CAPE GIRARDEAU MUNICIPAL AP | Jan: 34.7; Feb: 39; Mar: 47.8; Apr: 58; May: 67.4; Jun: 75.8; Jul: 78.8; Aug: 77.3; Sep: 69.1; Oct: 58.2; Nov: 46.9; Dec: 37.5; Jan: 24.1; Feb: 28.58; Mar: 39.7; Apr: 40.46; May: 50.4; Jun: 67.64; Jul: 67.28; Aug: 68.9; Sep: 56.1; Oct: 48.92; Nov: 43.5; Dec: 27.7
NC | CAPE HATTERAS NWS BLDG | Jan: 46.2; Feb: 47.4; Mar: 51.9; Apr: 59.7; May: 67.3; Jun: 76.2; Jul: 79.2; Aug: 78.9; Sep: 74.9; Oct: 66; Nov: 57.2; Dec: 49.4; Jan: 35.6; Feb: 39.74; Mar: 45.1; Apr: 51.62; May: 59.5; Jun: 68.36; Jul: 73.4; Aug: 70.88; Sep: 68.4; Oct: 53.96; Nov: 49.6; Dec: 37
NJ | CAPE MAY CO | Jan: 35.2; Feb: 36.6; Mar: 43; Apr: 52; May: 60.7; Jun: 70.9; Jul: 76.3; Aug: 74.2; Sep: 68; Oct: 57.6; Nov: 47.7; Dec: 40; Jan: 29.1; Feb: 28.58; Mar: 28.8; Apr: 36.32; May: 49.8; Jun: 60.98; Jul: 51.26; Aug: 62.96; Sep: 60.4; Oct: 47.48; Nov: 42.8; Dec: 29.8
ME | CARIBOU MUNICIPAL ARPT | Jan: 11.2; Feb: 13.9; Mar: 25; Apr: 38.5; May: 51.5; Jun: 61.2; Jul: 66; Aug: 64.2; Sep: 55.7; Oct: 44.1; Nov: 32.2; Dec: 19.6; Jan: 6.4; Feb: 7.7; Mar: 10.9; Apr: 26.24; May: 34.9; Jun: 49.1; Jul: 56.3; Aug: 55.76; Sep: 46; Oct: 34.7; Nov: 23; Dec: 9.9
NM | CARLSBAD CAVERN CITY AIR TERM | Jan: 44.9; Feb: 49.2; Mar: 56.2; Apr: 64.7; May: 73.8; Jun: 81.9; Jul: 82.4; Aug: 81.3; Sep: 74.3; Oct: 64.3; Nov: 52.1; Dec: 44.3; Jan: 26.1; Feb: 35.78; Mar: 20.7; Apr: 39.38; May: 39; Jun: 57.56; Jul: 55.76; Aug: 58.1; Sep: 54.9; Oct: 35.24; Nov: 28.4; Dec: 27.1
CA | CARLSBAD/PALOMAR | Jan: 56.4; Feb: 55.6; Mar: 57.1; Apr: 58.8; May: 62.3; Jun: 64.7; Jul: 68.9; Aug: 69.9; Sep: 68.9; Oct: 65.1; Nov: 60.4; Dec: 55.8; Jan: 46; Feb: 46.76; Mar: 47.8; Apr: 48.74; May: 52.2; Jun: 56.12; Jul: 60.8; Aug: 61.88; Sep: 59.9; Oct: 55.4; Nov: 44.1; Dec: 41.7
IA | CARROLL | Jan: 21.6; Feb: 24.5; Mar: 36.7; Apr: 50; May: 61.5; Jun: 71.1; Jul: 74.2; Aug: 71.9; Sep: 64; Oct: 52.1; Nov: 38.2; Dec: 24.8; Jan: 14; Feb: 13.1; Mar: 32; Apr: 41.36; May: 47.8; Jun: 61.16; Jul: 64.76; Aug: 63.32; Sep: 53.6; Oct: 39.74; Nov: 25.5; Dec: 14.2
WY | CASPER NATRONA CO INTL AP | Jan: 25.9; Feb: 27.6; Mar: 36.2; Apr: 42.8; May: 52.6; Jun: 62.6; Jul: 71.2; Aug: 69.7; Sep: 59.4; Oct: 46.1; Nov: 34.4; Dec: 25.3; Jan: 11.3; Feb: 14; Mar: 21.4; Apr: 23.36; May: 33.6; Jun: 39.74; Jul: 44.6; Aug: 39.74; Sep: 32.4; Oct: 27.86; Nov: 19; Dec: 13.6
UT | CEDAR CITY MUNICIPAL AP | Jan: 30.3; Feb: 34.3; Mar: 41.7; Apr: 47.6; May: 57.1; Jun: 67.1; Jul: 74.3; Aug: 72.3; Sep: 63.6; Oct: 51; Nov: 38.7; Dec: 29.4; Jan: 18.9; Feb: 18.5; Mar: 25.7; Apr: 22.1; May: 28.2; Jun: 29.12; Jul: 40.64; Aug: 42.44; Sep: 35.1; Oct: 29.12; Nov: 22.3; Dec: 18.1
IA | CEDAR RAPIDS MUNICIPAL AP | Jan: 20.2; Feb: 24.8; Mar: 36.7; Apr: 49.3; May: 60.3; Jun: 69.8; Jul: 73; Aug: 71.2; Sep: 63.1; Oct: 51.2; Nov: 37.4; Dec: 24.8; Jan: 13.5; Feb: 22.28; Mar: 30.2; Apr: 41; May: 49.1; Jun: 62.6; Jul: 65.66; Aug: 63.14; Sep: 55.4; Oct: 44.6; Nov: 30.4; Dec: 6.6
IL | CENTRAL ILLINOIS RG | Jan: 24.6; Feb: 27.2; Mar: 40.5; Apr: 52.6; May: 62.5; Jun: 71.9; Jul: 75; Aug: 73.3; Sep: 66.3; Oct: 53.9; Nov: 41.6; Dec: 29.6; Jan: 25.5; Feb: 20.84; Mar: 28.6; Apr: 31.64; May: 43.5; Jun: 58.82; Jul: 63.86; Aug: 61.16; Sep: 49.1; Oct: 39.2; Nov: 31.8; Dec: 22.8
NE | CHADRON MUNI AP | Jan: 26; Feb: 26; Mar: 38; Apr: 46; May: 55; Jun: 67; Jul: 76; Aug: 73; Sep: 63; Oct: 48; Nov: 36; Dec: 25; Jan: 18.9; Feb: 12.02; Mar: 22.6; Apr: 31.46; May: 43.2; Jun: 46.94; Jul: 57.02; Aug: 53.78; Sep: 42.4; Oct: 30.56; Nov: 24.6; Dec: 15.8
SD | CHAN GURNEY MUNI | Jan: 20.2; Feb: 24.4; Mar: 35.6; Apr: 48; May: 59.6; Jun: 69.2; Jul: 74.4; Aug: 72.1; Sep: 63.6; Oct: 50.5; Nov: 36.1; Dec: 24; Jan: 13.1; Feb: 11.84; Mar: 14.2; Apr: 36.86; May: 44.6; Jun: 55.58; Jul: 63.14; Aug: 62.24; Sep: 52.2; Oct: 34.52; Nov: 27.9; Dec: 16
KS | CHANUTE MARTIN JOHNSON AP | Jan: 33.1; Feb: 37.2; Mar: 47; Apr: 57.3; May: 66.3; Jun: 74.8; Jul: 79.8; Aug: 79.3; Sep: 70.1; Oct: 58.2; Nov: 46.7; Dec: 35.2; Jan: 30.6; Feb: 25.88; Mar: 37.9; Apr: 49.28; May: 59.4; Jun: 64.04; Jul: 68.36; Aug: 68.9; Sep: 65.3; Oct: 51.44; Nov: 31.8; Dec: 15.4
IA | CHARITON | Jan: 25.5; Feb: 28.9; Mar: 39.5; Apr: 52.5; May: 62.4; Jun: 71.6; Jul: 76.5; Aug: 74; Sep: 65.7; Oct: 54; Nov: 41.6; Dec: 28.3; Jan: 14; Feb: 16.52; Mar: 36.3; Apr: 44.42; May: 54; Jun: 65.12; Jul: 69.44; Aug: 66.92; Sep: 54.3; Oct: 41.18; Nov: 28; Dec: 21.7
IA | CHARLES CITY | Jan: 18.6; Feb: 23.2; Mar: 34.1; Apr: 48.2; May: 59.5; Jun: 69.2; Jul: 72.3; Aug: 70.2; Sep: 62.4; Oct: 50.5; Nov: 35.7; Dec: 22.6; Jan: 19; Feb: 12.92; Mar: 34; Apr: 42.44; May: 46.9; Jun: 55.22; Jul: 64.58; Aug: 69.26; Sep: 59.9; Oct: 43.88; Nov: 28.4; Dec: 21.6
SC | CHARLESTON INTL ARPT | Jan: 49.8; Feb: 52.5; Mar: 58.7; Apr: 65.7; May: 73.1; Jun: 79.3; Jul: 82.3; Aug: 81.2; Sep: 76.5; Oct: 67.4; Nov: 58.2; Dec: 52; Jan: 37.9; Feb: 36.5; Mar: 47.8; Apr: 51.8; May: 63.3; Jun: 69.62; Jul: 72.86; Aug: 72.32; Sep: 67.8; Oct: 56.84; Nov: 49.3; Dec: 40.1
WV | CHARLESTON YEAGER ARPT | Jan: 35.2; Feb: 38; Mar: 45.9; Apr: 56.8; May: 64; Jun: 71.9; Jul: 75.1; Aug: 74.1; Sep: 67.3; Oct: 56.4; Nov: 46.4; Dec: 38.3; Jan: 19; Feb: 25.16; Mar: 32.4; Apr: 39.02; May: 51.8; Jun: 62.24; Jul: 68.18; Aug: 65.48; Sep: 58.3; Oct: 45.14; Nov: 36.5; Dec: 25.9
NC | CHARLOTTE DOUGLAS INTL ARPT | Jan: 42.5; Feb: 45.7; Mar: 52.7; Apr: 61.1; May: 68.8; Jun: 76.3; Jul: 79.5; Aug: 78.3; Sep: 72.1; Oct: 61.6; Nov: 51.5; Dec: 44.6; Jan: 28.8; Feb: 31.28; Mar: 35.1; Apr: 42.8; May: 56.7; Jun: 63.14; Jul: 68.18; Aug: 69.26; Sep: 62.4; Oct: 49.28; Nov: 39.4; Dec: 28.4
VA | CHARLOTTESVILLE FAA | Jan: 36.4; Feb: 38.9; Mar: 46.8; Apr: 56.7; May: 64.6; Jun: 72.9; Jul: 76.1; Aug: 74.9; Sep: 67.5; Oct: 57; Nov: 47.8; Dec: 39.3; Jan: 18.3; Feb: 32.54; Mar: 31.1; Apr: 41.36; May: 56.1; Jun: 62.24; Jul: 64.58; Aug: 64.58; Sep: 59.7; Oct: 43.16; Nov: 34.5; Dec: 29.8
PE | CHARLOTTETOWN | Jan: 19.2; Feb: 19.4; Mar: 27.3; Apr: 37.8; May: 48.3; Jun: 58.5; Jul: 66.2; Aug: 65.5; Sep: 58.3; Oct: 48; Nov: 37.9; Dec: 27.6; Jan: 13.1; Feb: 12.56; Mar: 20.1; Apr: 29.3; May: 39.2; Jun: 50.9; Jul: 58.82; Aug: 58.1; Sep: 51.3; Oct: 41.72; Nov: 33.1; Dec: 21.4
TN | CHATTANOOGA LOVELL FIELD AP | Jan: 41.8; Feb: 45.2; Mar: 52.8; Apr: 61.4; May: 69.2; Jun: 76.8; Jul: 79.9; Aug: 79.6; Sep: 73.1; Oct: 61.8; Nov: 50.9; Dec: 43.8; Jan: 31.1; Feb: 32.54; Mar: 39.7; Apr: 45.32; May: 56.5; Jun: 67.46; Jul: 68.36; Aug: 68.9; Sep: 63.7; Oct: 51.8; Nov: 41.9; Dec: 30.2
NC | CHERRY POINT MCAS | Jan: 45.8; Feb: 47.6; Mar: 53.7; Apr: 61.9; May: 69.5; Jun: 76.9; Jul: 80.1; Aug: 79; Sep: 74.4; Oct: 64.6; Nov: 55.2; Dec: 48.7; Jan: 32.9; Feb: 34.16; Mar: 36.7; Apr: 44.42; May: 54; Jun: 68.18; Jul: 74.3; Aug: 68.9; Sep: 63; Oct: 50.18; Nov: 41.4; Dec: 30
WY | CHEYENNE MUNICIPAL ARPT | Jan: 29.1; Feb: 29.3; Mar: 36.5; Apr: 42.6; May: 52.1; Jun: 62.3; Jul: 69.4; Aug: 67.7; Sep: 58.9; Oct: 46.4; Nov: 35.8; Dec: 28.3; Jan: 12; Feb: 12.2; Mar: 18.1; Apr: 24.98; May: 34; Jun: 40.64; Jul: 44.06; Aug: 45.68; Sep: 37.6; Oct: 22.82; Nov: 14; Dec: 15.4
IL | CHICAGO MIDWAY AP | Jan: 25.9; Feb: 29.5; Mar: 39.3; Apr: 50.5; May: 61.1; Jun: 71.1; Jul: 75.7; Aug: 74.1; Sep: 66.5; Oct: 54.6; Nov: 41.9; Dec: 30.6; Jan: 12.6; Feb: 19.76; Mar: 29.8; Apr: 42.62; May: 44.4; Jun: 57.02; Jul: 60.8; Aug: 62.6; Sep: 58.6; Oct: 43.88; Nov: 33.6; Dec: 21.2
IL | CHICAGO OHARE INTL AP | Jan: 24.6; Feb: 28.2; Mar: 38.2; Apr: 49.2; May: 59.6; Jun: 69.5; Jul: 74.2; Aug: 72.7; Sep: 64.9; Oct: 53.1; Nov: 40.6; Dec: 29.3; Jan: 15.1; Feb: 17.24; Mar: 29.3; Apr: 39.2; May: 45; Jun: 55.4; Jul: 65.66; Aug: 61.88; Sep: 55.2; Oct: 41; Nov: 32.7; Dec: 18.3
IL | CHICAGO/WAUKEGAN | Jan: 23.3; Feb: 25.3; Mar: 35.7; Apr: 46.6; May: 56.1; Jun: 66.2; Jul: 71.5; Aug: 70.5; Sep: 62.9; Oct: 51.5; Nov: 40.2; Dec: 27.7; Jan: 19.4; Feb: 20.12; Mar: 23.2; Apr: 38.3; May: 42.1; Jun: 57.38; Jul: 66.92; Aug: 63.32; Sep: 52.3; Oct: 39.74; Nov: 34.5; Dec: 17.2
MA | CHICOPEE FALLS WESTO | Jan: 25.2; Feb: 26.7; Mar: 36.6; Apr: 48.1; May: 58.2; Jun: 67; Jul: 72.5; Aug: 69.9; Sep: 61.9; Oct: 51.4; Nov: 40.8; Dec: 31.3; Jan: 23; Feb: 20.48; Mar: 25.3; Apr: 30.2; May: 41.2; Jun: 57.56; Jul: 59.36; Aug: 58.46; Sep: 52.7; Oct: 40.46; Nov: 31.8; Dec: 29.3
TX | CHILDRESS MUNICIPAL AP | Jan: 41.9; Feb: 45.2; Mar: 53.6; Apr: 62.5; May: 71.5; Jun: 79.8; Jul: 83; Aug: 82; Sep: 74.1; Oct: 63.3; Nov: 51.6; Dec: 42.6; Jan: 26.6; Feb: 34.34; Mar: 36.1; Apr: 45.68; May: 57; Jun: 59.54; Jul: 62.96; Aug: 64.22; Sep: 56.8; Oct: 42.26; Nov: 41; Dec: 26.8
CA | CHINA LAKE NAF | Jan: 46; Feb: 50; Mar: 58; Apr: 64; May: 72; Jun: 82; Jul: 88; Aug: 86; Sep: 79; Oct: 66; Nov: 54; Dec: 44; Jan: 18.1; Feb: 25.7; Mar: 28; Apr: 25.34; May: 34.2; Jun: 30.2; Jul: 36.5; Aug: 40.28; Sep: 29.5; Oct: 24.44; Nov: 25.5; Dec: 23
CA | CHINO AIRPORT | Jan: 54.5; Feb: 54.4; Mar: 57.6; Apr: 60.4; May: 66.5; Jun: 70.7; Jul: 76.6; Aug: 77; Sep: 74.4; Oct: 66.7; Nov: 59.3; Dec: 53.4; Jan: 37; Feb: 39.2; Mar: 46.8; Apr: 49.28; May: 52.3; Jun: 54.86; Jul: 58.46; Aug: 58.1; Sep: 52.5; Oct: 49.1; Nov: 44.2; Dec: 38.5
MI | CHIPPEWA CO INTL | Jan: 16.1; Feb: 17.2; Mar: 26; Apr: 38.7; May: 51.6; Jun: 61.1; Jul: 64.9; Aug: 64.2; Sep: 56.5; Oct: 45; Nov: 33.3; Dec: 22.1; Jan: 4.1; Feb: 14.72; Mar: 13.6; Apr: 33.08; May: 36.9; Jun: 51.44; Jul: 53.6; Aug: 50.54; Sep: 46.8; Oct: 34.34; Nov: 27.7; Dec: 19.6
CA | CHULA VISTA BROWN FIELD NAAS | Jan: 55.9; Feb: 54.9; Mar: 57.2; Apr: 59.2; May: 63; Jun: 65.6; Jul: 69.5; Aug: 70.8; Sep: 70.1; Oct: 65.6; Nov: 60.3; Dec: 55.3; Jan: 42.8; Feb: 44.6; Mar: 48.2; Apr: 51.08; May: 51.1; Jun: 55.4; Jul: 59.54; Aug: 60.62; Sep: 56.7; Oct: 49.28; Nov: 43.2; Dec: 37.8
OH | CINCINNATI MUNICIPAL AP LUNKI | Jan: 32.6; Feb: 35.6; Mar: 44.3; Apr: 54.9; May: 64; Jun: 72.4; Jul: 76; Aug: 74.9; Sep: 67.5; Oct: 55.9; Nov: 45; Dec: 36.2; Jan: 24.6; Feb: 22.64; Mar: 31.5; Apr: 45.14; May: 52.3; Jun: 59.54; Jul: 66.38; Aug: 65.3; Sep: 57.6; Oct: 47.48; Nov: 40.3; Dec: 27.5
KY | CINCINNATI NORTHERN KY AP | Jan: 31.4; Feb: 34.7; Mar: 43.7; Apr: 54.6; May: 63.8; Jun: 72.1; Jul: 75.5; Aug: 74.9; Sep: 67.4; Oct: 55.8; Nov: 44.6; Dec: 35.3; Jan: 19.8; Feb: 20.5; Mar: 33.6; Apr: 38.3; May: 53.2; Jun: 61.7; Jul: 63.7; Aug: 62.8; Sep: 56.5; Oct: 43.5; Nov: 36.1; Dec: 25.3
IA | CLARINDA | Jan: 24.5; Feb: 28.1; Mar: 40.4; Apr: 51.8; May: 62.7; Jun: 71.9; Jul: 75.8; Aug: 74.1; Sep: 65.2; Oct: 53.5; Nov: 39.9; Dec: 28.6; Jan: 14.7; Feb: 27.86; Mar: 30.2; Apr: 44.24; May: 57.7; Jun: 64.58; Jul: 69.44; Aug: 69.44; Sep: 61.7; Oct: 42.8; Nov: 30.6; Dec: 19
NM | CLAYTON MUNICIPAL AIRPARK | Jan: 35.9; Feb: 38.1; Mar: 45.2; Apr: 52.7; May: 62.4; Jun: 71.8; Jul: 75.5; Aug: 73.9; Sep: 66.7; Oct: 55.6; Nov: 44.4; Dec: 35.7; Jan: 17.1; Feb: 17.24; Mar: 15.4; Apr: 28.22; May: 41; Jun: 50; Jul: 50.9; Aug: 54.14; Sep: 52.2; Oct: 39.02; Nov: 24.8; Dec: 15.1
OH | CLEVELAND HOPKINS INTL AP | Jan: 28.2; Feb: 30.1; Mar: 38; Apr: 49.6; May: 59.8; Jun: 69.2; Jul: 73; Aug: 71.6; Sep: 64.5; Oct: 53.7; Nov: 43; Dec: 33; Jan: 19; Feb: 18.14; Mar: 28.6; Apr: 37.4; May: 45.7; Jun: 59.18; Jul: 61.7; Aug: 61.34; Sep: 55; Oct: 42.44; Nov: 33.4; Dec: 20.5
IA | CLINTON MUNI (AWOS) | Jan: 20.9; Feb: 25; Mar: 36.9; Apr: 49.1; May: 60.7; Jun: 69.9; Jul: 73.2; Aug: 70.9; Sep: 63.3; Oct: 51.3; Nov: 38.8; Dec: 26.4; Jan: 14.7; Feb: 25.7; Mar: 26.8; Apr: 37.94; May: 44.8; Jun: 58.82; Jul: 63.5; Aug: 67.82; Sep: 57.2; Oct: 37.4; Nov: 26.8; Dec: 8.8
OK | CLINTON-SHERMAN | Jan: 40; Feb: 42.2; Mar: 50.5; Apr: 59.6; May: 70.1; Jun: 79; Jul: 83.7; Aug: 82.9; Sep: 74.5; Oct: 62.2; Nov: 49.8; Dec: 40.1; Jan: 30; Feb: 28.22; Mar: 34.5; Apr: 42.8; May: 57.4; Jun: 63.14; Jul: 65.48; Aug: 66.2; Sep: 55.6; Oct: 49.46; Nov: 34.7; Dec: 22.3
MN | CLOQUET (AWOS) | Jan: 10.6; Feb: 15.1; Mar: 26.4; Apr: 39.1; May: 50.3; Jun: 59.6; Jul: 66; Aug: 64.3; Sep: 55.8; Oct: 43.8; Nov: 29.4; Dec: 16.2; Jan: 9.5; Feb: 13.28; Mar: 25.2; Apr: 32.18; May: 36.7; Jun: 55.76; Jul: 61.34; Aug: 60.98; Sep: 50; Oct: 35.42; Nov: 14.4; Dec: 11.7
NM | CLOVIS CANNON AFB | Jan: 38.9; Feb: 43.5; Mar: 49.9; Apr: 57.8; May: 66.6; Jun: 75.8; Jul: 77.8; Aug: 76.8; Sep: 70.3; Oct: 59.3; Nov: 47.6; Dec: 40; Jan: 22.5; Feb: 27.14; Mar: 28.8; Apr: 34.34; May: 36.5; Jun: 39.02; Jul: 51.8; Aug: 57.74; Sep: 40.8; Oct: 40.28; Nov: 30.7; Dec: 25.2
NM | CLOVIS MUNI (AWOS) | Jan: 38.3; Feb: 41.1; Mar: 48.4; Apr: 56.1; May: 65.6; Jun: 74.6; Jul: 76.6; Aug: 75.4; Sep: 68.6; Oct: 57.7; Nov: 46.4; Dec: 37.9; Jan: 21; Feb: 24.98; Mar: 15.4; Apr: 33.08; May: 38.3; Jun: 53.78; Jul: 53.06; Aug: 51.08; Sep: 48.9; Oct: 43.7; Nov: 28; Dec: 17.6
WY | CODY MUNI (AWOS) | Jan: 26.2; Feb: 27.3; Mar: 36.3; Apr: 42.9; May: 52.4; Jun: 61; Jul: 69.9; Aug: 68.4; Sep: 59.1; Oct: 45.9; Nov: 34.5; Dec: 26.7; Jan: 15.3; Feb: 12.2; Mar: 15.8; Apr: 23.9; May: 30.2; Jun: 38.48; Jul: 39.74; Aug: 37.04; Sep: 34.7; Oct: 22.64; Nov: 21.2; Dec: 13.1
ID | COEUR D`ALENE(AWOS) | Jan: 29.3; Feb: 31.5; Mar: 38.4; Apr: 45.2; May: 53.7; Jun: 59.5; Jul: 68; Aug: 67.3; Sep: 59.3; Oct: 46.6; Nov: 36; Dec: 28.6; Jan: 22.8; Feb: 24.98; Mar: 29.3; Apr: 34.52; May: 37.9; Jun: 46.58; Jul: 49.1; Aug: 43.7; Sep: 42.1; Oct: 36.32; Nov: 31.1; Dec: 24.4
AK | COLD BAY ARPT | Jan: 28.4; Feb: 29.3; Mar: 29.4; Apr: 34.4; May: 40.4; Jun: 46.4; Jul: 50.8; Aug: 52.1; Sep: 48; Oct: 40.7; Nov: 34.7; Dec: 30.9; Jan: 26.6; Feb: 25.52; Mar: 25.7; Apr: 27.86; May: 33.8; Jun: 41.72; Jul: 45.5; Aug: 46.4; Sep: 44.1; Oct: 35.42; Nov: 30.4; Dec: 28.4
TX | COLLEGE STATION EASTERWOOD FL | Jan: 51.6; Feb: 55.3; Mar: 61.4; Apr: 68.7; May: 76.2; Jun: 82.6; Jul: 84.6; Aug: 85.3; Sep: 80.1; Oct: 70.8; Nov: 60.1; Dec: 52.9; Jan: 39.7; Feb: 46.94; Mar: 47.8; Apr: 52.52; May: 62.8; Jun: 73.58; Jul: 71.78; Aug: 70.88; Sep: 66; Oct: 61.52; Nov: 48; Dec: 40.5
CO | COLORADO SPRINGS MUNI AP | Jan: 31.1; Feb: 32.6; Mar: 40.1; Apr: 46.7; May: 56.3; Jun: 66.2; Jul: 71.2; Aug: 69.1; Sep: 61.7; Oct: 50; Nov: 38.7; Dec: 30.7; Jan: 11.48; Feb: 13.82; Mar: 18.5; Apr: 26.06; May: 35.24; Jun: 43.88; Jul: 47.66; Aug: 47.3; Sep: 40.64; Oct: 23.36; Nov: 19.76; Dec: 10.04
SC | COLUMBIA METRO ARPT | Jan: 46.2; Feb: 49.3; Mar: 56; Apr: 64.2; May: 72.1; Jun: 79.1; Jul: 82.2; Aug: 80.9; Sep: 75.1; Oct: 64.4; Nov: 54.2; Dec: 47.7; Jan: 27.7; Feb: 37.04; Mar: 44.6; Apr: 47.48; May: 59.9; Jun: 65.66; Jul: 67.28; Aug: 69.62; Sep: 65.7; Oct: 54.5; Nov: 47.3; Dec: 33.3
MO | COLUMBIA REGIONAL AIRPORT | Jan: 30.2; Feb: 34.9; Mar: 44.9; Apr: 55.3; May: 64.4; Jun: 73.2; Jul: 77.3; Aug: 76.4; Sep: 67.6; Oct: 56.5; Nov: 44.6; Dec: 33.8; Jan: 17.8; Feb: 21.74; Mar: 35.8; Apr: 43.34; May: 51.3; Jun: 60.8; Jul: 64.76; Aug: 66.2; Sep: 56.3; Oct: 45.5; Nov: 31.1; Dec: 23
MS | COLUMBUS AFB | Jan: 44.3; Feb: 49.2; Mar: 55.5; Apr: 63.2; May: 71.6; Jun: 78.8; Jul: 81.4; Aug: 80.7; Sep: 75.1; Oct: 63.6; Nov: 52.4; Dec: 47.1; Jan: 34; Feb: 35.24; Mar: 36.7; Apr: 44.78; May: 59.5; Jun: 69.8; Jul: 74.3; Aug: 69.98; Sep: 57.4; Oct: 48.74; Nov: 40.3; Dec: 30.6
GA | COLUMBUS METROPOLITAN ARPT | Jan: 48; Feb: 51.6; Mar: 58.1; Apr: 65.2; May: 73.2; Jun: 79.6; Jul: 82.3; Aug: 81.7; Sep: 76.7; Oct: 66.5; Nov: 56.6; Dec: 49.8; Jan: 33.3; Feb: 39.02; Mar: 49.3; Apr: 50.9; May: 60.4; Jun: 68.72; Jul: 70.88; Aug: 68; Sep: 68.4; Oct: 52.88; Nov: 48.7; Dec: 37.8
NE | COLUMBUS MUNI | Jan: 22.3; Feb: 26.6; Mar: 37.8; Apr: 49.4; May: 60.4; Jun: 70.3; Jul: 75.4; Aug: 72.6; Sep: 64.3; Oct: 51.7; Nov: 37.2; Dec: 25.4; Jan: 14; Feb: 19.22; Mar: 16.9; Apr: 35.42; May: 48.4; Jun: 59.36; Jul: 63.5; Aug: 63.5; Sep: 54.9; Oct: 39.92; Nov: 29.8; Dec: 19.9
OH | COLUMBUS PORT COLUMBUS INTL A | Jan: 30; Feb: 32.7; Mar: 41.9; Apr: 53.5; May: 63.1; Jun: 72; Jul: 75.3; Aug: 74.1; Sep: 66.8; Oct: 55.1; Nov: 44; Dec: 34.5; Jan: 20.1; Feb: 19.58; Mar: 31.3; Apr: 39.56; May: 48.6; Jun: 59.36; Jul: 63.86; Aug: 62.42; Sep: 55.4; Oct: 40.28; Nov: 34.3; Dec: 23.5
BC | COMOX AP | Jan: 38.8; Feb: 39.5; Mar: 42.6; Apr: 47.7; May: 54.2; Jun: 59.6; Jul: 64.7; Aug: 64.4; Sep: 58.4; Oct: 49; Nov: 42.4; Dec: 38.5; Jan: 35.8; Feb: 34.34; Mar: 36.1; Apr: 38.84; May: 44.2; Jun: 49.1; Jul: 53.06; Aug: 53.42; Sep: 49.8; Oct: 44.42; Nov: 39; Dec: 35.2
CA | CONCORD CONCORD-BUCHANAN FIEL | Jan: 48.3; Feb: 51.6; Mar: 55.8; Apr: 58.5; May: 64.8; Jun: 69.6; Jul: 72.1; Aug: 71.9; Sep: 70.2; Oct: 63.7; Nov: 54.8; Dec: 48.8; Jan: 41.2; Feb: 40.1; Mar: 42.6; Apr: 46.04; May: 49.3; Jun: 51.08; Jul: 50.72; Aug: 52.7; Sep: 52.5; Oct: 46.58; Nov: 47.3; Dec: 41.2
NH | CONCORD MUNICIPAL ARPT | Jan: 22; Feb: 24.5; Mar: 33.3; Apr: 45.4; May: 56; Jun: 65.5; Jul: 70.4; Aug: 69; Sep: 60.5; Oct: 48.9; Nov: 38.5; Dec: 28.1; Jan: 10.9; Feb: 12.92; Mar: 19.9; Apr: 29.84; May: 45; Jun: 53.96; Jul: 60.44; Aug: 57.02; Sep: 52.7; Oct: 37.76; Nov: 26.8; Dec: 15.1
KS | CONCORDIA BLOSSER MUNI AP | Jan: 29; Feb: 33.1; Mar: 43.3; Apr: 53.1; May: 63.5; Jun: 74; Jul: 79; Aug: 76.9; Sep: 68.2; Oct: 55.9; Nov: 42.1; Dec: 31.1; Jan: 16.2; Feb: 17.06; Mar: 29.5; Apr: 43.34; May: 57.7; Jun: 61.16; Jul: 62.24; Aug: 63.14; Sep: 54; Oct: 41.36; Nov: 34.7; Dec: 25.2
AB | COP UPPER | Jan: 20.5; Feb: 23.1; Mar: 28.7; Apr: 39; May: 48.6; Jun: 54.8; Jul: 61.6; Aug: 60.3; Sep: 52.8; Oct: 41.8; Nov: 29.2; Dec: 22.7; Jan: 9; Feb: 10.4; Mar: 15.1; Apr: 22.28; May: 30; Jun: 40.64; Jul: 45.5; Aug: 42.8; Sep: 35.4; Oct: 25.34; Nov: 16.5; Dec: 10
AK | CORDOVA | Jan: 26; Feb: 28.6; Mar: 30.9; Apr: 38.2; May: 45.5; Jun: 51.4; Jul: 54.5; Aug: 54; Sep: 48.3; Oct: 40.2; Nov: 31.2; Dec: 28.6; Jan: 23.5; Feb: 26.78; Mar: 27.1; Apr: 30.38; May: 35.4; Jun: 44.42; Jul: 48.56; Aug: 46.04; Sep: 39.6; Oct: 28.58; Nov: 24.1; Dec: 19.8
TX | CORPUS CHRISTI INTL ARPT [UT] | Jan: 58.1; Feb: 61.5; Mar: 66.7; Apr: 73; May: 78.5; Jun: 82.9; Jul: 84.1; Aug: 85.1; Sep: 81.4; Oct: 74.8; Nov: 65.9; Dec: 59.4; Jan: 45.9; Feb: 48.92; Mar: 56.8; Apr: 63.86; May: 68; Jun: 74.84; Jul: 74.3; Aug: 73.94; Sep: 71.1; Oct: 64.4; Nov: 59.2; Dec: 47.1
TX | CORPUS CHRISTI NAS | Jan: 58.8; Feb: 62; Mar: 67.1; Apr: 73.1; May: 78.8; Jun: 83.8; Jul: 84.7; Aug: 85.3; Sep: 82.2; Oct: 76.1; Nov: 67.3; Dec: 60.4; Jan: 53.8; Feb: 57.74; Mar: 62.8; Apr: 60.62; May: 70.9; Jun: 74.3; Jul: 76.82; Aug: 75.2; Sep: 75.4; Oct: 67.82; Nov: 63.5; Dec: 50.4
CO | CORTEZ/MONTEZUMA | Jan: 28.1; Feb: 32.3; Mar: 40.1; Apr: 46.7; May: 56.3; Jun: 65.6; Jul: 72.9; Aug: 69.9; Sep: 61.7; Oct: 49; Nov: 37.8; Dec: 28.6; Jan: 21.7; Feb: 22.28; Mar: 24.6; Apr: 25.7; May: 31.1; Jun: 32; Jul: 47.48; Aug: 53.42; Sep: 44.8; Oct: 31.46; Nov: 22.3; Dec: 18
OR | CORVALLIS MUNI | Jan: 41.7; Feb: 43.7; Mar: 47.8; Apr: 51.6; May: 58.1; Jun: 62.8; Jul: 69.4; Aug: 69; Sep: 64; Oct: 54.6; Nov: 46.4; Dec: 41.4; Jan: 36.3; Feb: 37.22; Mar: 42.6; Apr: 35.96; May: 41.7; Jun: 49.46; Jul: 51.62; Aug: 53.06; Sep: 49.8; Oct: 40.1; Nov: 39.4; Dec: 38.5
TX | COTULLA FAA AP | Jan: 55.7; Feb: 59.6; Mar: 66.5; Apr: 74.1; May: 80.2; Jun: 85.7; Jul: 85.6; Aug: 87.2; Sep: 81.5; Oct: 74.3; Nov: 64.4; Dec: 56.2; Jan: 48.4; Feb: 51.8; Mar: 57.6; Apr: 50.54; May: 66.4; Jun: 69.08; Jul: 72.32; Aug: 69.62; Sep: 67.5; Oct: 58.46; Nov: 48.2; Dec: 36.9
IA | COUNCIL BLUFFS | Jan: 25.2; Feb: 29.5; Mar: 40.2; Apr: 52.8; May: 63.4; Jun: 72.8; Jul: 76; Aug: 75.1; Sep: 66.6; Oct: 54.6; Nov: 40.1; Dec: 28.3; Jan: 17.4; Feb: 15.44; Mar: 35.2; Apr: 44.24; May: 46.9; Jun: 65.3; Jul: 65.48; Aug: 68; Sep: 56.3; Oct: 42.44; Nov: 24.4; Dec: 26.8
TX | COX FLD | Jan: 44; Feb: 47.7; Mar: 55.5; Apr: 63.3; May: 71.3; Jun: 79.2; Jul: 82.5; Aug: 83.4; Sep: 75.6; Oct: 64.9; Nov: 53.7; Dec: 45.4; Jan: 30.6; Feb: 31.1; Mar: 32.7; Apr: 44.6; May: 57.7; Jun: 67.46; Jul: 68.72; Aug: 65.84; Sep: 60.1; Oct: 51.62; Nov: 36.5; Dec: 30.9
CO | CRAIG-MOFFAT | Jan: 15.8; Feb: 21.4; Mar: 33.2; Apr: 42.1; May: 51.2; Jun: 59.8; Jul: 67.1; Aug: 65.2; Sep: 56.2; Oct: 43.9; Nov: 30.3; Dec: 18; Jan: 3.9; Feb: 15.8; Mar: 15.6; Apr: 29.66; May: 26.8; Jun: 37.4; Jul: 40.82; Aug: 48.02; Sep: 40.6; Oct: 24.8; Nov: 18.3; Dec: 14.5
BC | CRANBROOK AP | Jan: 21.3; Feb: 26.2; Mar: 35.2; Apr: 43.4; May: 52.1; Jun: 58.3; Jul: 66.4; Aug: 65.1; Sep: 55.9; Oct: 42.2; Nov: 29.7; Dec: 20; Jan: 16; Feb: 17.78; Mar: 23; Apr: 27.86; May: 35.4; Jun: 42.08; Jul: 44.96; Aug: 43.34; Sep: 39.2; Oct: 30.92; Nov: 23.5; Dec: 14.7
MN | CRANE LAKE (AWOS) | Jan: 6.7; Feb: 10.8; Mar: 23.7; Apr: 38; May: 50.8; Jun: 61.2; Jul: 65.3; Aug: 63.5; Sep: 55.1; Oct: 42.3; Nov: 27.5; Dec: 12.8; Jan: -5.8; Feb: 11.12; Mar: 7.5; Apr: 28.58; May: 32.5; Jun: 47.48; Jul: 56.48; Aug: 51.26; Sep: 49.1; Oct: 38.3; Nov: 25.3; Dec: 1.4
CA | CRESCENT CITY FAA AI | Jan: 48; Feb: 48; Mar: 48.5; Apr: 49.5; May: 52.6; Jun: 54.5; Jul: 56.4; Aug: 57.4; Sep: 56.2; Oct: 53.7; Nov: 50.7; Dec: 47.9; Jan: 38.7; Feb: 39.74; Mar: 41.2; Apr: 42.26; May: 46.2; Jun: 50; Jul: 53.06; Aug: 54.86; Sep: 51.8; Oct: 47.84; Nov: 45.1; Dec: 41.4
IA | CRESTON | Jan: 23.9; Feb: 27.3; Mar: 38.5; Apr: 51.2; May: 62.1; Jun: 70.6; Jul: 75.3; Aug: 73.4; Sep: 64.3; Oct: 52.5; Nov: 39.6; Dec: 26.2; Jan: 12.2; Feb: 22.28; Mar: 33.3; Apr: 45.32; May: 51.6; Jun: 63.32; Jul: 66.02; Aug: 67.82; Sep: 53.4; Oct: 43.34; Nov: 29.7; Dec: 20.1
FL | CRESTVIEW BOB SIKES AP | Jan: 50.1; Feb: 52.6; Mar: 58.7; Apr: 65.7; May: 73.1; Jun: 79.9; Jul: 80.9; Aug: 80.9; Sep: 76.8; Oct: 67.3; Nov: 57.3; Dec: 51.6; Jan: 44.2; Feb: 47.66; Mar: 44.4; Apr: 54.5; May: 61.3; Jun: 69.98; Jul: 72.5; Aug: 69.62; Sep: 71.6; Oct: 65.66; Nov: 54.7; Dec: 44.8
MN | CROOKSTON MUNI FLD | Jan: 5.4; Feb: 10.1; Mar: 23.9; Apr: 41.4; May: 53.8; Jun: 64.2; Jul: 68.4; Aug: 66.6; Sep: 57.6; Oct: 43.9; Nov: 27.2; Dec: 12.6; Jan: 8.1; Feb: 10.22; Mar: 21.4; Apr: 34.88; May: 41; Jun: 50.54; Jul: 57.74; Aug: 56.84; Sep: 49.6; Oct: 27.32; Nov: 21.9; Dec: 15.4
TN | CROSSVILLE MEMORIAL AP | Jan: 36.6; Feb: 39.8; Mar: 47.1; Apr: 56.3; May: 63.9; Jun: 71; Jul: 74.4; Aug: 73.7; Sep: 67.5; Oct: 57; Nov: 46.9; Dec: 39.4; Jan: 32.5; Feb: 31.28; Mar: 36.9; Apr: 46.04; May: 55; Jun: 63.32; Jul: 67.46; Aug: 62.42; Sep: 62.1; Oct: 44.06; Nov: 41.9; Dec: 30.2
MT | CUT BANK MUNI AP | Jan: 22.2; Feb: 23.4; Mar: 31; Apr: 40; May: 49.4; Jun: 56.8; Jul: 65; Aug: 63.5; Sep: 54.8; Oct: 42.8; Nov: 30.7; Dec: 22.9; Jan: 14.9; Feb: 13.1; Mar: 17.4; Apr: 25.88; May: 32.4; Jun: 38.3; Jul: 43.16; Aug: 41.72; Sep: 33.8; Oct: 28.76; Nov: 20.7; Dec: 15.6
CA | DAGGETT BARSTOW-DAGGETT AP | Jan: 49.2; Feb: 52.7; Mar: 59.3; Apr: 65.3; May: 74.7; Jun: 83.2; Jul: 89.5; Aug: 88.3; Sep: 81.3; Oct: 69.1; Nov: 56.3; Dec: 47.7; Jan: 26.4; Feb: 26.42; Mar: 31.3; Apr: 33.8; May: 38.3; Jun: 42.08; Jul: 45.14; Aug: 46.4; Sep: 43.5; Oct: 40.1; Nov: 27.3; Dec: 29.7
TX | DALHART MUNICIPAL AP | Jan: 35.7; Feb: 38.9; Mar: 46.5; Apr: 54.7; May: 64.5; Jun: 74.3; Jul: 77.5; Aug: 76.1; Sep: 68.6; Oct: 56.5; Nov: 44.5; Dec: 35.5; Jan: 22.1; Feb: 17.24; Mar: 17.8; Apr: 32.9; May: 40.1; Jun: 55.58; Jul: 57.38; Aug: 55.76; Sep: 49.8; Oct: 41; Nov: 25.5; Dec: 21.7
TX | DALLAS-FORT WORTH INTL AP | Jan: 47; Feb: 51; Mar: 58.1; Apr: 66.1; May: 74.4; Jun: 82.2; Jul: 85.8; Aug: 86.1; Sep: 78.7; Oct: 68.1; Nov: 56.8; Dec: 48.2; Jan: 30.7; Feb: 35.6; Mar: 45.9; Apr: 54.32; May: 62.4; Jun: 64.76; Jul: 70.7; Aug: 70.34; Sep: 62.8; Oct: 47.48; Nov: 45.3; Dec: 28.6
TX | DALLAS-LOVE FIELD | Jan: 48; Feb: 52; Mar: 59; Apr: 67; May: 75; Jun: 83; Jul: 87; Aug: 87; Sep: 80; Oct: 69; Nov: 58; Dec: 49; Jan: 34.9; Feb: 34.88; Mar: 41.7; Apr: 45.68; May: 63.3; Jun: 68; Jul: 69.26; Aug: 67.82; Sep: 66.7; Oct: 58.64; Nov: 38.7; Dec: 40.3
TX | DALLAS/ADDISON ARPT | Jan: 47.9; Feb: 51.8; Mar: 59; Apr: 67; May: 75.1; Jun: 82.9; Jul: 86.6; Aug: 86.9; Sep: 79.4; Oct: 68.8; Nov: 57.4; Dec: 48.9; Jan: 29.5; Feb: 31.28; Mar: 32.9; Apr: 45.5; May: 56.1; Jun: 68.36; Jul: 68.72; Aug: 67.82; Sep: 55.8; Oct: 53.6; Nov: 40.3; Dec: 30.9
TX | DALLAS/REDBIRD ARPT | Jan: 48; Feb: 50.7; Mar: 58.2; Apr: 66.3; May: 74.1; Jun: 81.7; Jul: 85.4; Aug: 86.4; Sep: 78.7; Oct: 68.1; Nov: 57.4; Dec: 48.4; Jan: 35.8; Feb: 31.82; Mar: 48.7; Apr: 57.56; May: 64.6; Jun: 67.1; Jul: 68.54; Aug: 64.4; Sep: 63; Oct: 55.22; Nov: 38.8; Dec: 35.1
CT | DANBURY MUNICIPAL | Jan: 26.8; Feb: 29.4; Mar: 37.6; Apr: 48.9; May: 58.1; Jun: 67; Jul: 71.7; Aug: 70.2; Sep: 63.4; Oct: 51.9; Nov: 42.2; Dec: 32.6; Jan: 16; Feb: 15.08; Mar: 31.5; Apr: 35.42; May: 43.3; Jun: 59; Jul: 61.52; Aug: 59.9; Sep: 54.7; Oct: 42.98; Nov: 36; Dec: 27.7
VA | DANVILLE FAA AP | Jan: 39.6; Feb: 42; Mar: 49.4; Apr: 58.7; May: 66.6; Jun: 74.6; Jul: 78; Aug: 77.2; Sep: 70; Oct: 59.3; Nov: 49.1; Dec: 41.7; Jan: 25.2; Feb: 34.34; Mar: 35.4; Apr: 45.32; May: 55.2; Jun: 64.58; Jul: 66.92; Aug: 69.08; Sep: 61.2; Oct: 49.28; Nov: 32.9; Dec: 34.7
NC | DARE CO RGNL | Jan: 43.9; Feb: 45.5; Mar: 51.2; Apr: 60.2; May: 68.1; Jun: 76.6; Jul: 80.6; Aug: 79.7; Sep: 74.6; Oct: 65.5; Nov: 55.7; Dec: 48.4; Jan: 31.5; Feb: 30.38; Mar: 35.2; Apr: 42.8; May: 53.2; Jun: 65.48; Jul: 74.48; Aug: 68.72; Sep: 62.2; Oct: 57.2; Nov: 49.6; Dec: 46.2
AZ | DAVIS MONTHAN AFB | Jan: 53.1; Feb: 55.2; Mar: 60.8; Apr: 67; May: 76.1; Jun: 85.2; Jul: 86.9; Aug: 85.6; Sep: 82.2; Oct: 71.9; Nov: 60.8; Dec: 52.4; Jan: 30.6; Feb: 43.34; Mar: 35.4; Apr: 24.62; May: 23.2; Jun: 32.36; Jul: 49.82; Aug: 51.98; Sep: 52.5; Oct: 34.88; Nov: 34.7; Dec: 21.4
VA | DAVISON AAF | Jan: 35.8; Feb: 39.1; Mar: 46; Apr: 56.6; May: 65; Jun: 73.7; Jul: 78.6; Aug: 76.3; Sep: 69.4; Oct: 57.7; Nov: 47; Dec: 39.2; Jan: 21.9; Feb: 24.98; Mar: 27; Apr: 33.8; May: 50.2; Jun: 64.4; Jul: 68.9; Aug: 65.84; Sep: 61.9; Oct: 47.3; Nov: 33.1; Dec: 31.3
OH | DAYTON INTERNATIONAL AIRPORT | Jan: 28.3; Feb: 31.5; Mar: 40.9; Apr: 52.4; May: 62.3; Jun: 71.2; Jul: 74.4; Aug: 73; Sep: 65.7; Oct: 54.4; Nov: 42.9; Dec: 32.8; Jan: 17.2; Feb: 19.22; Mar: 30.6; Apr: 38.48; May: 47.3; Jun: 58.82; Jul: 66.02; Aug: 63.5; Sep: 57; Oct: 40.64; Nov: 32.2; Dec: 24.3
FL | DAYTONA BEACH INTL AP | Jan: 59; Feb: 61.1; Mar: 64.7; Apr: 69.7; May: 75.5; Jun: 79.9; Jul: 81.5; Aug: 81.6; Sep: 79.8; Oct: 74.1; Nov: 66.5; Dec: 61.4; Jan: 47.3; Feb: 50; Mar: 55.9; Apr: 58.1; May: 65.8; Jun: 71.24; Jul: 72.32; Aug: 73.22; Sep: 71.2; Oct: 62.42; Nov: 58.5; Dec: 52.7
AK | DEADHORSE | Jan: -15.9; Feb: -16.6; Mar: -14.8; Apr: 3.2; May: 23.4; Jun: 40; Jul: 47.3; Aug: 43.8; Sep: 34.5; Oct: 17.8; Nov: 0.1; Dec: -10; Jan: -15.7; Feb: -27.76; Mar: -23.1; Apr: 5.18; May: 25.3; Jun: 35.6; Jul: 36.86; Aug: 35.24; Sep: 32; Oct: 21.56; Nov: 5.9; Dec: -7.4
IL | DECATUR | Jan: 27.8; Feb: 31.8; Mar: 42.1; Apr: 53.4; May: 63.6; Jun: 72.4; Jul: 75.9; Aug: 74; Sep: 66.8; Oct: 55.2; Nov: 42.8; Dec: 32; Jan: 23.7; Feb: 28.76; Mar: 33.8; Apr: 47.12; May: 55.4; Jun: 62.96; Jul: 62.24; Aug: 70.88; Sep: 55.4; Oct: 43.34; Nov: 30.6; Dec: 21.6
IA | DECORAH | Jan: 19.9; Feb: 23.1; Mar: 35.4; Apr: 48.8; May: 59.5; Jun: 69.1; Jul: 72.9; Aug: 69.8; Sep: 62.3; Oct: 50.9; Nov: 37.6; Dec: 23.8; Jan: 13.1; Feb: 22.82; Mar: 33.8; Apr: 40.46; May: 50.7; Jun: 59.9; Jul: 63.32; Aug: 66.02; Sep: 55.2; Oct: 37.94; Nov: 27.5; Dec: 18.5
AZ | DEER VALLEY/PHOENIX | Jan: 55.1; Feb: 56.8; Mar: 63; Apr: 69.4; May: 79.3; Jun: 88.3; Jul: 92.8; Aug: 91.2; Sep: 86.4; Oct: 74.6; Nov: 63; Dec: 53.6; Jan: 36.7; Feb: 36.86; Mar: 35.1; Apr: 32.72; May: 30.2; Jun: 42.8; Jul: 57.92; Aug: 50; Sep: 48.9; Oct: 43.52; Nov: 33.4; Dec: 19.8
GA | DEKALB PEACHTREE | Jan: 42.9; Feb: 46.4; Mar: 53.6; Apr: 61.9; May: 69.9; Jun: 77.2; Jul: 79.7; Aug: 79.5; Sep: 73.2; Oct: 62.6; Nov: 52.6; Dec: 45; Jan: 26.4; Feb: 33.98; Mar: 35.2; Apr: 44.24; May: 58.5; Jun: 65.12; Jul: 69.62; Aug: 68.72; Sep: 65.1; Oct: 44.6; Nov: 36.9; Dec: 31.1
TX | DEL RIO [UT] | Jan: 53.2; Feb: 57.9; Mar: 65.2; Apr: 72.7; May: 79.5; Jun: 85.2; Jul: 86.3; Aug: 86.7; Sep: 80.7; Oct: 72.2; Nov: 60.9; Dec: 53.3; Jan: 42.1; Feb: 47.3; Mar: 34.3; Apr: 51.44; May: 64.9; Jun: 66.2; Jul: 68; Aug: 67.28; Sep: 61.7; Oct: 62.24; Nov: 49.3; Dec: 38.5
TX | DEL RIO LAUGHLIN AFB | Jan: 54; Feb: 59.5; Mar: 65.7; Apr: 73.1; May: 80.1; Jun: 85.9; Jul: 86.9; Aug: 87.4; Sep: 81.2; Oct: 72.6; Nov: 61.5; Dec: 54.5; Jan: 41.7; Feb: 41.72; Mar: 55.2; Apr: 57.2; May: 61.9; Jun: 68.36; Jul: 65.84; Aug: 69.08; Sep: 65.1; Oct: 55.58; Nov: 49.1; Dec: 43.2
IN | DELAWARE CO JOHNSON | Jan: 27.1; Feb: 29.3; Mar: 41; Apr: 53; May: 62.9; Jun: 71.4; Jul: 73.7; Aug: 71.8; Sep: 65.1; Oct: 54; Nov: 43.1; Dec: 31.4; Jan: 20.1; Feb: 23.18; Mar: 26.6; Apr: 40.82; May: 48.7; Jun: 56.48; Jul: 63.68; Aug: 65.48; Sep: 56.7; Oct: 45.32; Nov: 36.5; Dec: 27
NM | DEMING MUNI | Jan: 42.4; Feb: 45.9; Mar: 53.3; Apr: 60.8; May: 69.4; Jun: 79.3; Jul: 80.9; Aug: 78.7; Sep: 72.8; Oct: 62.3; Nov: 50.2; Dec: 42.1; Jan: 24.8; Feb: 23; Mar: 19.8; Apr: 19.76; May: 27.7; Jun: 40.46; Jul: 49.1; Aug: 54.68; Sep: 40.8; Oct: 34.52; Nov: 24.6; Dec: 21.4
IA | DENISON | Jan: 22.8; Feb: 26.1; Mar: 37.4; Apr: 50.2; May: 60.5; Jun: 71; Jul: 75.2; Aug: 72.3; Sep: 64.6; Oct: 51.7; Nov: 38.5; Dec: 25.1; Jan: 17.8; Feb: 14.36; Mar: 27.3; Apr: 38.48; May: 49.5; Jun: 58.82; Jul: 67.82; Aug: 62.06; Sep: 59.9; Oct: 43.88; Nov: 27.5; Dec: 19.9
CO | DENVER INTL AP | Jan: 31.6; Feb: 32.3; Mar: 41; Apr: 47.3; May: 57.1; Jun: 67.5; Jul: 74.9; Aug: 72.8; Sep: 63.8; Oct: 51; Nov: 40.1; Dec: 30.9; Jan: 13.3; Feb: 15.98; Mar: 17.8; Apr: 27.5; May: 38.8; Jun: 43.88; Jul: 49.1; Aug: 46.94; Sep: 37.4; Oct: 34.34; Nov: 19.4; Dec: 15.6
CO | DENVER/CENTENNIAL [GOLDEN - NREL] | Jan: 31.7; Feb: 32.8; Mar: 40.4; Apr: 46.3; May: 56.2; Jun: 66.6; Jul: 72.7; Aug: 70.7; Sep: 62.4; Oct: 50; Nov: 39.5; Dec: 31.2; Jan: 16; Feb: 17.96; Mar: 25; Apr: 29.3; May: 32.5; Jun: 46.4; Jul: 47.84; Aug: 46.4; Sep: 39.4; Oct: 32; Nov: 22.8; Dec: 13.8
IA | DES MOINES INTL AP | Jan: 22.7; Feb: 27.6; Mar: 39.4; Apr: 51.5; May: 62.2; Jun: 71.8; Jul: 76; Aug: 74.2; Sep: 65.8; Oct: 53.6; Nov: 39.5; Dec: 27.3; Jan: 9.7; Feb: 13.82; Mar: 26.2; Apr: 34.52; May: 45.1; Jun: 58.46; Jul: 66.02; Aug: 65.3; Sep: 53.8; Oct: 34.52; Nov: 30.2; Dec: 16.7
MI | DETROIT CITY AIRPORT | Jan: 26.7; Feb: 28.7; Mar: 37.2; Apr: 49; May: 60; Jun: 70.2; Jul: 74.4; Aug: 72.7; Sep: 65; Oct: 53.5; Nov: 42; Dec: 31.8; Jan: 17.6; Feb: 15.44; Mar: 24.8; Apr: 29.84; May: 41.5; Jun: 55.58; Jul: 60.44; Aug: 65.48; Sep: 49.5; Oct: 41.36; Nov: 36; Dec: 22.3
MN | DETROIT LAKES(AWOS) | Jan: 9.1; Feb: 13.8; Mar: 26.4; Apr: 42.1; May: 54.8; Jun: 64.8; Jul: 69.6; Aug: 67.9; Sep: 59.1; Oct: 45.5; Nov: 29.8; Dec: 15.9; Jan: 6.6; Feb: 11.84; Mar: 16.9; Apr: 31.82; May: 46.6; Jun: 53.24; Jul: 58.82; Aug: 60.08; Sep: 51.4; Oct: 30.02; Nov: 25.2; Dec: 16
MI | DETROIT METROPOLITAN ARPT | Jan: 26; Feb: 28.2; Mar: 37.3; Apr: 49.2; May: 60; Jun: 69.9; Jul: 73.6; Aug: 72.1; Sep: 64.5; Oct: 52.9; Nov: 41.4; Dec: 31.1; Jan: 15.8; Feb: 16.34; Mar: 25.5; Apr: 34.16; May: 45.5; Jun: 55.76; Jul: 63.14; Aug: 61.16; Sep: 55.2; Oct: 41.54; Nov: 30.7; Dec: 22.6
MI | DETROIT WILLOW RUN AP | Jan: 24.8; Feb: 26.7; Mar: 36.2; Apr: 48.3; May: 59.4; Jun: 69; Jul: 72.9; Aug: 71; Sep: 63.2; Oct: 51.9; Nov: 40.6; Dec: 30.2; Jan: 17.2; Feb: 23.9; Mar: 19.4; Apr: 36.32; May: 49.3; Jun: 61.16; Jul: 63.14; Aug: 59.36; Sep: 55.9; Oct: 43.16; Nov: 32.4; Dec: 18.3
ND | DEVILS LAKE(AWOS) | Jan: 6.9; Feb: 10.9; Mar: 23.5; Apr: 39.8; May: 52.8; Jun: 63; Jul: 67.8; Aug: 66.7; Sep: 57.7; Oct: 43.3; Nov: 27.2; Dec: 12.3; Jan: -2.7; Feb: 9.14; Mar: 8.1; Apr: 30.74; May: 31.1; Jun: 51.26; Jul: 51.44; Aug: 55.04; Sep: 46.2; Oct: 37.4; Nov: 26.6; Dec: 8.4
ND | DICKINSON MUNICIPAL AP | Jan: 16.5; Feb: 20.5; Mar: 30; Apr: 41.8; May: 52.8; Jun: 61.9; Jul: 69.2; Aug: 68.7; Sep: 58.6; Oct: 44.2; Nov: 30; Dec: 19.3; Jan: 5; Feb: 13.28; Mar: 19.9; Apr: 32; May: 41.2; Jun: 42.62; Jul: 58.28; Aug: 53.24; Sep: 41; Oct: 31.28; Nov: 17.1; Dec: 5.7
NH | DILLANT HOPKINS | Jan: 21.9; Feb: 24.4; Mar: 33.4; Apr: 44.9; May: 55.6; Jun: 65; Jul: 69.4; Aug: 67.8; Sep: 60; Oct: 48.2; Nov: 38.2; Dec: 28.2; Jan: 7.7; Feb: 15.08; Mar: 20.7; Apr: 32.36; May: 40.5; Jun: 52.34; Jul: 55.58; Aug: 58.1; Sep: 54; Oct: 38.12; Nov: 31.8; Dec: 16
AK | DILLINGHAM (AMOS) | Jan: 14.5; Feb: 19.1; Mar: 21.3; Apr: 32.4; May: 43.2; Jun: 50.8; Jul: 54.7; Aug: 53.8; Sep: 47.1; Oct: 34.8; Nov: 22.4; Dec: 17.2; Jan: 16.3; Feb: 28.94; Mar: 23.9; Apr: 26.96; May: 29.5; Jun: 39.2; Jul: 45.86; Aug: 47.66; Sep: 32.4; Oct: 19.22; Nov: 18.9; Dec: 14
BC | DISCOVERY ISLAND | Jan: 44.1; Feb: 44.6; Mar: 46.1; Apr: 49.5; May: 53.5; Jun: 56.9; Jul: 59.3; Aug: 59.7; Sep: 58; Oct: 52.5; Nov: 47.5; Dec: 44.2; Jan: 36.3; Feb: 35.96; Mar: 38.5; Apr: 40.46; May: 45.1; Jun: 49.1; Jul: 52.7; Aug: 53.24; Sep: 50.7; Oct: 45.86; Nov: 41; Dec: 36
KS | DODGE CITY REGIONAL AP | Jan: 32.5; Feb: 36; Mar: 44.7; Apr: 53.9; May: 64.5; Jun: 74.6; Jul: 79.6; Aug: 77.9; Sep: 69.2; Oct: 56.7; Nov: 43.3; Dec: 33.3; Jan: 15.8; Feb: 23; Mar: 30; Apr: 40.1; May: 49.1; Jun: 58.64; Jul: 60.44; Aug: 60.62; Sep: 53.8; Oct: 39.2; Nov: 27; Dec: 20.1
AL | DOTHAN MUNICIPAL AP | Jan: 50.5; Feb: 53.8; Mar: 59.8; Apr: 66.5; May: 74.8; Jun: 80.5; Jul: 82; Aug: 81.4; Sep: 77.3; Oct: 67.9; Nov: 58.1; Dec: 52.3; Jan: 29.7; Feb: 35.24; Mar: 52.3; Apr: 49.46; May: 61; Jun: 68.54; Jul: 70.88; Aug: 72.86; Sep: 71.6; Oct: 52.34; Nov: 47.3; Dec: 35.6
AZ | DOUGLAS BISBEE-DOUGLAS INTL A | Jan: 46.4; Feb: 49.5; Mar: 55; Apr: 61.6; May: 70.2; Jun: 78.9; Jul: 80.1; Aug: 78.1; Sep: 74.6; Oct: 64.8; Nov: 53.8; Dec: 46.1; Jan: 27; Feb: 25.16; Mar: 34.5; Apr: 22.1; May: 27.3; Jun: 35.96; Jul: 58.28; Aug: 57.56; Sep: 45.7; Oct: 39.02; Nov: 28.8; Dec: 24.3
DE | DOVER AFB | Jan: 34.9; Feb: 37; Mar: 44.2; Apr: 53.9; May: 63.2; Jun: 72.4; Jul: 77.2; Aug: 75.3; Sep: 68.6; Oct: 57.8; Nov: 47.5; Dec: 39.4; Jan: 25.7; Feb: 24.62; Mar: 26.4; Apr: 38.3; May: 45.5; Jun: 61.34; Jul: 68.54; Aug: 65.12; Sep: 56.5; Oct: 45.5; Nov: 32.5; Dec: 28.9
TX | DRAUGHON MILLER CEN | Jan: 48.8; Feb: 52.1; Mar: 58.9; Apr: 67.1; May: 74.5; Jun: 81.3; Jul: 83.9; Aug: 84.4; Sep: 78.1; Oct: 68.6; Nov: 57.5; Dec: 49.8; Jan: 34.5; Feb: 34.16; Mar: 35.2; Apr: 45.68; May: 66.7; Jun: 69.8; Jul: 69.26; Aug: 67.1; Sep: 58.6; Oct: 48.74; Nov: 45.5; Dec: 38.5
PA | DUBOIS FAA AP | Jan: 25.1; Feb: 26.7; Mar: 35.4; Apr: 47.3; May: 56.9; Jun: 65; Jul: 68.8; Aug: 67.4; Sep: 60.3; Oct: 49.8; Nov: 39.4; Dec: 29.6; Jan: 20.1; Feb: 16.16; Mar: 28.6; Apr: 30.92; May: 42.8; Jun: 54.5; Jul: 53.78; Aug: 60.26; Sep: 48.4; Oct: 39.38; Nov: 30.6; Dec: 22.8
IA | DUBUQUE REGIONAL AP | Jan: 19.2; Feb: 23.7; Mar: 35.5; Apr: 47.8; May: 58.8; Jun: 68.4; Jul: 71.7; Aug: 70.1; Sep: 62; Oct: 50.1; Nov: 36.7; Dec: 24.1; Jan: 10.9; Feb: 15.26; Mar: 27.5; Apr: 33.8; May: 46.4; Jun: 58.28; Jul: 62.6; Aug: 62.24; Sep: 55.8; Oct: 37.4; Nov: 21.6; Dec: 15.3
MN | DULUTH INTERNATIONAL ARPT | Jan: 10.9; Feb: 15.6; Mar: 26.4; Apr: 39.2; May: 51.2; Jun: 60.5; Jul: 65.9; Aug: 64.9; Sep: 56.3; Oct: 43.7; Nov: 29.4; Dec: 16.3; Jan: 2.3; Feb: 7.88; Mar: 17.4; Apr: 25.88; May: 40.5; Jun: 52.16; Jul: 55.22; Aug: 55.94; Sep: 47.8; Oct: 34.16; Nov: 16.9; Dec: 3.2
CO | DURANGO/LA PLATA CO | Jan: 24.8; Feb: 29.2; Mar: 38.1; Apr: 45; May: 53.8; Jun: 63.5; Jul: 70.4; Aug: 67.7; Sep: 59.9; Oct: 47.8; Nov: 36.5; Dec: 26.4; Jan: 19.4; Feb: 20.3; Mar: 15.6; Apr: 21.38; May: 29.1; Jun: 33.62; Jul: 48.56; Aug: 48.92; Sep: 46.8; Oct: 27.14; Nov: 21.6; Dec: 10.8
AK | DUTCH HARBOR | Jan: 33.3; Feb: 33.8; Mar: 33.8; Apr: 36.6; May: 41.1; Jun: 46.4; Jul: 51.1; Aug: 53; Sep: 49.1; Oct: 43; Nov: 38.2; Dec: 35.1; Jan: 29.7; Feb: 26.78; Mar: 23.9; Apr: 29.66; May: 31.5; Jun: 36.5; Jul: 44.42; Aug: 46.58; Sep: 38.5; Oct: 32.18; Nov: 31.1; Dec: 24.6
TN | DYERSBURG MUNICIPAL AP | Jan: 38.8; Feb: 42.1; Mar: 50.5; Apr: 60.4; May: 69.3; Jun: 77.4; Jul: 79.7; Aug: 79.2; Sep: 71.4; Oct: 61; Nov: 49.4; Dec: 40.9; Jan: 28.2; Feb: 29.84; Mar: 31.6; Apr: 42.08; May: 51.4; Jun: 67.64; Jul: 68.9; Aug: 63.68; Sep: 63.9; Oct: 49.64; Nov: 40.3; Dec: 30.7
CO | EAGLE COUNTY AP | Jan: 22.8; Feb: 27.1; Mar: 36.1; Apr: 42.9; May: 52.6; Jun: 60.3; Jul: 66.7; Aug: 64.8; Sep: 56.5; Oct: 45.4; Nov: 31.1; Dec: 21.4; Jan: 9.9; Feb: 13.82; Mar: 21.6; Apr: 24.62; May: 28.4; Jun: 31.82; Jul: 47.12; Aug: 41.18; Sep: 33.1; Oct: 26.06; Nov: 22.1; Dec: 12
WI | EAU CLAIRE COUNTY AP | Jan: 15.1; Feb: 19.7; Mar: 31.5; Apr: 45.5; May: 57.4; Jun: 67.2; Jul: 71.3; Aug: 69.4; Sep: 60.7; Oct: 47.9; Nov: 33.6; Dec: 20.4; Jan: 3.4; Feb: 8.6; Mar: 21.9; Apr: 30.38; May: 41.2; Jun: 53.96; Jul: 61.52; Aug: 58.46; Sep: 51.3; Oct: 36.68; Nov: 25; Dec: 8.1
AB | EDMONTON AP | Jan: 9.8; Feb: 14.1; Mar: 22.7; Apr: 38.5; May: 49.9; Jun: 57.1; Jul: 61; Aug: 59.2; Sep: 51.1; Oct: 38.4; Nov: 22.4; Dec: 11.7; Jan: 4.5; Feb: 6.62; Mar: 13.5; Apr: 24.62; May: 32.5; Jun: 44.42; Jul: 51.44; Aug: 48.74; Sep: 39.4; Oct: 27.68; Nov: 17.8; Dec: 5
AB | EDMONTON MUN AP | Jan: 13.3; Feb: 18.3; Mar: 26.5; Apr: 40.8; May: 52.3; Jun: 59.7; Jul: 64.3; Aug: 62.5; Sep: 53.9; Oct: 41.1; Nov: 25.4; Dec: 15.1; Jan: 5.5; Feb: 8.6; Mar: 13.6; Apr: 23.54; May: 32.7; Jun: 44.96; Jul: 51.8; Aug: 49.1; Sep: 40.3; Oct: 28.04; Nov: 18.1; Dec: 5.4
AB | EDMONTON NAMAO | Jan: 12.9; Feb: 15; Mar: 24.7; Apr: 38.8; May: 50.4; Jun: 57.7; Jul: 62.1; Aug: 60.3; Sep: 52; Oct: 39.3; Nov: 24.1; Dec: 12.8; Jan: 5; Feb: 7.7; Mar: 13.3; Apr: 23.54; May: 32; Jun: 44.78; Jul: 52.16; Aug: 49.46; Sep: 40.5; Oct: 28.4; Nov: 18.3; Dec: 5.5
CA | EDWARDS AFB | Jan: 45.1; Feb: 48.3; Mar: 54.5; Apr: 60; May: 68; Jun: 76.4; Jul: 83.1; Aug: 82.4; Sep: 75.6; Oct: 63; Nov: 52; Dec: 43.6; Jan: 29.5; Feb: 30.02; Mar: 32; Apr: 31.1; May: 34.9; Jun: 38.66; Jul: 41.9; Aug: 37.22; Sep: 33.4; Oct: 32.36; Nov: 30.9; Dec: 28.6
AR | EL DORADO GOODWIN FIELD | Jan: 44.8; Feb: 48.1; Mar: 55.8; Apr: 63.7; May: 71.5; Jun: 78.8; Jul: 82; Aug: 81.8; Sep: 75; Oct: 64.1; Nov: 53.3; Dec: 46.4; Jan: 37.2; Feb: 31.46; Mar: 50.4; Apr: 52.34; May: 66.9; Jun: 69.8; Jul: 72.14; Aug: 68.72; Sep: 69.3; Oct: 49.28; Nov: 50.7; Dec: 35.6
TX | EL PASO INTERNATIONAL AP [UT] | Jan: 46.3; Feb: 50.9; Mar: 57.9; Apr: 66; May: 75.1; Jun: 83.5; Jul: 83.3; Aug: 81.7; Sep: 76; Oct: 66.1; Nov: 53.7; Dec: 45.7; Jan: 26.6; Feb: 23.72; Mar: 22.1; Apr: 27.14; May: 36.7; Jun: 42.62; Jul: 58.28; Aug: 53.6; Sep: 52.2; Oct: 45.14; Nov: 29.3; Dec: 23.4
NC | ELIZABETH CITY COAST GUARD AI [NREL] | Jan: 42.3; Feb: 44.6; Mar: 51; Apr: 60.2; May: 68.4; Jun: 76.3; Jul: 79.2; Aug: 78.5; Sep: 72.9; Oct: 63.1; Nov: 53.4; Dec: 45.9; Jan: 37.8; Feb: 34.7; Mar: 41.5; Apr: 50.9; May: 59; Jun: 67.1; Jul: 73.22; Aug: 67.64; Sep: 65.7; Oct: 53.96; Nov: 45.9; Dec: 40.8
WV | ELKINS ELKINS-RANDOLPH CO ARP | Jan: 30.3; Feb: 32.4; Mar: 40.1; Apr: 50.6; May: 58.7; Jun: 66.6; Jul: 70.2; Aug: 69.4; Sep: 62.5; Oct: 51.4; Nov: 41.4; Dec: 33.7; Jan: 16.3; Feb: 24.44; Mar: 30.9; Apr: 36.14; May: 47.5; Jun: 58.28; Jul: 62.6; Aug: 61.7; Sep: 54.3; Oct: 38.48; Nov: 34.3; Dec: 24.4
NV | ELKO MUNICIPAL ARPT | Jan: 25.7; Feb: 30.1; Mar: 38.9; Apr: 44.8; May: 53.3; Jun: 61.8; Jul: 70.7; Aug: 68.4; Sep: 59.6; Oct: 46.7; Nov: 34.9; Dec: 26; Jan: 15.4; Feb: 23.36; Mar: 24.6; Apr: 28.94; May: 33.6; Jun: 33.08; Jul: 33.26; Aug: 32.54; Sep: 28.8; Oct: 25.7; Nov: 21.4; Dec: 17.2
SD | ELLSWORTH AFB | Jan: 25.3; Feb: 28.3; Mar: 35.9; Apr: 44.6; May: 54.8; Jun: 64.9; Jul: 72.1; Aug: 72.6; Sep: 62.7; Oct: 48.1; Nov: 35.1; Dec: 25.5; Jan: 13.5; Feb: 24.08; Mar: 23.2; Apr: 28.76; May: 36.5; Jun: 48.02; Jul: 50.72; Aug: 49.46; Sep: 37.8; Oct: 29.84; Nov: 27.3; Dec: 17.2
NY | ELMIRA CORNING REGIONAL AP | Jan: 24.8; Feb: 26.4; Mar: 34.4; Apr: 46.2; May: 56.9; Jun: 66; Jul: 69.9; Aug: 68.5; Sep: 60.9; Oct: 49.7; Nov: 39.1; Dec: 30; Jan: 19.8; Feb: 20.48; Mar: 27.5; Apr: 36.86; May: 39.6; Jun: 58.28; Jul: 60.98; Aug: 60.26; Sep: 53.6; Oct: 42.8; Nov: 31.3; Dec: 22.6
MN | ELY MUNI | Jan: 6.4; Feb: 11.3; Mar: 23.8; Apr: 37.7; May: 50.4; Jun: 60.5; Jul: 64.7; Aug: 63; Sep: 54.7; Oct: 42.2; Nov: 27.5; Dec: 13.2; Jan: -10.8; Feb: 7.7; Mar: 19; Apr: 30.56; May: 42.4; Jun: 49.28; Jul: 54.32; Aug: 58.1; Sep: 52.3; Oct: 35.6; Nov: 19; Dec: 14.2
NV | ELY YELLAND FIELD | Jan: 26.2; Feb: 29.1; Mar: 36.9; Apr: 42.5; May: 50.8; Jun: 60.1; Jul: 68.5; Aug: 66.6; Sep: 57.8; Oct: 46; Nov: 34.5; Dec: 25.9; Jan: 13.3; Feb: 19.22; Mar: 22.3; Apr: 19.58; May: 28.4; Jun: 27.32; Jul: 37.58; Aug: 36.14; Sep: 30.4; Oct: 26.96; Nov: 15.6; Dec: 11.1
AK | EMMONAK | Jan: 7.6; Feb: 10.3; Mar: 10.2; Apr: 21.7; May: 36.3; Jun: 49.6; Jul: 53; Aug: 52.2; Sep: 44.9; Oct: 32; Nov: 19.6; Dec: 9.2; Jan: 4.6; Feb: 8.96; Mar: 18.7; Apr: 24.98; May: 33.1; Jun: 40.64; Jul: 44.24; Aug: 43.34; Sep: 34.5; Oct: 29.66; Nov: 22.1; Dec: 14.4
KS | EMPORIA MUNICIPAL AP | Jan: 31.5; Feb: 35.3; Mar: 45.2; Apr: 55.9; May: 65.5; Jun: 74; Jul: 79.3; Aug: 78.3; Sep: 69.1; Oct: 57.5; Nov: 45.2; Dec: 33.7; Jan: 16.5; Feb: 24.62; Mar: 22.5; Apr: 45.5; May: 57.6; Jun: 65.48; Jul: 67.1; Aug: 65.84; Sep: 59.7; Oct: 43.88; Nov: 31.5; Dec: 13.8
LA | ENGLAND AFB | Jan: 50.1; Feb: 53.3; Mar: 59.9; Apr: 67.1; May: 75.1; Jun: 80.9; Jul: 82.5; Aug: 82.9; Sep: 77.8; Oct: 67.5; Nov: 57.5; Dec: 51; Jan: 43.3; Feb: 38.12; Mar: 54; Apr: 57.56; May: 63.3; Jun: 67.28; Jul: 73.4; Aug: 67.28; Sep: 64.8; Oct: 60.98; Nov: 51.1; Dec: 41.4
BC | ENTRANCE ISLAND | Jan: 42.1; Feb: 42.8; Mar: 45.1; Apr: 49.3; May: 54.9; Jun: 60; Jul: 64.6; Aug: 64.8; Sep: 60; Oct: 51.8; Nov: 45.8; Dec: 42.2; Jan: 34.9; Feb: 33.98; Mar: 36.5; Apr: 39.38; May: 44.8; Jun: 49.46; Jul: 53.78; Aug: 53.78; Sep: 50.2; Oct: 44.6; Nov: 38.8; Dec: 34.3
WA | EPHRATA AP FCWOS | Jan: 29.5; Feb: 35.1; Mar: 43.1; Apr: 50.2; May: 59.5; Jun: 67.1; Jul: 76.5; Aug: 73.9; Sep: 65.3; Oct: 51.3; Nov: 37.4; Dec: 29.7; Jan: 24.1; Feb: 26.6; Mar: 30.4; Apr: 32.9; May: 41; Jun: 44.78; Jul: 45.68; Aug: 44.06; Sep: 41; Oct: 33.08; Nov: 30.4; Dec: 28.2
PA | ERIE INTERNATIONAL AP | Jan: 28.2; Feb: 28.5; Mar: 35.8; Apr: 47.3; May: 58; Jun: 67.7; Jul: 71.9; Aug: 70.7; Sep: 63.9; Oct: 53.5; Nov: 43.1; Dec: 33.4; Jan: 18.3; Feb: 17.78; Mar: 22.5; Apr: 37.22; May: 48.6; Jun: 55.58; Jul: 59.54; Aug: 59.54; Sep: 53.8; Oct: 41.54; Nov: 34.2; Dec: 20.3
ON | ERIEAU | Jan: 25.9; Feb: 26.4; Mar: 32.7; Apr: 43.4; May: 54.3; Jun: 65.4; Jul: 70.6; Aug: 70.5; Sep: 64.3; Oct: 53.3; Nov: 42.3; Dec: 32.2; Jan: 17.1; Feb: 18.86; Mar: 25.9; Apr: 34.52; May: 45.1; Jun: 57.2; Jul: 62.06; Aug: 62.6; Sep: 56.3; Oct: 44.24; Nov: 36; Dec: 21.4
MI | ESCANABA (AWOS) | Jan: 17.8; Feb: 19; Mar: 27.8; Apr: 39.2; May: 50.7; Jun: 60.8; Jul: 65.4; Aug: 64.5; Sep: 57; Oct: 45.7; Nov: 34.7; Dec: 24; Jan: 14.4; Feb: 16.88; Mar: 16.2; Apr: 30.92; May: 32.4; Jun: 49.64; Jul: 56.84; Aug: 52.7; Sep: 45.5; Oct: 35.06; Nov: 27.5; Dec: 18.9
BC | ESQUIMALT HARBOUR | Jan: 41.6; Feb: 42.3; Mar: 44.4; Apr: 48.1; May: 52.9; Jun: 56.9; Jul: 60.3; Aug: 60.1; Sep: 56.6; Oct: 50.3; Nov: 44.9; Dec: 41.4; Jan: 36.5; Feb: 36.14; Mar: 38.8; Apr: 40.82; May: 45.5; Jun: 49.46; Jul: 52.7; Aug: 53.42; Sep: 51.1; Oct: 46.4; Nov: 41.4; Dec: 36
IA | ESTHERVILLE MUNI | Jan: 15.9; Feb: 20.3; Mar: 32.7; Apr: 47; May: 58.7; Jun: 68.1; Jul: 72.3; Aug: 69; Sep: 61.7; Oct: 49; Nov: 34.6; Dec: 20.8; Jan: 7; Feb: 10.22; Mar: 17.2; Apr: 38.3; May: 48.4; Jun: 56.84; Jul: 62.24; Aug: 61.34; Sep: 53.1; Oct: 35.42; Nov: 24.3; Dec: 2.7
OR | EUGENE MAHLON SWEET ARPT [UO] | Jan: 41.2; Feb: 43.2; Mar: 46.9; Apr: 50.3; May: 55.5; Jun: 60.4; Jul: 67.8; Aug: 67.7; Sep: 63.1; Oct: 53.2; Nov: 45.4; Dec: 40.3; Jan: 38.7; Feb: 36.5; Mar: 41; Apr: 42.98; May: 47.5; Jun: 50.36; Jul: 51.98; Aug: 53.06; Sep: 48.9; Oct: 44.96; Nov: 39; Dec: 37.8
WY | EVANSTON-UINTA COUNTY AP-BURNS FIELD | Jan: 22; Feb: 24; Mar: 32; Apr: 40; May: 49; Jun: 59; Jul: 69; Aug: 66; Sep: 57; Oct: 44; Nov: 32; Dec: 22; Jan: 10.6; Feb: 15.98; Mar: 22.6; Apr: 23.18; May: 28.9; Jun: 31.1; Jul: 36.32; Aug: 42.8; Sep: 40.1; Oct: 25.16; Nov: 21.7; Dec: 15.1
IN | EVANSVILLE REGIONAL AP | Jan: 33.7; Feb: 37.4; Mar: 46.5; Apr: 57; May: 66.4; Jun: 75.1; Jul: 78.1; Aug: 77.1; Sep: 69.5; Oct: 58.1; Nov: 46.4; Dec: 37; Jan: 24.6; Feb: 24.44; Mar: 37; Apr: 43.16; May: 54.3; Jun: 63.86; Jul: 65.84; Aug: 68; Sep: 56.5; Oct: 45.32; Nov: 39; Dec: 27.5
MN | EVELETH MUNI (AWOS) | Jan: 8.7; Feb: 13.5; Mar: 25.7; Apr: 39.4; May: 51.4; Jun: 61; Jul: 65.9; Aug: 63.7; Sep: 55.1; Oct: 43; Nov: 28.2; Dec: 14.8; Jan: 2.3; Feb: 12.38; Mar: 13.6; Apr: 28.76; May: 32.9; Jun: 53.6; Jul: 58.64; Aug: 55.76; Sep: 47.5; Oct: 36.5; Nov: 20.5; Dec: -1.7
IA | FAIR FIELD | Jan: 24.5; Feb: 27.2; Mar: 40.1; Apr: 52.7; May: 63; Jun: 72.4; Jul: 76.1; Aug: 74; Sep: 65.3; Oct: 53.6; Nov: 41.6; Dec: 28.2; Jan: 19.6; Feb: 15.08; Mar: 36.7; Apr: 47.3; May: 53.4; Jun: 61.7; Jul: 68.72; Aug: 63.86; Sep: 56.5; Oct: 42.98; Nov: 27.5; Dec: 20.5
AK | FAIRBANKS INTL ARPT | Jan: -8.5; Feb: -0.8; Mar: 10.6; Apr: 33.5; May: 50; Jun: 61; Jul: 62.6; Aug: 56.9; Sep: 45.5; Oct: 25.3; Nov: 3.1; Dec: -5.1; Jan: -3.8; Feb: -2.02; Mar: 1.2; Apr: 16.16; May: 29.3; Jun: 43.52; Jul: 49.82; Aug: 45.68; Sep: 35.2; Oct: 19.22; Nov: -4.5; Dec: -7.4
AK | FAIRBANKS/EIELSON A | Jan: -8.2; Feb: -1.5; Mar: 12.6; Apr: 33.9; May: 49.2; Jun: 59.8; Jul: 62; Aug: 56.3; Sep: 45; Oct: 23; Nov: 2.4; Dec: -6.5; Jan: 5; Feb: 9.32; Mar: 12.4; Apr: 16.34; May: 28.8; Jun: 39.74; Jul: 47.12; Aug: 44.06; Sep: 31.3; Oct: 26.24; Nov: 16; Dec: -0.9
WA | FAIRCHILD AFB | Jan: 28.5; Feb: 32.2; Mar: 39.4; Apr: 46; May: 53.9; Jun: 60.2; Jul: 69.4; Aug: 68.4; Sep: 60.4; Oct: 46.8; Nov: 35.6; Dec: 28.1; Jan: 26.6; Feb: 27.68; Mar: 27.3; Apr: 31.1; May: 36.5; Jun: 42.26; Jul: 37.94; Aug: 40.28; Sep: 32.5; Oct: 28.76; Nov: 30.9; Dec: 21.7
MN | FAIRMONT MUNI(AWOS) | Jan: 15.5; Feb: 20.1; Mar: 32.1; Apr: 46.3; May: 58.6; Jun: 68.5; Jul: 71.6; Aug: 69.2; Sep: 61.7; Oct: 49; Nov: 34.2; Dec: 20.9; Jan: 9.3; Feb: 22.28; Mar: 15.6; Apr: 36.32; May: 37.8; Jun: 54.14; Jul: 64.76; Aug: 60.98; Sep: 50.9; Oct: 36.32; Nov: 24.1; Dec: 18.1
NV | FALLON NAAS | Jan: 33.7; Feb: 40; Mar: 46.8; Apr: 52.1; May: 60.3; Jun: 68.5; Jul: 77.3; Aug: 75; Sep: 67.1; Oct: 54.2; Nov: 41.7; Dec: 32.4; Jan: 21.7; Feb: 19.22; Mar: 22.3; Apr: 26.24; May: 25.3; Jun: 37.76; Jul: 39.2; Aug: 41; Sep: 35.6; Oct: 28.94; Nov: 19.2; Dec: 20.3
NE | FALLS CITY/BRENNER | Jan: 26.9; Feb: 29.2; Mar: 42.6; Apr: 54.6; May: 64.4; Jun: 73.7; Jul: 77.7; Aug: 75.5; Sep: 66.7; Oct: 55; Nov: 42; Dec: 29.6; Jan: 15.1; Feb: 15.62; Mar: 34; Apr: 42.26; May: 48.6; Jun: 59.72; Jul: 65.3; Aug: 66.56; Sep: 55.6; Oct: 40.64; Nov: 28; Dec: 24.3
ND | FARGO HECTOR INTERNATIONAL AP | Jan: 9.3; Feb: 14.3; Mar: 27.4; Apr: 43.6; May: 56.7; Jun: 66.5; Jul: 70.7; Aug: 69.2; Sep: 60.2; Oct: 46.1; Nov: 29.6; Dec: 15.5; Jan: -2.2; Feb: 3.02; Mar: 22.5; Apr: 28.58; May: 44.6; Jun: 53.24; Jul: 59.9; Aug: 54.86; Sep: 46; Oct: 31.64; Nov: 19.6; Dec: 3.9
MN | FARIBAULT MUNI AWOS | Jan: 14.6; Feb: 19.2; Mar: 31.8; Apr: 46.3; May: 58.1; Jun: 68; Jul: 71.8; Aug: 69.2; Sep: 61.3; Oct: 48.3; Nov: 33.8; Dec: 20.5; Jan: 9.1; Feb: 0.68; Mar: 31.5; Apr: 37.4; May: 47.1; Jun: 56.48; Jul: 66.02; Aug: 61.34; Sep: 48.7; Oct: 35.96; Nov: 29.8; Dec: 19.8
MO | FARMINGTON | Jan: 33.3; Feb: 36.8; Mar: 46; Apr: 55.6; May: 64.6; Jun: 73; Jul: 76.7; Aug: 76.1; Sep: 67.2; Oct: 56.7; Nov: 45.2; Dec: 35.4; Jan: 29.5; Feb: 24.44; Mar: 32.5; Apr: 40.28; May: 50.7; Jun: 61.7; Jul: 66.02; Aug: 67.82; Sep: 52.3; Oct: 40.64; Nov: 34.2; Dec: 27.3
NM | FARMINGTON FOUR CORNERS REGL | Jan: 31; Feb: 36.7; Mar: 44.4; Apr: 51.2; May: 61; Jun: 70.8; Jul: 77.1; Aug: 74.4; Sep: 66.3; Oct: 53.2; Nov: 40.9; Dec: 31; Jan: 22.1; Feb: 22.64; Mar: 23.9; Apr: 20.48; May: 32.2; Jun: 33.44; Jul: 44.6; Aug: 46.58; Sep: 38.7; Oct: 31.64; Nov: 23.5; Dec: 18.7
VA | FARMVILLE | Jan: 38.5; Feb: 40.4; Mar: 48.5; Apr: 58; May: 66; Jun: 74.4; Jul: 78.5; Aug: 77.2; Sep: 69.6; Oct: 58.6; Nov: 48.3; Dec: 41.3; Jan: 24.8; Feb: 27.68; Mar: 25.5; Apr: 45.68; May: 57; Jun: 61.7; Jul: 63.32; Aug: 62.78; Sep: 60.4; Oct: 53.6; Nov: 43.3; Dec: 32
AR | FAYETTEVILLE DRAKE FIELD | Jan: 37.2; Feb: 41; Mar: 48.8; Apr: 57.8; May: 65.9; Jun: 74; Jul: 78.3; Aug: 77.7; Sep: 69.3; Oct: 58.5; Nov: 47.9; Dec: 39.1; Jan: 29.8; Feb: 25.7; Mar: 40.1; Apr: 50.72; May: 53.1; Jun: 65.48; Jul: 70.16; Aug: 66.92; Sep: 63.5; Oct: 50.36; Nov: 43.5; Dec: 24.4
NC | FAYETTEVILLE POPE AFB | Jan: 43.6; Feb: 46.7; Mar: 53.6; Apr: 63.1; May: 71; Jun: 78.4; Jul: 81.5; Aug: 79.7; Sep: 73.5; Oct: 63.2; Nov: 52.8; Dec: 46.1; Jan: 28.4; Feb: 31.64; Mar: 32; Apr: 43.7; May: 52.7; Jun: 64.4; Jul: 72.32; Aug: 66.38; Sep: 60.3; Oct: 48.74; Nov: 36.7; Dec: 31.5
NC | FAYETTEVILLE RGNL G | Jan: 44.6; Feb: 47.3; Mar: 54; Apr: 62.8; May: 70.5; Jun: 77.9; Jul: 81.3; Aug: 79.6; Sep: 73.7; Oct: 63.5; Nov: 53.6; Dec: 46.6; Jan: 28.6; Feb: 31.46; Mar: 32.2; Apr: 42.98; May: 53.1; Jun: 64.58; Jul: 68.54; Aug: 68.9; Sep: 62.1; Oct: 48.38; Nov: 38.3; Dec: 25.2
WA | FELTS FLD | Jan: 31.6; Feb: 34.6; Mar: 41.2; Apr: 47.6; May: 55.9; Jun: 62.2; Jul: 70.8; Aug: 69.8; Sep: 61.6; Oct: 48.8; Nov: 38; Dec: 30.7; Jan: 28.9; Feb: 30.38; Mar: 27; Apr: 33.08; May: 36.7; Jun: 46.58; Jul: 47.12; Aug: 46.58; Sep: 49.6; Oct: 36.5; Nov: 33.1; Dec: 28.4
MN | FERGUS FALLS AWOS | Jan: 11; Feb: 13; Mar: 29; Apr: 44; May: 57; Jun: 67; Jul: 72; Aug: 69; Sep: 61; Oct: 47; Nov: 31; Dec: 15; Jan: 10.8; Feb: 14.18; Mar: 23.4; Apr: 34.88; May: 42.8; Jun: 53.96; Jul: 61.52; Aug: 59.54; Sep: 52.2; Oct: 41.54; Nov: 26.1; Dec: 18
OH | FINDLAY AIRPORT | Jan: 26.6; Feb: 29.2; Mar: 38.5; Apr: 50.2; May: 60.9; Jun: 70.1; Jul: 73.2; Aug: 71.3; Sep: 64.4; Oct: 53.3; Nov: 41.7; Dec: 31.4; Jan: 21.7; Feb: 24.08; Mar: 32; Apr: 39.92; May: 50.7; Jun: 57.74; Jul: 61.34; Aug: 57.92; Sep: 53.6; Oct: 39.38; Nov: 36.9; Dec: 24.3
AZ | FLAGSTAFF PULLIAM ARPT | Jan: 30.3; Feb: 32.3; Mar: 37.8; Apr: 43.4; May: 51.8; Jun: 60.8; Jul: 66.5; Aug: 64.4; Sep: 58.1; Oct: 47.3; Nov: 37.4; Dec: 29.7; Jan: 16.7; Feb: 13.46; Mar: 19.9; Apr: 24.8; May: 21.4; Jun: 32.54; Jul: 38.66; Aug: 41.36; Sep: 37.4; Oct: 31.82; Nov: 19; Dec: 15.4
MI | FLINT BISHOP INTL ARPT | Jan: 23.7; Feb: 25.6; Mar: 34.9; Apr: 47; May: 58; Jun: 67.7; Jul: 71.2; Aug: 69.6; Sep: 61.8; Oct: 50.7; Nov: 39.4; Dec: 29; Jan: 16; Feb: 14.36; Mar: 26.8; Apr: 33.44; May: 47.1; Jun: 53.78; Jul: 60.44; Aug: 59.9; Sep: 54.1; Oct: 39.38; Nov: 27.1; Dec: 22.5
AR | FLIPPIN (AWOS) | Jan: 37.1; Feb: 41.1; Mar: 49.2; Apr: 59.2; May: 67; Jun: 75.3; Jul: 79.2; Aug: 79.1; Sep: 70.4; Oct: 60; Nov: 48.9; Dec: 39.6; Jan: 25.7; Feb: 30.74; Mar: 30.7; Apr: 42.62; May: 55.9; Jun: 60.26; Jul: 66.74; Aug: 61.7; Sep: 60.8; Oct: 51.08; Nov: 41.4; Dec: 24.6
SC | FLORENCE REGIONAL AP | Jan: 46.5; Feb: 49.2; Mar: 55.8; Apr: 63.9; May: 71.5; Jun: 78.3; Jul: 81.5; Aug: 80.1; Sep: 74.7; Oct: 64.8; Nov: 55; Dec: 48.4; Jan: 39; Feb: 31.1; Mar: 48.4; Apr: 50.72; May: 59.7; Jun: 66.74; Jul: 73.04; Aug: 71.78; Sep: 66.6; Oct: 55.76; Nov: 48.2; Dec: 30.6
MN | FLYING CLOUD | Jan: 16.1; Feb: 19.9; Mar: 32.5; Apr: 47.9; May: 59.5; Jun: 68.6; Jul: 74.5; Aug: 71.6; Sep: 63.6; Oct: 49.8; Nov: 35.9; Dec: 21.2; Jan: 17.6; Feb: 6.62; Mar: 21; Apr: 35.96; May: 43.3; Jun: 57.92; Jul: 62.06; Aug: 61.88; Sep: 54.5; Oct: 33.8; Nov: 28.6; Dec: 0.1
GA | FORT BENNING LAWSON | Jan: 46.6; Feb: 50.6; Mar: 56.7; Apr: 63.1; May: 71.7; Jun: 78.4; Jul: 80.9; Aug: 80.2; Sep: 75.1; Oct: 64.8; Nov: 54.9; Dec: 48.3; Jan: 31.6; Feb: 36.5; Mar: 38.5; Apr: 46.76; May: 63.1; Jun: 66.2; Jul: 68; Aug: 69.26; Sep: 64.4; Oct: 48.38; Nov: 41.4; Dec: 32.7
NC | FORT BRAGG SIMMONS AAF | Jan: 44; Feb: 47.6; Mar: 53.9; Apr: 63; May: 70.8; Jun: 78.5; Jul: 81.8; Aug: 79.6; Sep: 73.8; Oct: 63.4; Nov: 52.7; Dec: 46.8; Jan: 34.7; Feb: 32.18; Mar: 32.5; Apr: 42.08; May: 57.4; Jun: 64.58; Jul: 72.86; Aug: 67.82; Sep: 62.8; Oct: 48.02; Nov: 37; Dec: 31.8
KY | FORT CAMPBELL AAF | Jan: 37.1; Feb: 41.6; Mar: 49.7; Apr: 59.3; May: 68; Jun: 75.7; Jul: 78.8; Aug: 78; Sep: 71; Oct: 59.9; Nov: 48.7; Dec: 40.2; Jan: 24.6; Feb: 28.8; Mar: 30.7; Apr: 40.1; May: 50.4; Jun: 68.2; Jul: 68.9; Aug: 70.9; Sep: 57.2; Oct: 46.9; Nov: 38.7; Dec: 32.5
CO | FORT COLLINS (AWOS) | Jan: 29.6; Feb: 31.4; Mar: 40.7; Apr: 47.1; May: 57.3; Jun: 66.4; Jul: 72.8; Aug: 70.6; Sep: 62.8; Oct: 49.7; Nov: 37.4; Dec: 29.7; Jan: 14; Feb: 14.72; Mar: 22.6; Apr: 28.22; May: 38.3; Jun: 43.34; Jul: 48.92; Aug: 42.08; Sep: 36.5; Oct: 25.16; Nov: 23.4; Dec: 14.2
IA | FORT DODGE (AWOS) | Jan: 17.7; Feb: 22.4; Mar: 34.9; Apr: 47.9; May: 59.6; Jun: 69.2; Jul: 73.1; Aug: 70.8; Sep: 62.6; Oct: 50.7; Nov: 36.4; Dec: 22.9; Jan: 12.2; Feb: 22.82; Mar: 23.7; Apr: 38.66; May: 48.6; Jun: 60.08; Jul: 64.58; Aug: 61.7; Sep: 52.9; Oct: 33.08; Nov: 26.8; Dec: 11.8
NY | FORT DRUM/WHEELER-S | Jan: 19; Feb: 20.8; Mar: 30.3; Apr: 43.8; May: 55.9; Jun: 65.1; Jul: 69.1; Aug: 67.8; Sep: 60.1; Oct: 48.6; Nov: 37; Dec: 25.8; Jan: 22.1; Feb: 18.68; Mar: 28.6; Apr: 29.66; May: 38.3; Jun: 54.14; Jul: 59.54; Aug: 55.4; Sep: 50.5; Oct: 39.38; Nov: 31.3; Dec: 27.5
TX | FORT HOOD | Jan: 49.9; Feb: 54.4; Mar: 61.2; Apr: 68.2; May: 75.3; Jun: 83.5; Jul: 85.1; Aug: 86.5; Sep: 79.8; Oct: 70.2; Nov: 59.4; Dec: 52; Jan: 34.2; Feb: 39.92; Mar: 38.1; Apr: 47.84; May: 61.5; Jun: 69.08; Jul: 68.54; Aug: 67.64; Sep: 58.3; Oct: 50.72; Nov: 42.6; Dec: 33.8
KY | FORT KNOX GODMAN AAF | Jan: 33.7; Feb: 38.4; Mar: 46.3; Apr: 56.9; May: 65.7; Jun: 73.6; Jul: 76.5; Aug: 75.9; Sep: 68.8; Oct: 57.8; Nov: 46.6; Dec: 37.2; Jan: 29.5; Feb: 27.1; Mar: 27.9; Apr: 37.8; May: 56.1; Jun: 63.7; Jul: 66.9; Aug: 63; Sep: 47.5; Oct: 46.9; Nov: 33.6; Dec: 28.8
FL | FORT LAUDERDALE | Jan: 67; Feb: 69.5; Mar: 71.7; Apr: 75.4; May: 79.1; Jun: 82.1; Jul: 83.4; Aug: 83.9; Sep: 82.4; Oct: 79.1; Nov: 73.1; Dec: 69.8; Jan: 56.3; Feb: 57.2; Mar: 65.1; Apr: 63.32; May: 64.4; Jun: 73.04; Jul: 74.3; Aug: 72.32; Sep: 72.3; Oct: 68; Nov: 63.3; Dec: 56.3
FL | FORT LAUDERDALE HOLLYWOOD INT | Jan: 68.8; Feb: 70.4; Mar: 72.7; Apr: 76.2; May: 80; Jun: 82.7; Jul: 83.9; Aug: 84.2; Sep: 82.8; Oct: 79.9; Nov: 74.4; Dec: 71; Jan: 63; Feb: 63.86; Mar: 59.5; Apr: 64.94; May: 71.1; Jun: 74.66; Jul: 74.84; Aug: 74.48; Sep: 72.9; Oct: 69.08; Nov: 61.7; Dec: 57.6
IA | FORT MADISON | Jan: 26; Feb: 30; Mar: 42.1; Apr: 53.5; May: 64.4; Jun: 72.6; Jul: 76.6; Aug: 75.6; Sep: 67.2; Oct: 55.8; Nov: 42.2; Dec: 31.3; Jan: 19.9; Feb: 24.62; Mar: 36; Apr: 47.3; May: 52.3; Jun: 60.62; Jul: 69.08; Aug: 64.76; Sep: 61.7; Oct: 39.74; Nov: 32.2; Dec: 27.1
AB | FORT MCMURRAY AP | Jan: 0.6; Feb: 8.1; Mar: 20; Apr: 37; May: 49.3; Jun: 58.4; Jul: 62.9; Aug: 59.9; Sep: 50.2; Oct: 36.4; Nov: 17.6; Dec: 4; Jan: -4.4; Feb: -1.12; Mar: 7; Apr: 20.12; May: 30.7; Jun: 43.88; Jul: 51.44; Aug: 49.28; Sep: 41.2; Oct: 27.14; Nov: 14.7; Dec: -2.7
FL | FORT MYERS PAGE FIELD | Jan: 64.9; Feb: 66.9; Mar: 69.8; Apr: 74.1; May: 79; Jun: 82.1; Jul: 82.9; Aug: 83.2; Sep: 82; Oct: 77.6; Nov: 71; Dec: 66.8; Jan: 54.5; Feb: 56.48; Mar: 59.7; Apr: 63.86; May: 68; Jun: 73.22; Jul: 73.76; Aug: 74.66; Sep: 73.9; Oct: 70.34; Nov: 66.7; Dec: 56.8
BC | FORT NELSON | Jan: -4.6; Feb: 5.2; Mar: 17.5; Apr: 37; May: 49.3; Jun: 58.7; Jul: 62.7; Aug: 59.2; Sep: 49; Oct: 33.2; Nov: 9.8; Dec: -2.3; Jan: -10.1; Feb: -1.3; Mar: 4.8; Apr: 21.02; May: 31.6; Jun: 44.78; Jul: 51.62; Aug: 48.38; Sep: 39.7; Oct: 26.6; Nov: 8.6; Dec: -6.5
LA | FORT POLK AAF | Jan: 50.5; Feb: 54; Mar: 60; Apr: 67; May: 74.5; Jun: 80.6; Jul: 82.5; Aug: 82.9; Sep: 77.9; Oct: 67.9; Nov: 57.8; Dec: 51.6; Jan: 39.7; Feb: 43.16; Mar: 41.7; Apr: 55.76; May: 68.7; Jun: 71.24; Jul: 72.32; Aug: 70.7; Sep: 64.6; Oct: 55.58; Nov: 48.7; Dec: 34.3
KS | FORT RILEY MARSHALL AAF | Jan: 30.8; Feb: 33.9; Mar: 46.2; Apr: 54.6; May: 64.8; Jun: 75.7; Jul: 80.2; Aug: 79; Sep: 69.2; Oct: 57.1; Nov: 44; Dec: 32.8; Jan: 20.5; Feb: 21.2; Mar: 35.1; Apr: 42.62; May: 52.7; Jun: 64.94; Jul: 65.66; Aug: 66.56; Sep: 57.2; Oct: 45.32; Nov: 31.8; Dec: 26.6
BC | FORT SAINT JOHN | Jan: 8.6; Feb: 15; Mar: 22.7; Apr: 38.2; May: 49.4; Jun: 57.2; Jul: 61; Aug: 58.9; Sep: 51; Oct: 38; Nov: 20.3; Dec: 10.9; Jan: 1.4; Feb: 5.54; Mar: 8.8; Apr: 21.56; May: 30.2; Jun: 41.36; Jul: 47.48; Aug: 45.5; Sep: 38.5; Oct: 27.5; Nov: 16.2; Dec: 4.6
OK | FORT SILL POST FIELD AF | Jan: 40.9; Feb: 45.6; Mar: 53.3; Apr: 61.4; May: 70.6; Jun: 80.2; Jul: 84; Aug: 82.9; Sep: 74.8; Oct: 63.2; Nov: 51; Dec: 41.9; Jan: 29.5; Feb: 33.08; Mar: 28.6; Apr: 38.3; May: 58.3; Jun: 60.62; Jul: 65.48; Aug: 63.14; Sep: 50; Oct: 44.78; Nov: 38.1; Dec: 33.1
AR | FORT SMITH REGIONAL AP | Jan: 40.6; Feb: 44.9; Mar: 53.3; Apr: 62.1; May: 70.2; Jun: 78.5; Jul: 82.8; Aug: 82.4; Sep: 74.2; Oct: 63.2; Nov: 51.7; Dec: 42.4; Jan: 26.1; Feb: 26.42; Mar: 39.6; Apr: 47.84; May: 57.9; Jun: 67.64; Jul: 70.7; Aug: 68.72; Sep: 64.4; Oct: 49.1; Nov: 43.7; Dec: 26.1
IN | FORT WAYNE INTL AP | Jan: 25.6; Feb: 28.8; Mar: 38.8; Apr: 50.4; May: 61; Jun: 70.5; Jul: 73.5; Aug: 71.5; Sep: 64.2; Oct: 53; Nov: 41.3; Dec: 30.5; Jan: 14.4; Feb: 17.42; Mar: 28.9; Apr: 37.4; May: 51.6; Jun: 54.32; Jul: 60.8; Aug: 62.42; Sep: 55.9; Oct: 42.62; Nov: 32.4; Dec: 18
TX | FORT WORTH ALLIANCE | Jan: 45.8; Feb: 49.3; Mar: 57.1; Apr: 64.9; May: 73.2; Jun: 81.6; Jul: 85.4; Aug: 85.6; Sep: 77.5; Oct: 66.8; Nov: 55.6; Dec: 46.6; Jan: 34.2; Feb: 34.88; Mar: 41.9; Apr: 48.2; May: 62.6; Jun: 70.16; Jul: 67.64; Aug: 68.72; Sep: 62.8; Oct: 55.94; Nov: 39.2; Dec: 27.1
TX | FORT WORTH MEACHAM | Jan: 46.7; Feb: 50.5; Mar: 57.5; Apr: 65.5; May: 73.8; Jun: 81.8; Jul: 85.4; Aug: 85.6; Sep: 78; Oct: 67.5; Nov: 56.4; Dec: 47.8; Jan: 34.2; Feb: 41.9; Mar: 42.8; Apr: 48.92; May: 65.1; Jun: 69.08; Jul: 69.08; Aug: 67.64; Sep: 63; Oct: 55.4; Nov: 41.7; Dec: 34.7
TX | FORT WORTH NAS | Jan: 47.4; Feb: 51.7; Mar: 58.9; Apr: 66.3; May: 75.1; Jun: 82.9; Jul: 86.3; Aug: 86.1; Sep: 79.4; Oct: 68.4; Nov: 57.3; Dec: 48.4; Jan: 33.1; Feb: 43.34; Mar: 47.5; Apr: 53.6; May: 61; Jun: 66.02; Jul: 67.1; Aug: 68.36; Sep: 63.3; Oct: 53.42; Nov: 38.3; Dec: 27.9
AK | FORT YUKON | Jan: -17.4; Feb: -11; Mar: 1; Apr: 25.5; May: 46.1; Jun: 59.7; Jul: 61.8; Aug: 54.8; Sep: 42.3; Oct: 19.7; Nov: -5; Dec: -11; Jan: -12.8; Feb: -18.76; Mar: -6.2; Apr: 10.22; May: 29.8; Jun: 39.02; Jul: 42.44; Aug: 37.4; Sep: 30.9; Oct: 14.54; Nov: 6.1; Dec: -24.2
MN | FOSSTON(AWOS) | Jan: 6.8; Feb: 11.1; Mar: 24.7; Apr: 41.1; May: 53.7; Jun: 63.5; Jul: 67.6; Aug: 66.1; Sep: 57.6; Oct: 44; Nov: 27.2; Dec: 12.9; Jan: 0.9; Feb: 13.28; Mar: 15.8; Apr: 20.66; May: 32.2; Jun: 51.98; Jul: 58.1; Aug: 58.82; Sep: 50.4; Oct: 35.96; Nov: 19.9; Dec: -3.1
PA | FRANKLIN | Jan: 25.5; Feb: 26.7; Mar: 35.6; Apr: 47.5; May: 57.3; Jun: 65.4; Jul: 69.2; Aug: 67.7; Sep: 60.7; Oct: 50; Nov: 39.8; Dec: 29.9; Jan: 27.3; Feb: 17.42; Mar: 31.6; Apr: 31.82; May: 35.4; Jun: 55.22; Jul: 56.48; Aug: 54.68; Sep: 47.3; Oct: 38.48; Nov: 29.3; Dec: 21.6
VA | FRANKLIN NAAS | Jan: 41.6; Feb: 43.8; Mar: 50.9; Apr: 60.2; May: 68.3; Jun: 76.6; Jul: 80.2; Aug: 78.7; Sep: 72.6; Oct: 61.7; Nov: 51.5; Dec: 44.6; Jan: 29.1; Feb: 33.26; Mar: 38.8; Apr: 45.68; May: 56.8; Jun: 61.7; Jul: 68.54; Aug: 67.28; Sep: 64.6; Oct: 52.88; Nov: 40.3; Dec: 33.1
NB | FREDERICTON | Jan: 16; Feb: 18.4; Mar: 28.7; Apr: 40.8; May: 52.4; Jun: 62; Jul: 67.5; Aug: 66.1; Sep: 57.7; Oct: 46.4; Nov: 35.5; Dec: 24; Jan: 7.5; Feb: 9.68; Mar: 18.1; Apr: 28.76; May: 39.7; Jun: 51.44; Jul: 58.1; Aug: 57.02; Sep: 50; Oct: 39.2; Nov: 30.2; Dec: 16.5
NE | FREMONT MUNI ARPT | Jan: 23.8; Feb: 27.9; Mar: 39; Apr: 51.1; May: 61.9; Jun: 71.7; Jul: 76.5; Aug: 73.6; Sep: 65.7; Oct: 53.3; Nov: 39.3; Dec: 26.7; Jan: 18; Feb: 15.44; Mar: 33.1; Apr: 40.28; May: 38.3; Jun: 57.56; Jul: 63.68; Aug: 62.06; Sep: 54.3; Oct: 41.54; Nov: 21.7; Dec: 7.5
CA | FRESNO YOSEMITE INTL AP | Jan: 47.7; Feb: 52; Mar: 57.3; Apr: 62.1; May: 70.1; Jun: 77; Jul: 83.3; Aug: 81.9; Sep: 77; Oct: 66.7; Nov: 55; Dec: 47.3; Jan: 39.9; Feb: 42.44; Mar: 43.7; Apr: 44.06; May: 48.7; Jun: 46.4; Jul: 53.96; Aug: 52.16; Sep: 52.7; Oct: 48.74; Nov: 44.4; Dec: 39.7
CA | FULLERTON MUNICIPAL | Jan: 57.7; Feb: 57.7; Mar: 60.6; Apr: 62.8; May: 67.1; Jun: 70.1; Jul: 74.5; Aug: 75.5; Sep: 74; Oct: 68.4; Nov: 62.2; Dec: 56.6; Jan: 40.8; Feb: 45.32; Mar: 46.4; Apr: 47.3; May: 53.4; Jun: 57.56; Jul: 61.34; Aug: 62.96; Sep: 56.1; Oct: 55.22; Nov: 44.6; Dec: 41.5
GA | FULTON CO ARPT BROW | Jan: 43.9; Feb: 47.2; Mar: 53.9; Apr: 61.6; May: 69.5; Jun: 76.7; Jul: 79.6; Aug: 78.9; Sep: 73; Oct: 62.5; Nov: 52.3; Dec: 45.7; Jan: 31.5; Feb: 38.48; Mar: 45; Apr: 55.94; May: 60.8; Jun: 65.84; Jul: 68.72; Aug: 69.08; Sep: 64.9; Oct: 43.88; Nov: 38.1; Dec: 29.3
AL | GADSEN MUNI AWOS | Jan: 42; Feb: 47; Mar: 54; Apr: 60; May: 69; Jun: 76; Jul: 79; Aug: 79; Sep: 73; Oct: 62; Nov: 50; Dec: 44; Jan: 30.6; Feb: 37.04; Mar: 45.1; Apr: 50.54; May: 53.1; Jun: 64.22; Jul: 68.9; Aug: 67.28; Sep: 59.5; Oct: 50.9; Nov: 42.1; Dec: 27.5
OK | GAGE AIRPORT | Jan: 35.9; Feb: 39.3; Mar: 48.3; Apr: 57.6; May: 67.4; Jun: 76.4; Jul: 80.9; Aug: 79.7; Sep: 71.2; Oct: 59.1; Nov: 46.4; Dec: 36.5; Jan: 20.3; Feb: 24.26; Mar: 28; Apr: 41.54; May: 55.4; Jun: 62.96; Jul: 61.16; Aug: 61.88; Sep: 58.5; Oct: 42.8; Nov: 31.6; Dec: 24.3
FL | GAINESVILLE REGIONAL AP | Jan: 55.3; Feb: 58.2; Mar: 62.6; Apr: 68.2; May: 74.9; Jun: 79.5; Jul: 81.1; Aug: 81; Sep: 78.3; Oct: 71; Nov: 62.3; Dec: 56.9; Jan: 47.1; Feb: 48.56; Mar: 53.8; Apr: 57.2; May: 65.7; Jun: 69.62; Jul: 72.68; Aug: 73.94; Sep: 69.1; Oct: 63.32; Nov: 52.7; Dec: 44.2
NM | GALLUP SEN CLARKE FLD | Jan: 29.6; Feb: 34; Mar: 40.2; Apr: 46.7; May: 55.9; Jun: 65.3; Jul: 71.1; Aug: 69; Sep: 61.7; Oct: 49.3; Nov: 37.6; Dec: 28.9; Jan: 18; Feb: 22.1; Mar: 23.5; Apr: 23.54; May: 28; Jun: 26.42; Jul: 46.4; Aug: 50.72; Sep: 39.2; Oct: 27.5; Nov: 23.4; Dec: 15.3
TX | GALVESTON/SCHOLES | Jan: 55.6; Feb: 58.1; Mar: 64.1; Apr: 70.5; May: 77.2; Jun: 83.3; Jul: 84.6; Aug: 85.3; Sep: 81.7; Oct: 74.3; Nov: 64.6; Dec: 57.3; Jan: 54.7; Feb: 55.22; Mar: 52.7; Apr: 57.38; May: 69.3; Jun: 72.5; Jul: 75.2; Aug: 75.74; Sep: 73.2; Oct: 65.48; Nov: 53.4; Dec: 43
AK | GAMBELL | Jan: 6.7; Feb: 9; Mar: 8.4; Apr: 18.5; May: 30.7; Jun: 39.3; Jul: 46.1; Aug: 46.9; Sep: 41.8; Oct: 33.1; Nov: 25.1; Dec: 11.6; Jan: 7.3; Feb: 7.34; Mar: 11.7; Apr: 2.66; May: 29.5; Jun: 34.52; Jul: 32; Aug: 34.16; Sep: 32.5; Oct: 29.12; Nov: 21.9; Dec: 9.7
KS | GARDEN CITY MUNICIPAL AP | Jan: 31.7; Feb: 35.4; Mar: 44.2; Apr: 53.1; May: 63.9; Jun: 73.7; Jul: 78.5; Aug: 76.8; Sep: 68.5; Oct: 55.9; Nov: 42.2; Dec: 32.3; Jan: 24.4; Feb: 24.98; Mar: 20.3; Apr: 37.58; May: 46.2; Jun: 59.54; Jul: 61.88; Aug: 64.58; Sep: 52; Oct: 33.44; Nov: 27.1; Dec: 21.2
TX | GEORGETOWN (AWOS) | Jan: 49.6; Feb: 52.4; Mar: 58.5; Apr: 66.6; May: 74.5; Jun: 79.8; Jul: 83.2; Aug: 83.7; Sep: 78; Oct: 69.2; Nov: 57.5; Dec: 50.2; Jan: 30.2; Feb: 35.06; Mar: 36.3; Apr: 44.78; May: 61.7; Jun: 67.82; Jul: 63.32; Aug: 66.92; Sep: 57.9; Oct: 48.38; Nov: 41.4; Dec: 35.4
WY | GILLETTE/GILLETTE-C | Jan: 25.6; Feb: 26.6; Mar: 35.5; Apr: 42.9; May: 52.1; Jun: 62.4; Jul: 71.4; Aug: 70.2; Sep: 60.1; Oct: 46.1; Nov: 34.2; Dec: 25.5; Jan: 13.6; Feb: 21.74; Mar: 20.5; Apr: 31.64; May: 36.5; Jun: 46.76; Jul: 51.8; Aug: 44.78; Sep: 44.2; Oct: 31.82; Nov: 22.3; Dec: 20.3
MT | GLASGOW INTL ARPT | Jan: 14; Feb: 18.9; Mar: 30.8; Apr: 44.1; May: 54.4; Jun: 63.3; Jul: 71; Aug: 70.3; Sep: 59.5; Oct: 44.8; Nov: 29.3; Dec: 17.1; Jan: 5.7; Feb: 15.44; Mar: 20.8; Apr: 30.38; May: 39.9; Jun: 44.06; Jul: 50.72; Aug: 48.74; Sep: 37; Oct: 31.82; Nov: 22.3; Dec: 11.3
MT | GLENDIVE(AWOS) | Jan: 16.6; Feb: 20.5; Mar: 32; Apr: 43.2; May: 53.2; Jun: 62.5; Jul: 71; Aug: 69.5; Sep: 59.2; Oct: 45.1; Nov: 31.3; Dec: 20.1; Jan: 11.1; Feb: 15.26; Mar: 11.8; Apr: 33.8; May: 41.5; Jun: 45.32; Jul: 48.56; Aug: 46.76; Sep: 41.5; Oct: 26.42; Nov: 22.8; Dec: 9.1
NY | GLENS FALLS AP | Jan: 20.3; Feb: 22.7; Mar: 32.3; Apr: 45.5; May: 56.7; Jun: 65.6; Jul: 69.8; Aug: 68.1; Sep: 59.8; Oct: 48.3; Nov: 37.8; Dec: 27; Jan: 10; Feb: 4.46; Mar: 26.8; Apr: 36.5; May: 41.4; Jun: 57.56; Jul: 64.04; Aug: 60.98; Sep: 55.4; Oct: 40.46; Nov: 33.6; Dec: 23
MN | GLENWOOD (ASOS) | Jan: 11.7; Feb: 16.1; Mar: 28; Apr: 44.3; May: 56.4; Jun: 66.4; Jul: 71.8; Aug: 69.3; Sep: 60.8; Oct: 47; Nov: 31.4; Dec: 17.2; Jan: 7.2; Feb: 18.32; Mar: 20.1; Apr: 37.58; May: 42.4; Jun: 52.88; Jul: 65.3; Aug: 58.1; Sep: 50.5; Oct: 32.9; Nov: 23.9; Dec: 15.8
MS | GOLDEN TRI(AWOS) | Jan: 44.5; Feb: 48.2; Mar: 54.8; Apr: 62.7; May: 71.1; Jun: 77.5; Jul: 81; Aug: 80.1; Sep: 74.5; Oct: 64; Nov: 53.4; Dec: 45.3; Jan: 29.3; Feb: 33.26; Mar: 35.4; Apr: 44.6; May: 64.4; Jun: 66.2; Jul: 68.54; Aug: 68.9; Sep: 64.9; Oct: 48.56; Nov: 36.9; Dec: 32.7
NC | GOLDSBORO SEYMOUR JOHNSON AFB | Jan: 44.6; Feb: 47.6; Mar: 54.1; Apr: 62.7; May: 70.7; Jun: 78.1; Jul: 81.6; Aug: 79.3; Sep: 73.8; Oct: 63.6; Nov: 53.5; Dec: 47.3; Jan: 29.5; Feb: 32.18; Mar: 33.3; Apr: 41.72; May: 50; Jun: 65.84; Jul: 73.4; Aug: 68.54; Sep: 61.7; Oct: 48.74; Nov: 39; Dec: 27.5
KS | GOODLAND RENNER FIELD | Jan: 30.1; Feb: 32.4; Mar: 41.1; Apr: 49.3; May: 59.7; Jun: 70.4; Jul: 75.8; Aug: 73.8; Sep: 65; Oct: 52.1; Nov: 39.5; Dec: 30.5; Jan: 11.5; Feb: 19.76; Mar: 24.4; Apr: 33.98; May: 47.3; Jun: 54.5; Jul: 57.56; Aug: 56.48; Sep: 48.6; Oct: 32.9; Nov: 23.9; Dec: 17.8
AZ | GRAND CANYON NATL P | Jan: 29.4; Feb: 31.5; Mar: 37.8; Apr: 42.7; May: 51.4; Jun: 60.1; Jul: 67.2; Aug: 65.5; Sep: 58.4; Oct: 46.8; Nov: 37.1; Dec: 29; Jan: 14.2; Feb: 20.12; Mar: 23.2; Apr: 17.96; May: 20.5; Jun: 21.74; Jul: 35.42; Aug: 42.8; Sep: 46.9; Oct: 29.3; Nov: 16.2; Dec: 16
ND | GRAND FORKS AF | Jan: 7.2; Feb: 12.4; Mar: 25.1; Apr: 41; May: 54.5; Jun: 64.8; Jul: 69.2; Aug: 68.1; Sep: 58.3; Oct: 44; Nov: 27.2; Dec: 14.1; Jan: 14.4; Feb: 25.16; Mar: 20.8; Apr: 28.04; May: 37.8; Jun: 54.14; Jul: 57.92; Aug: 58.28; Sep: 43.9; Oct: 29.84; Nov: 26.1; Dec: 20.1
ND | GRAND FORKS INTERNATIONAL AP | Jan: 7; Feb: 11.8; Mar: 24.8; Apr: 41.6; May: 54.6; Jun: 64.9; Jul: 69; Aug: 67.8; Sep: 58.4; Oct: 44; Nov: 27; Dec: 12.9; Jan: 2.5; Feb: -1.48; Mar: 20.8; Apr: 34.16; May: 45.3; Jun: 54.14; Jul: 59.36; Aug: 58.82; Sep: 50.2; Oct: 30.02; Nov: 19.4; Dec: -4.2
NE | GRAND ISLAND CENTRAL NE REGIO | Jan: 25.4; Feb: 29.6; Mar: 39.8; Apr: 50.4; May: 61.3; Jun: 71.5; Jul: 76.1; Aug: 74.1; Sep: 65.5; Oct: 52.7; Nov: 38.7; Dec: 27.8; Jan: 7.7; Feb: 13.28; Mar: 24.1; Apr: 39.2; May: 45.9; Jun: 60.26; Jul: 61.88; Aug: 60.08; Sep: 51.3; Oct: 36.5; Nov: 23.5; Dec: 14.5
CO | GRAND JUNCTION WALKER FIELD | Jan: 27.8; Feb: 35.3; Mar: 44.9; Apr: 52.1; May: 62.4; Jun: 72.9; Jul: 79.3; Aug: 76.1; Sep: 67; Oct: 53.5; Nov: 39.5; Dec: 28.2; Jan: 17.1; Feb: 21.38; Mar: 23.2; Apr: 26.96; May: 32.9; Jun: 34.52; Jul: 44.42; Aug: 44.6; Sep: 37; Oct: 28.76; Nov: 24.4; Dec: 18
AB | GRAND PRAIRIE | Jan: 7.2; Feb: 13.3; Mar: 22.1; Apr: 38.5; May: 50; Jun: 57.5; Jul: 61.3; Aug: 59.5; Sep: 51.2; Oct: 38.4; Nov: 20.5; Dec: 9.7; Jan: 2.5; Feb: 5.9; Mar: 11.3; Apr: 23.18; May: 32; Jun: 42.26; Jul: 48.2; Aug: 46.58; Sep: 39.4; Oct: 28.58; Nov: 17.4; Dec: 4.8
MI | GRAND RAPIDS KENT COUNTY INT | Jan: 24.5; Feb: 26.3; Mar: 35.4; Apr: 47.4; May: 58.5; Jun: 68.3; Jul: 71.9; Aug: 70.3; Sep: 62.4; Oct: 50.9; Nov: 39.6; Dec: 29.7; Jan: 15.8; Feb: 16.34; Mar: 25.3; Apr: 32.18; May: 47.3; Jun: 54.5; Jul: 60.26; Aug: 60.8; Sep: 54.9; Oct: 38.48; Nov: 34.5; Dec: 21.4
MN | GRAND RAPIDS(AWOS) | Jan: 9.4; Feb: 14.1; Mar: 26.5; Apr: 40; May: 52; Jun: 61.9; Jul: 66.4; Aug: 64.5; Sep: 56.1; Oct: 43.8; Nov: 28.3; Dec: 15.1; Jan: 7.5; Feb: 8.42; Mar: 4.5; Apr: 30.74; May: 39.9; Jun: 52.7; Jul: 54.68; Aug: 52.88; Sep: 46.8; Oct: 26.06; Nov: 27.3; Dec: 5.9
WA | GRAY AAF | Jan: 40; Feb: 41.6; Mar: 44.9; Apr: 48.7; May: 54.8; Jun: 59.7; Jul: 65.2; Aug: 65.4; Sep: 60.4; Oct: 51.3; Nov: 43.9; Dec: 38.5; Jan: 34.3; Feb: 34.52; Mar: 35.1; Apr: 35.78; May: 42.8; Jun: 47.66; Jul: 51.8; Aug: 51.8; Sep: 52.3; Oct: 41.54; Nov: 34.9; Dec: 34.2
KS | GREAT BEND (AWOS) | Jan: 30.6; Feb: 33.9; Mar: 43.6; Apr: 53.2; May: 64.4; Jun: 74.7; Jul: 79.6; Aug: 77.9; Sep: 68.9; Oct: 56.5; Nov: 42.8; Dec: 32.5; Jan: 21.2; Feb: 28.04; Mar: 19.2; Apr: 40.82; May: 45.7; Jun: 60.26; Jul: 61.34; Aug: 62.06; Sep: 52.9; Oct: 41.36; Nov: 28.6; Dec: 21.9
MT | GREAT FALLS INTL ARPT | Jan: 25.8; Feb: 27.8; Mar: 34.6; Apr: 42.9; May: 51.7; Jun: 59.2; Jul: 68.3; Aug: 67.1; Sep: 58.1; Oct: 45.7; Nov: 34.1; Dec: 26.2; Jan: 3; Feb: 14.18; Mar: 16.9; Apr: 26.78; May: 32.4; Jun: 40.82; Jul: 43.88; Aug: 40.28; Sep: 39.9; Oct: 30.2; Nov: 19.6; Dec: 12
CO | GREELEY/WELD (AWOS) | Jan: 25.7; Feb: 29.3; Mar: 39.9; Apr: 47.2; May: 57.4; Jun: 67.4; Jul: 73.5; Aug: 70.7; Sep: 61.9; Oct: 48.7; Nov: 35.8; Dec: 26.1; Jan: 19.9; Feb: 12.74; Mar: 22.3; Apr: 23.9; May: 35.2; Jun: 43.16; Jul: 46.58; Aug: 48.38; Sep: 43.3; Oct: 26.6; Nov: 22.1; Dec: 16.5
WI | GREEN BAY AUSTIN STRAUBEL INT | Jan: 18.1; Feb: 21.3; Mar: 31.9; Apr: 44.6; May: 56.1; Jun: 66.1; Jul: 69.9; Aug: 68.3; Sep: 60.2; Oct: 48.4; Nov: 35.9; Dec: 23.8; Jan: 7.2; Feb: 10.94; Mar: 23.9; Apr: 33.08; May: 46.8; Jun: 56.3; Jul: 62.42; Aug: 59.36; Sep: 53.1; Oct: 36.5; Nov: 28.6; Dec: 18.5
WY | GREEN RIVER-GREATER GREEN RIVER INTERGALACTIC SPACEPORT | Jan: 22; Feb: 25; Mar: 34; Apr: 41; May: 51; Jun: 61; Jul: 70; Aug: 67; Sep: 58; Oct: 44; Nov: 32; Dec: 22; Jan: 15.6; Feb: 18.5; Mar: 17.2; Apr: 24.62; May: 30.2; Jun: 32; Jul: 38.84; Aug: 36.68; Sep: 30.9; Oct: 24.44; Nov: 21.4; Dec: 12.4
NC | GREENSBORO PIEDMONT TRIAD INT | Jan: 39.9; Feb: 42.8; Mar: 50; Apr: 59.1; May: 66.9; Jun: 74.9; Jul: 78.3; Aug: 76.8; Sep: 70.2; Oct: 59.7; Nov: 49.7; Dec: 42.3; Jan: 21.7; Feb: 28.58; Mar: 39; Apr: 42.98; May: 54; Jun: 65.84; Jul: 67.64; Aug: 67.28; Sep: 59.7; Oct: 47.48; Nov: 37.9; Dec: 27.1
SC | GREENVILLE DOWNTOWN AP | Jan: 42.8; Feb: 45.9; Mar: 53.8; Apr: 62.3; May: 69.7; Jun: 77.1; Jul: 79.4; Aug: 79.2; Sep: 72.8; Oct: 62.4; Nov: 53; Dec: 45.1; Jan: 24.8; Feb: 28.4; Mar: 31.6; Apr: 39.56; May: 46.8; Jun: 64.4; Jul: 69.44; Aug: 68.18; Sep: 61.7; Oct: 46.22; Nov: 42.8; Dec: 27.9
MS | GREENVILLE MUNI AP | Jan: 44; Feb: 47; Mar: 56; Apr: 65; May: 73; Jun: 80; Jul: 82; Aug: 82; Sep: 77; Oct: 65; Nov: 54; Dec: 47; Jan: 38.7; Feb: 43.52; Mar: 45; Apr: 52.88; May: 59.9; Jun: 68.72; Jul: 70.7; Aug: 71.24; Sep: 61.2; Oct: 50.9; Nov: 41.4; Dec: 41.9
TX | GREENVILLE MUNICIPAL AP | Jan: 46; Feb: 49; Mar: 58; Apr: 64; May: 73; Jun: 81; Jul: 84; Aug: 85; Sep: 78; Oct: 67; Nov: 56; Dec: 48; Jan: 29.3; Feb: 36.68; Mar: 36.7; Apr: 48.92; May: 66; Jun: 68.72; Jul: 69.98; Aug: 69.08; Sep: 57.2; Oct: 49.82; Nov: 41.4; Dec: 33.8
NS | GREENWOOD AP | Jan: 23.2; Feb: 23.7; Mar: 31.4; Apr: 41.9; May: 52.5; Jun: 61.8; Jul: 68.3; Aug: 66.8; Sep: 59.2; Oct: 48.9; Nov: 39.7; Dec: 30.1; Jan: 17.6; Feb: 17.42; Mar: 23.5; Apr: 31.46; May: 41; Jun: 51.98; Jul: 58.46; Aug: 57.74; Sep: 51.3; Oct: 41.54; Nov: 34.7; Dec: 24.1
MS | GREENWOOD LEFLORE ARPT | Jan: 44.8; Feb: 48.4; Mar: 56; Apr: 64.2; May: 72.4; Jun: 79.1; Jul: 81.4; Aug: 81.2; Sep: 75.3; Oct: 64.6; Nov: 54.1; Dec: 46.9; Jan: 36.9; Feb: 41.54; Mar: 37; Apr: 52.52; May: 59; Jun: 69.26; Jul: 73.58; Aug: 68.72; Sep: 64.6; Oct: 51.98; Nov: 48.7; Dec: 35.8
SC | GREER GREENV-SPARTANBRG AP | Jan: 42.8; Feb: 45.9; Mar: 52.7; Apr: 60.8; May: 68.5; Jun: 76; Jul: 79.3; Aug: 78.1; Sep: 71.9; Oct: 61.4; Nov: 51.7; Dec: 44.7; Jan: 28.4; Feb: 31.28; Mar: 39.9; Apr: 45.32; May: 56.1; Jun: 62.06; Jul: 67.46; Aug: 67.82; Sep: 62.6; Oct: 46.94; Nov: 38.5; Dec: 30.2
IN | GRISSOM ARB | Jan: 25; Feb: 29; Mar: 40.6; Apr: 51.5; May: 62.6; Jun: 71.1; Jul: 73.9; Aug: 71.9; Sep: 64.4; Oct: 53.2; Nov: 41.1; Dec: 30.7; Jan: 24.6; Feb: 23; Mar: 30.9; Apr: 35.42; May: 44.1; Jun: 58.28; Jul: 63.14; Aug: 62.6; Sep: 48.9; Oct: 42.8; Nov: 32.7; Dec: 32.4
CT | GROTON NEW LONDON AP | Jan: 30.1; Feb: 31.9; Mar: 38.5; Apr: 47.7; May: 56.4; Jun: 65.5; Jul: 71.4; Aug: 70.9; Sep: 64.6; Oct: 54.1; Nov: 45.1; Dec: 35.6; Jan: 20.1; Feb: 19.76; Mar: 32.5; Apr: 38.3; May: 47.8; Jun: 57.92; Jul: 59.54; Aug: 64.58; Sep: 58.8; Oct: 48.2; Nov: 34; Dec: 25.5
MS | GULFPORT BILOXI INT | Jan: 51.5; Feb: 54.3; Mar: 60.2; Apr: 67.8; May: 75; Jun: 80.9; Jul: 82.4; Aug: 82.4; Sep: 78.6; Oct: 69.5; Nov: 59.6; Dec: 53.4; Jan: 47.8; Feb: 48.02; Mar: 49.1; Apr: 57.92; May: 64.9; Jun: 73.4; Jul: 74.12; Aug: 73.04; Sep: 73.2; Oct: 62.06; Nov: 48.6; Dec: 43.5
AK | GULKANA INTERMEDIATE FIELD | Jan: -1.3; Feb: 5.7; Mar: 14.7; Apr: 32; May: 45.5; Jun: 54.7; Jul: 57.3; Aug: 53.5; Sep: 43.2; Oct: 27.3; Nov: 5.6; Dec: -0.8; Jan: -7.8; Feb: -0.04; Mar: 5.9; Apr: 17.24; May: 26.8; Jun: 39.92; Jul: 43.88; Aug: 40.46; Sep: 32; Oct: 23.72; Nov: 3.6; Dec: -4
CO | GUNNISON CO. (AWOS) | Jan: 12.1; Feb: 16.4; Mar: 29.5; Apr: 39.3; May: 48.6; Jun: 57; Jul: 63.1; Aug: 60.8; Sep: 52.9; Oct: 41.8; Nov: 28.1; Dec: 14.3; Jan: 10.4; Feb: 9.86; Mar: 14.7; Apr: 19.4; May: 16.5; Jun: 29.84; Jul: 39.02; Aug: 41; Sep: 23.2; Oct: 22.1; Nov: 12.4; Dec: 2.7
AK | GUSTAVUS | Jan: 28.1; Feb: 30.1; Mar: 32.7; Apr: 39.6; May: 46.7; Jun: 52.7; Jul: 55.8; Aug: 55.6; Sep: 50.1; Oct: 42.4; Nov: 33.3; Dec: 30.3; Jan: 27.9; Feb: 27.5; Mar: 26.2; Apr: 28.76; May: 24.1; Jun: 44.6; Jul: 49.46; Aug: 45.32; Sep: 41; Oct: 35.6; Nov: 19.8; Dec: 18
MD | HAGERSTOWN RGNL RIC | Jan: 31.7; Feb: 33.8; Mar: 42.9; Apr: 54.1; May: 63.5; Jun: 72.3; Jul: 76.1; Aug: 74.4; Sep: 67.1; Oct: 55.6; Nov: 45.6; Dec: 35.5; Jan: 21.4; Feb: 23.18; Mar: 31.1; Apr: 37.58; May: 47.3; Jun: 56.84; Jul: 66.02; Aug: 63.32; Sep: 55.6; Oct: 47.66; Nov: 34.2; Dec: 20.1
NS | HALIFAX | Jan: 22.2; Feb: 23; Mar: 30.2; Apr: 40; May: 49.9; Jun: 59.5; Jul: 66.4; Aug: 66.1; Sep: 59.1; Oct: 48.7; Nov: 38.9; Dec: 29.3; Jan: 16.5; Feb: 15.98; Mar: 22.1; Apr: 30.56; May: 39.6; Jun: 50.18; Jul: 57.74; Aug: 58.1; Sep: 52; Oct: 42.62; Nov: 34; Dec: 23.7
MN | HALLOCK | Jan: 5.1; Feb: 8.8; Mar: 22.7; Apr: 41.4; May: 53.3; Jun: 63.6; Jul: 67.7; Aug: 66.4; Sep: 57.2; Oct: 43.3; Nov: 26.8; Dec: 12.2; Jan: 1.6; Feb: 1.58; Mar: 21.4; Apr: 36.32; May: 34.7; Jun: 56.12; Jul: 61.52; Aug: 58.64; Sep: 43.3; Oct: 37.22; Nov: 15.3; Dec: 10.4
MI | HANCOCK HOUGHTON CO AP | Jan: 16.5; Feb: 18; Mar: 25.9; Apr: 38; May: 50.5; Jun: 60.2; Jul: 65.1; Aug: 64.6; Sep: 56.3; Oct: 44.4; Nov: 32.2; Dec: 21.8; Jan: 5.9; Feb: 11.12; Mar: 25; Apr: 32; May: 34.5; Jun: 51.98; Jul: 57.2; Aug: 57.2; Sep: 52.5; Oct: 32.72; Nov: 27.7; Dec: 18
WA | HANFORD | Jan: 33.8; Feb: 38.4; Mar: 46.9; Apr: 55.3; May: 63.5; Jun: 71.1; Jul: 76.1; Aug: 76.5; Sep: 67.9; Oct: 55.2; Nov: 42.2; Dec: 32.6; Jan: 25.7; Feb: 23; Mar: 29.5; Apr: 30.56; May: 32.7; Jun: 41; Jul: 42.62; Aug: 40.64; Sep: 36; Oct: 31.1; Nov: 31.8; Dec: 24.8
UT | HANKSVILLE AP | Jan: 31; Feb: 37; Mar: 47; Apr: 54; May: 63; Jun: 76; Jul: 82; Aug: 78; Sep: 69; Oct: 55; Nov: 41; Dec: 30; Jan: 23.4; Feb: 23; Mar: 31.6; Apr: 25.34; May: 31.8; Jun: 31.1; Jul: 36.14; Aug: 35.96; Sep: 37.8; Oct: 30.56; Nov: 30.2; Dec: 21.9
TX | HARLINGEN RIO GRANDE VALLEY I | Jan: 61.3; Feb: 64.7; Mar: 69.6; Apr: 75.4; May: 80.6; Jun: 84.5; Jul: 85.3; Aug: 85.7; Sep: 81.8; Oct: 76.2; Nov: 68; Dec: 62.2; Jan: 55.8; Feb: 52.52; Mar: 58.5; Apr: 63.5; May: 70.7; Jun: 73.94; Jul: 72.14; Aug: 73.94; Sep: 71.8; Oct: 69.44; Nov: 56.5; Dec: 58.5
PA | HARRISBURG CAPITAL CITY ARPT | Jan: 31.6; Feb: 33.6; Mar: 42.3; Apr: 53.4; May: 62.9; Jun: 71.8; Jul: 76; Aug: 74.4; Sep: 66.8; Oct: 55.6; Nov: 45.4; Dec: 35.3; Jan: 16.9; Feb: 19.58; Mar: 23.9; Apr: 41; May: 48.2; Jun: 59.72; Jul: 64.76; Aug: 62.96; Sep: 57.9; Oct: 45.32; Nov: 34.3; Dec: 19.2
AR | HARRISON FAA AP | Jan: 37.5; Feb: 41.1; Mar: 49; Apr: 58.7; May: 66.2; Jun: 74.4; Jul: 78.6; Aug: 78; Sep: 69.7; Oct: 59.5; Nov: 48.7; Dec: 39.4; Jan: 27.9; Feb: 28.04; Mar: 38.5; Apr: 43.34; May: 54.9; Jun: 63.86; Jul: 67.1; Aug: 66.2; Sep: 63.1; Oct: 48.92; Nov: 39; Dec: 30.9
WV | HARRISON MARION RGN | Jan: 31.7; Feb: 33.8; Mar: 42.9; Apr: 54.8; May: 62.3; Jun: 69.9; Jul: 72.9; Aug: 72.1; Sep: 65.5; Oct: 54.3; Nov: 44.8; Dec: 36.2; Jan: 25.9; Feb: 26.06; Mar: 32.4; Apr: 43.52; May: 49.3; Jun: 57.92; Jul: 64.58; Aug: 63.5; Sep: 56.5; Oct: 43.7; Nov: 30.2; Dec: 22.3
CT | HARTFORD BRADLEY INTL AP | Jan: 27.4; Feb: 29.7; Mar: 38; Apr: 49.8; May: 59.7; Jun: 68.9; Jul: 74; Aug: 72.2; Sep: 64.4; Oct: 53; Nov: 42.6; Dec: 32.8; Jan: 12.7; Feb: 17.6; Mar: 24.8; Apr: 31.82; May: 44.1; Jun: 57.02; Jul: 62.78; Aug: 60.08; Sep: 52.5; Oct: 41.72; Nov: 28.2; Dec: 19.4
CT | HARTFORD BRAINARD FD | Jan: 29.2; Feb: 31.5; Mar: 39.2; Apr: 50.4; May: 60.2; Jun: 69.4; Jul: 74.8; Aug: 73.2; Sep: 65.7; Oct: 54.2; Nov: 44.1; Dec: 34.2; Jan: 15.6; Feb: 18.86; Mar: 30.6; Apr: 34.7; May: 47.7; Jun: 54.5; Jul: 60.62; Aug: 56.48; Sep: 57.4; Oct: 43.52; Nov: 38.8; Dec: 30.7
NE | HASTINGS MUNICIPAL | Jan: 25.8; Feb: 29.7; Mar: 40.1; Apr: 50.9; May: 61.7; Jun: 71.9; Jul: 77.2; Aug: 74.5; Sep: 65.7; Oct: 53.2; Nov: 39.8; Dec: 28.1; Jan: 17.6; Feb: 17.24; Mar: 29.8; Apr: 40.28; May: 46.8; Jun: 57.38; Jul: 63.68; Aug: 62.78; Sep: 54.1; Oct: 37.04; Nov: 25.3; Dec: 18.5
MS | HATTIESBURG LAUREL | Jan: 48.4; Feb: 51.6; Mar: 58.1; Apr: 65.1; May: 72.9; Jun: 78.9; Jul: 80.8; Aug: 81; Sep: 76.3; Oct: 66.2; Nov: 55.9; Dec: 50; Jan: 32.4; Feb: 38.3; Mar: 50.9; Apr: 53.24; May: 64.6; Jun: 66.74; Jul: 70.34; Aug: 66.2; Sep: 63.7; Oct: 50.36; Nov: 45; Dec: 30.4
MT | HAVRE CITY-COUNTY AP | Jan: 17.7; Feb: 22.1; Mar: 32.1; Apr: 44; May: 53.5; Jun: 61.5; Jul: 69.6; Aug: 68.4; Sep: 58.1; Oct: 44.7; Nov: 30.7; Dec: 20.7; Jan: 12.2; Feb: 14.72; Mar: 15.3; Apr: 29.12; May: 30.9; Jun: 47.3; Jul: 44.42; Aug: 47.84; Sep: 37.2; Oct: 31.1; Nov: 22.1; Dec: 17.8
CO | HAYDEN/YAMPA (AWOS) | Jan: 19.5; Feb: 22.8; Mar: 32.4; Apr: 41.5; May: 51.1; Jun: 60.2; Jul: 67.8; Aug: 65.7; Sep: 57.3; Oct: 45.1; Nov: 31.9; Dec: 20.6; Jan: 13.6; Feb: 16.88; Mar: 18; Apr: 24.8; May: 32; Jun: 38.12; Jul: 37.4; Aug: 35.24; Sep: 32.4; Oct: 23.36; Nov: 20.5; Dec: 12.9
KS | HAYS MUNI (AWOS) | Jan: 29.7; Feb: 32.8; Mar: 42.8; Apr: 52.2; May: 63.2; Jun: 74; Jul: 79.2; Aug: 77.2; Sep: 68.2; Oct: 55.3; Nov: 41.8; Dec: 31; Jan: 21.7; Feb: 24.98; Mar: 26.2; Apr: 39.02; May: 48; Jun: 54.14; Jul: 58.28; Aug: 58.46; Sep: 56.1; Oct: 34.88; Nov: 31.8; Dec: 18.7
CA | HAYWARD AIR TERM | Jan: 50.4; Feb: 52.4; Mar: 55.1; Apr: 56.9; May: 60.4; Jun: 63.3; Jul: 65.6; Aug: 66; Sep: 66.3; Oct: 62.6; Nov: 55.8; Dec: 50.9; Jan: 40.3; Feb: 43.16; Mar: 47.5; Apr: 47.3; May: 52.2; Jun: 53.24; Jul: 55.04; Aug: 55.94; Sep: 55.4; Oct: 51.26; Nov: 45; Dec: 42.1
MT | HELENA REGIONAL AIRPORT | Jan: 23.4; Feb: 27.6; Mar: 36.1; Apr: 44.3; May: 53.5; Jun: 61.1; Jul: 70.4; Aug: 68.6; Sep: 59.1; Oct: 45.8; Nov: 32.8; Dec: 23.1; Jan: 13.8; Feb: 15.62; Mar: 20.8; Apr: 25.88; May: 32.7; Jun: 41.54; Jul: 42.8; Aug: 42.26; Sep: 39.6; Oct: 30.56; Nov: 23.2; Dec: 16.3
KY | HENDERSON CITY | Jan: 33.2; Feb: 36.3; Mar: 46.2; Apr: 57.5; May: 67; Jun: 74.9; Jul: 77.5; Aug: 76.3; Sep: 68.7; Oct: 57.5; Nov: 46; Dec: 36.5; Jan: 27.1; Feb: 26.6; Mar: 28.2; Apr: 39; May: 48; Jun: 58.3; Jul: 62.4; Aug: 56.7; Sep: 54.3; Oct: 41; Nov: 29.7; Dec: 28.9
MN | HIBBING CHISHOLM-HIBBING AP | Jan: 7.9; Feb: 12.9; Mar: 25.1; Apr: 39; May: 51.1; Jun: 60.6; Jul: 64.9; Aug: 63.4; Sep: 54.3; Oct: 41.9; Nov: 27.1; Dec: 13.4; Jan: -1.3; Feb: -2.38; Mar: 18.7; Apr: 25.52; May: 39.4; Jun: 53.6; Jul: 56.66; Aug: 55.4; Sep: 48.7; Oct: 37.4; Nov: 23.2; Dec: 7.3
NC | HICKORY REGIONAL AP | Jan: 40.4; Feb: 43.3; Mar: 50.3; Apr: 59.4; May: 66.9; Jun: 74.6; Jul: 77.4; Aug: 76.4; Sep: 70.1; Oct: 59.5; Nov: 50.1; Dec: 42.4; Jan: 23.4; Feb: 21.38; Mar: 40.1; Apr: 43.88; May: 55.9; Jun: 63.14; Jul: 64.94; Aug: 68; Sep: 60.4; Oct: 45.86; Nov: 40.1; Dec: 30.9
KS | HILL CITY MUNICIPAL AP | Jan: 30.6; Feb: 33.1; Mar: 42.9; Apr: 52.4; May: 63.4; Jun: 73.9; Jul: 80.2; Aug: 77.3; Sep: 68.1; Oct: 54.9; Nov: 41.7; Dec: 31; Jan: 16.9; Feb: 16.7; Mar: 18.5; Apr: 40.46; May: 46; Jun: 57.2; Jul: 66.02; Aug: 55.58; Sep: 54.9; Oct: 37.76; Nov: 26.2; Dec: 22.6
VA | HILLSVILLE | Jan: 35.4; Feb: 37.3; Mar: 44.8; Apr: 54.5; May: 62.2; Jun: 69.4; Jul: 72.4; Aug: 71.7; Sep: 65.1; Oct: 55.7; Nov: 45.4; Dec: 38.3; Jan: 24.6; Feb: 26.06; Mar: 25.7; Apr: 36.5; May: 42.6; Jun: 60.98; Jul: 62.6; Aug: 64.76; Sep: 53.8; Oct: 41; Nov: 29.7; Dec: 27.1
HI | HILO INTERNATIONAL AP | Jan: 71.4; Feb: 71.1; Mar: 71.7; Apr: 72.4; May: 74; Jun: 75; Jul: 76; Aug: 76.5; Sep: 76.4; Oct: 75.7; Nov: 74; Dec: 72.3; Jan: 62.6; Feb: 64.22; Mar: 63.7; Apr: 65.3; May: 67.1; Jun: 67.46; Jul: 69.08; Aug: 68.54; Sep: 68.5; Oct: 68.54; Nov: 67.6; Dec: 64.4
OK | HOBART MUNICIPAL AP | Jan: 39.2; Feb: 43.1; Mar: 51; Apr: 59.7; May: 69.9; Jun: 79.6; Jul: 83.8; Aug: 82.8; Sep: 74.4; Oct: 62.4; Nov: 49.6; Dec: 40.1; Jan: 24.6; Feb: 30.02; Mar: 44.4; Apr: 49.46; May: 57.7; Jun: 63.68; Jul: 65.48; Aug: 59.18; Sep: 59; Oct: 50.72; Nov: 37.6; Dec: 22.6
NM | HOLLOMAN AFB | Jan: 41; Feb: 46; Mar: 52.8; Apr: 61.1; May: 70.2; Jun: 79.5; Jul: 80.3; Aug: 78.9; Sep: 72.5; Oct: 61.4; Nov: 48.8; Dec: 41.2; Jan: 27.7; Feb: 29.3; Mar: 28.6; Apr: 32.72; May: 28.2; Jun: 38.48; Jul: 43.52; Aug: 53.06; Sep: 39.7; Oct: 33.98; Nov: 31.3; Dec: 26.2
AK | HOMER ARPT | Jan: 24.7; Feb: 26.6; Mar: 29; Apr: 37.5; May: 44.8; Jun: 50.9; Jul: 54.9; Aug: 54.2; Sep: 48.7; Oct: 39.3; Nov: 29.6; Dec: 26.6; Jan: 20.5; Feb: 11.66; Mar: 20.8; Apr: 31.46; May: 37.2; Jun: 42.98; Jul: 48.56; Aug: 49.1; Sep: 45; Oct: 34.88; Nov: 17.2; Dec: 17.2
FL | HOMESTEAD AFB | Jan: 67.4; Feb: 69.5; Mar: 71.9; Apr: 75.1; May: 78.6; Jun: 81.6; Jul: 82.8; Aug: 83.1; Sep: 81.9; Oct: 78.8; Nov: 73.1; Dec: 70; Jan: 50; Feb: 55.22; Mar: 63.5; Apr: 62.24; May: 71.2; Jun: 73.76; Jul: 75.2; Aug: 73.76; Sep: 74.8; Oct: 70.7; Nov: 62.6; Dec: 60.4
TX | HONDO MUNICIPAL AP | Jan: 51.8; Feb: 56; Mar: 62.3; Apr: 69.6; May: 76.6; Jun: 82.4; Jul: 83.4; Aug: 84.4; Sep: 79.1; Oct: 70.8; Nov: 59.8; Dec: 52.5; Jan: 40.3; Feb: 42.8; Mar: 51.4; Apr: 57.56; May: 64.6; Jun: 70.34; Jul: 66.74; Aug: 69.08; Sep: 66; Oct: 63.68; Nov: 49.3; Dec: 33.4
HI | HONOLULU INTL ARPT | Jan: 73.4; Feb: 73.6; Mar: 74.4; Apr: 76.3; May: 77.9; Jun: 80.1; Jul: 81.1; Aug: 81.9; Sep: 81.4; Oct: 80.1; Nov: 77.6; Dec: 75.2; Jan: 60.6; Feb: 64.76; Mar: 62.2; Apr: 61.7; May: 64.8; Jun: 65.66; Jul: 67.1; Aug: 67.28; Sep: 68.7; Oct: 67.46; Nov: 65.5; Dec: 63.9
AK | HOONAH | Jan: 31; Feb: 30; Mar: 32; Apr: 39; May: 47; Jun: 53; Jul: 57; Aug: 57; Sep: 50; Oct: 42; Nov: 34; Dec: 31; Jan: 22.1; Feb: 24.98; Mar: 22.1; Apr: 32.54; May: 34.3; Jun: 46.58; Jul: 51.8; Aug: 50.18; Sep: 42.1; Oct: 36.86; Nov: 29.3; Dec: 25.9
AK | HOOPER BAY | Jan: 11.6; Feb: 15; Mar: 12.3; Apr: 25.1; May: 35; Jun: 45.7; Jul: 50.7; Aug: 51.4; Sep: 45.7; Oct: 33.3; Nov: 23.4; Dec: 13.3; Jan: 4.8; Feb: 6.08; Mar: 20.1; Apr: 21.38; May: 32.4; Jun: 35.78; Jul: 44.06; Aug: 43.52; Sep: 36; Oct: 27.32; Nov: 25.3; Dec: 9.1
WA | HOQUIAM AP | Jan: 43.1; Feb: 43.8; Mar: 45.8; Apr: 48.6; May: 53.2; Jun: 57.3; Jul: 60.3; Aug: 60.9; Sep: 59.1; Oct: 52.7; Nov: 46; Dec: 42.5; Jan: 39.9; Feb: 37.58; Mar: 40.3; Apr: 43.34; May: 44.4; Jun: 51.26; Jul: 54.86; Aug: 54.68; Sep: 53.6; Oct: 47.66; Nov: 43; Dec: 40.6
VA | HOT SPRINGS/INGALLS | Jan: 28.3; Feb: 30.7; Mar: 38.3; Apr: 48.9; May: 57.8; Jun: 65.5; Jul: 69; Aug: 68.1; Sep: 61.1; Oct: 51.4; Nov: 40.3; Dec: 32.3; Jan: 24.3; Feb: 20.48; Mar: 27.7; Apr: 32.72; May: 37; Jun: 51.08; Jul: 58.28; Aug: 55.4; Sep: 45.7; Oct: 38.3; Nov: 30.4; Dec: 25.7
MI | HOUGHTON LAKE ROSCOMMON CO AR | Jan: 19.5; Feb: 20.7; Mar: 30.1; Apr: 42.8; May: 54.7; Jun: 64.1; Jul: 67.5; Aug: 65.7; Sep: 58; Oct: 46.9; Nov: 35.7; Dec: 25.4; Jan: 11.3; Feb: 10.04; Mar: 22.8; Apr: 29.48; May: 43; Jun: 51.44; Jul: 59; Aug: 57.56; Sep: 50.9; Oct: 38.12; Nov: 27; Dec: 19.8
ME | HOULTON INTL ARPT | Jan: 13; Feb: 15.3; Mar: 26.1; Apr: 38.9; May: 51.2; Jun: 60.7; Jul: 66.1; Aug: 64.4; Sep: 55.8; Oct: 44.5; Nov: 33.2; Dec: 21.2; Jan: 1.4; Feb: 9.86; Mar: 15.1; Apr: 29.48; May: 46.2; Jun: 48.74; Jul: 58.46; Aug: 53.6; Sep: 51.4; Oct: 41.36; Nov: 25; Dec: 11.7
TX | HOUSTON BUSH INTERCONTINENTAL | Jan: 53.6; Feb: 57; Mar: 62.9; Apr: 69.6; May: 77; Jun: 82.4; Jul: 84; Aug: 84.4; Sep: 79.7; Oct: 71.1; Nov: 61.3; Dec: 54.8; Jan: 41.5; Feb: 43.52; Mar: 49.1; Apr: 59.54; May: 65.8; Jun: 71.78; Jul: 72.86; Aug: 73.22; Sep: 67.6; Oct: 57.38; Nov: 53.8; Dec: 43.7
TX | HOUSTON ELLINGTON AFB [CLEAR LAKE - UT] | Jan: 55; Feb: 58.2; Mar: 63; Apr: 69.8; May: 77; Jun: 82.5; Jul: 84.4; Aug: 84.4; Sep: 80.7; Oct: 72.4; Nov: 62.4; Dec: 56.2; Jan: 42.3; Feb: 46.04; Mar: 44.2; Apr: 56.48; May: 67.3; Jun: 72.14; Jul: 72.5; Aug: 74.48; Sep: 67.5; Oct: 61.34; Nov: 55.2; Dec: 47.3
TX | HOUSTON WILLIAM P HOBBY AP | Jan: 55.2; Feb: 58.3; Mar: 63.8; Apr: 70.2; May: 77.2; Jun: 82.6; Jul: 84; Aug: 84.5; Sep: 80.5; Oct: 72.3; Nov: 62.7; Dec: 56.4; Jan: 54.7; Feb: 52.52; Mar: 54.9; Apr: 55.04; May: 66.6; Jun: 74.12; Jul: 73.4; Aug: 71.78; Sep: 66.4; Oct: 57.2; Nov: 52; Dec: 45.3
TX | HOUSTON/D.W. HOOKS | Jan: 53; Feb: 56; Mar: 62.3; Apr: 69.4; May: 76.4; Jun: 82; Jul: 83.3; Aug: 84.1; Sep: 79.5; Oct: 70.3; Nov: 60.8; Dec: 53.4; Jan: 44.8; Feb: 50.36; Mar: 53.2; Apr: 64.76; May: 66.6; Jun: 71.96; Jul: 73.4; Aug: 70.88; Sep: 68; Oct: 68.54; Nov: 48.2; Dec: 43.9
MI | HOWELL | Jan: 24.8; Feb: 26.5; Mar: 35.5; Apr: 47.7; May: 58.4; Jun: 68.2; Jul: 71.7; Aug: 69.8; Sep: 63; Oct: 51.4; Nov: 40.6; Dec: 29.5; Jan: 15.4; Feb: 18.14; Mar: 30.7; Apr: 36.5; May: 42.6; Jun: 60.62; Jul: 61.52; Aug: 61.52; Sep: 54.3; Oct: 40.46; Nov: 34.9; Dec: 24.1
GA | HUNTER AAF | Jan: 51; Feb: 54.6; Mar: 60.4; Apr: 66.7; May: 74.4; Jun: 80.1; Jul: 82.8; Aug: 81.7; Sep: 77.6; Oct: 68.7; Nov: 59.6; Dec: 53.5; Jan: 36.1; Feb: 40.82; Mar: 43.3; Apr: 48.56; May: 65.1; Jun: 69.08; Jul: 73.76; Aug: 71.06; Sep: 68.5; Oct: 52.7; Nov: 47.1; Dec: 34.3
IN | HUNTINGBURG | Jan: 32.7; Feb: 36.3; Mar: 45.4; Apr: 56.2; May: 65; Jun: 73.2; Jul: 76.5; Aug: 75.7; Sep: 68; Oct: 57; Nov: 45.9; Dec: 37; Jan: 33.4; Feb: 30.2; Mar: 37; Apr: 36.68; May: 55.9; Jun: 62.96; Jul: 66.56; Aug: 68.9; Sep: 55.6; Oct: 47.84; Nov: 35.4; Dec: 28.6
WV | HUNTINGTON TRI-STATE ARPT | Jan: 34.8; Feb: 37.9; Mar: 46.1; Apr: 57; May: 64.4; Jun: 72.4; Jul: 75.7; Aug: 74.6; Sep: 67.7; Oct: 56.6; Nov: 46.5; Dec: 38.1; Jan: 24.1; Feb: 23.54; Mar: 33.6; Apr: 38.84; May: 55; Jun: 61.7; Jul: 66.56; Aug: 65.66; Sep: 58.8; Oct: 41; Nov: 32.9; Dec: 26.1
AL | HUNTSVILLE INTL/JONES FIELD | Jan: 41.8; Feb: 45.4; Mar: 53; Apr: 61.8; May: 69.9; Jun: 77.2; Jul: 79.7; Aug: 79.3; Sep: 73.3; Oct: 62.3; Nov: 51.5; Dec: 44.2; Jan: 26.6; Feb: 32.54; Mar: 41; Apr: 45.86; May: 57.6; Jun: 65.3; Jul: 68; Aug: 68; Sep: 60.8; Oct: 47.48; Nov: 44.8; Dec: 30.7
SD | HURON REGIONAL ARPT | Jan: 15.9; Feb: 21.4; Mar: 33; Apr: 46.1; May: 58; Jun: 68; Jul: 73.5; Aug: 71.7; Sep: 62.6; Oct: 48.3; Nov: 32.9; Dec: 20.4; Jan: 10.6; Feb: 13.64; Mar: 21; Apr: 31.82; May: 43.7; Jun: 56.3; Jul: 59.9; Aug: 57.38; Sep: 46.2; Oct: 34.7; Nov: 20.7; Dec: 8.2
AK | HUSLIA | Jan: -3; Feb: 6; Mar: 7.8; Apr: 26; May: 45; Jun: 57; Jul: 59; Aug: 53; Sep: 43; Oct: 25; Nov: 7.1; Dec: 1.5; Jan: -14.6; Feb: 4.46; Mar: 5.4; Apr: 16.52; May: 27; Jun: 33.98; Jul: 43.34; Aug: 37.58; Sep: 27.7; Oct: 26.6; Nov: 2.7; Dec: 3.6
MN | HUTCHINSON (AWOS) | Jan: 13.4; Feb: 17.4; Mar: 29.3; Apr: 45.1; May: 56.9; Jun: 67.2; Jul: 71.6; Aug: 68.7; Sep: 61; Oct: 47.9; Nov: 33.2; Dec: 19.9; Jan: 12.9; Feb: 8.42; Mar: 17.2; Apr: 35.24; May: 44.4; Jun: 55.94; Jul: 67.1; Aug: 59.54; Sep: 52.3; Oct: 34.7; Nov: 25.5; Dec: 19.4
KS | HUTCHINSON MUNICIPAL AP | Jan: 32; Feb: 35.3; Mar: 45.6; Apr: 55.6; May: 66; Jun: 75.5; Jul: 80.5; Aug: 79.2; Sep: 69.8; Oct: 57.5; Nov: 44.4; Dec: 33.1; Jan: 23.4; Feb: 29.3; Mar: 35.8; Apr: 41.9; May: 55.2; Jun: 63.68; Jul: 64.58; Aug: 64.58; Sep: 55.9; Oct: 47.84; Nov: 34.9; Dec: 20.1
AK | HYDABURG SEAPLANE | Jan: 36.5; Feb: 37.4; Mar: 38.4; Apr: 42.6; May: 47.5; Jun: 53.1; Jul: 56.6; Aug: 57.3; Sep: 53.3; Oct: 47.7; Nov: 41.1; Dec: 38.3; Jan: 27.7; Feb: 26.96; Mar: 23.4; Apr: 32.36; May: 34.3; Jun: 42.26; Jul: 48.74; Aug: 46.58; Sep: 39.2; Oct: 36.68; Nov: 32.9; Dec: 30.2
ID | IDAHO FALLS FANNING FIELD | Jan: 20.5; Feb: 25; Mar: 36.5; Apr: 44.9; May: 53.1; Jun: 60.5; Jul: 68.9; Aug: 67.1; Sep: 58.3; Oct: 45.8; Nov: 32.6; Dec: 22.4; Jan: 14.9; Feb: 16.88; Mar: 28.4; Apr: 29.48; May: 36; Jun: 41.36; Jul: 46.76; Aug: 41.18; Sep: 34.7; Oct: 32.54; Nov: 24.8; Dec: 20.8
AK | ILIAMNA ARPT | Jan: 16.8; Feb: 21.7; Mar: 21.9; Apr: 33.6; May: 44.1; Jun: 51.6; Jul: 55.7; Aug: 55; Sep: 48.5; Oct: 36.3; Nov: 24.8; Dec: 19.8; Jan: 23.2; Feb: 26.6; Mar: 24.3; Apr: 24.26; May: 29.5; Jun: 40.46; Jul: 48.2; Aug: 47.66; Sep: 36.9; Oct: 21.38; Nov: 21; Dec: 19.6
CA | IMPERIAL | Jan: 56.3; Feb: 59.4; Mar: 65.4; Apr: 70.8; May: 78.9; Jun: 86.8; Jul: 92.9; Aug: 93; Sep: 87.5; Oct: 75.3; Nov: 63.6; Dec: 55.1; Jan: 33.3; Feb: 43.16; Mar: 44.2; Apr: 42.8; May: 43.2; Jun: 50.72; Jul: 54.5; Aug: 60.8; Sep: 56.1; Oct: 45.32; Nov: 33.3; Dec: 27.1
NE | IMPERIAL MUNI AP | Jan: 30; Feb: 30; Mar: 41; Apr: 50; May: 59; Jun: 71; Jul: 77; Aug: 74; Sep: 66; Oct: 52; Nov: 39; Dec: 29; Jan: 19.4; Feb: 21.2; Mar: 20.7; Apr: 33.98; May: 39.9; Jun: 55.22; Jul: 59.9; Aug: 57.2; Sep: 47.1; Oct: 37.4; Nov: 24.6; Dec: 20.1
IN | INDIANAPOLIS INTL AP | Jan: 28.8; Feb: 32.6; Mar: 42.6; Apr: 53.7; May: 63.2; Jun: 72.3; Jul: 75.5; Aug: 74.6; Sep: 67.2; Oct: 55.3; Nov: 43.6; Dec: 33.1; Jan: 18.7; Feb: 18.68; Mar: 31.5; Apr: 39.2; May: 49.1; Jun: 62.42; Jul: 65.84; Aug: 62.78; Sep: 55.9; Oct: 40.1; Nov: 32; Dec: 22.3
MN | INTERNATIONAL FALLS INTL AP | Jan: 5.6; Feb: 11.1; Mar: 24.1; Apr: 39; May: 51.6; Jun: 61.4; Jul: 65.2; Aug: 63.6; Sep: 54.5; Oct: 41.7; Nov: 26.5; Dec: 11.6; Jan: -4; Feb: 1.94; Mar: 12.6; Apr: 23.36; May: 38.3; Jun: 52.88; Jul: 58.64; Aug: 56.48; Sep: 46; Oct: 33.98; Nov: 19.6; Dec: -0.6
NU | IQALUIT | Jan: -14.9; Feb: -16.4; Mar: -8.3; Apr: 7.9; May: 25.9; Jun: 38.8; Jul: 47; Aug: 45.2; Sep: 37.1; Oct: 26.5; Nov: 12.1; Dec: -2.8; Jan: -23.6; Feb: -22.36; Mar: -13.9; Apr: 3.2; May: 21.6; Jun: 32.54; Jul: 41; Aug: 40.1; Sep: 32.2; Oct: 22.82; Nov: 7.9; Dec: -7.8
MI | IRON MOUNTAIN/FORD | Jan: 15.3; Feb: 18; Mar: 27.9; Apr: 41; May: 53.1; Jun: 63.1; Jul: 67.5; Aug: 65.4; Sep: 57.4; Oct: 45; Nov: 32.5; Dec: 20.3; Jan: 5.5; Feb: 16.16; Mar: 24.3; Apr: 33.98; May: 37.4; Jun: 56.3; Jul: 58.46; Aug: 59.18; Sep: 53.8; Oct: 35.78; Nov: 27.5; Dec: 5.5
MI | IRONWOOD (AWOS) | Jan: 14.1; Feb: 17; Mar: 26.9; Apr: 39.6; May: 52; Jun: 61.4; Jul: 65.7; Aug: 63.6; Sep: 56.1; Oct: 44.8; Nov: 31.8; Dec: 19.7; Jan: -0.6; Feb: 14.18; Mar: 11.5; Apr: 27.5; May: 37; Jun: 48.2; Jul: 57.56; Aug: 54.86; Sep: 49.3; Oct: 30.56; Nov: 25.9; Dec: 13.1
NY | ISLIP LONG ISL MACARTHUR AP | Jan: 32.1; Feb: 33.2; Mar: 39.9; Apr: 49.7; May: 59.2; Jun: 68.9; Jul: 74.6; Aug: 73.3; Sep: 66.3; Oct: 55.5; Nov: 45.6; Dec: 37; Jan: 18.7; Feb: 25.52; Mar: 30.4; Apr: 39.74; May: 49.1; Jun: 60.26; Jul: 68.36; Aug: 64.94; Sep: 58.1; Oct: 44.78; Nov: 37.9; Dec: 27.3
CA | JACK NORTHROP FLD H | Jan: 58.6; Feb: 58.3; Mar: 60.1; Apr: 61.5; May: 64.8; Jun: 67; Jul: 70.3; Aug: 70.8; Sep: 70.5; Oct: 67.5; Nov: 63; Dec: 57.8; Jan: 45; Feb: 45.68; Mar: 49.8; Apr: 46.58; May: 52.2; Jun: 56.3; Jul: 59.9; Aug: 58.82; Sep: 57.9; Oct: 55.04; Nov: 44.4; Dec: 40.5
WY | JACKSON HOLE | Jan: 15.8; Feb: 16.8; Mar: 26.8; Apr: 35.8; May: 45.5; Jun: 52.4; Jul: 59.9; Aug: 59; Sep: 50.2; Oct: 39.6; Nov: 25.1; Dec: 15.6; Jan: 16.7; Feb: 8.42; Mar: 20.5; Apr: 23.54; May: 26.8; Jun: 36.5; Jul: 35.06; Aug: 40.82; Sep: 36.7; Oct: 25.34; Nov: 18.3; Dec: 13.8
MS | JACKSON INTERNATIONAL AP | Jan: 47.1; Feb: 50.5; Mar: 57.4; Apr: 64.8; May: 72.7; Jun: 79.4; Jul: 81.6; Aug: 81.5; Sep: 76.2; Oct: 65.5; Nov: 55.1; Dec: 48.7; Jan: 36; Feb: 37.76; Mar: 49.3; Apr: 53.78; May: 61.5; Jun: 68.54; Jul: 73.4; Aug: 69.98; Sep: 59.7; Oct: 52.52; Nov: 46; Dec: 37
KY | JACKSON JULIAN CARROLL AP | Jan: 35.7; Feb: 39.2; Mar: 47.4; Apr: 57.8; May: 64.8; Jun: 72; Jul: 75; Aug: 74.3; Sep: 68.1; Oct: 57.9; Nov: 47.9; Dec: 39; Jan: 27.5; Feb: 28.4; Mar: 31.1; Apr: 43.9; May: 54.9; Jun: 63.1; Jul: 68.2; Aug: 64.2; Sep: 55.8; Oct: 46.2; Nov: 32.4; Dec: 32.7
TN | JACKSON MCKELLAR-SIPES REGL A | Jan: 39.7; Feb: 43.2; Mar: 51.3; Apr: 60.8; May: 69.1; Jun: 76.6; Jul: 79.4; Aug: 78.8; Sep: 71.6; Oct: 60.7; Nov: 49.8; Dec: 42; Jan: 28; Feb: 37.4; Mar: 42.3; Apr: 52.34; May: 54.7; Jun: 66.2; Jul: 68.18; Aug: 65.3; Sep: 61.9; Oct: 48.92; Nov: 43.9; Dec: 32.9
MI | JACKSON REYNOLDS FIELD | Jan: 24.2; Feb: 26.3; Mar: 35.5; Apr: 47.7; May: 58.1; Jun: 67.5; Jul: 70.9; Aug: 69.3; Sep: 61.7; Oct: 50.7; Nov: 39.6; Dec: 29.2; Jan: 21.9; Feb: 12.38; Mar: 30.4; Apr: 37.76; May: 50.9; Jun: 57.38; Jul: 62.42; Aug: 62.24; Sep: 53.1; Oct: 44.06; Nov: 33.4; Dec: 18
NC | JACKSONVILLE (AWOS) | Jan: 43.8; Feb: 45.8; Mar: 52.4; Apr: 60.8; May: 68.8; Jun: 76.1; Jul: 79.8; Aug: 78.1; Sep: 72.5; Oct: 62.5; Nov: 52.5; Dec: 45.9; Jan: 30.2; Feb: 30.92; Mar: 33.8; Apr: 38.12; May: 59.4; Jun: 61.52; Jul: 65.84; Aug: 65.66; Sep: 63.1; Oct: 47.3; Nov: 36.9; Dec: 28.2
FL | JACKSONVILLE INTL ARPT | Jan: 54; Feb: 56.9; Mar: 61.7; Apr: 67.3; May: 74.2; Jun: 79.7; Jul: 82; Aug: 81.5; Sep: 78; Oct: 70.3; Nov: 61.4; Dec: 55.9; Jan: 42.3; Feb: 46.4; Mar: 53.8; Apr: 57.2; May: 61.3; Jun: 71.06; Jul: 73.58; Aug: 72.86; Sep: 70.2; Oct: 59.72; Nov: 56.7; Dec: 48.7
FL | JACKSONVILLE NAS | Jan: 56.5; Feb: 59.5; Mar: 64.4; Apr: 70.5; May: 77.3; Jun: 81.9; Jul: 83.9; Aug: 83.6; Sep: 80.8; Oct: 73.4; Nov: 64.6; Dec: 58.8; Jan: 49.8; Feb: 49.1; Mar: 57.2; Apr: 57.2; May: 66.4; Jun: 71.96; Jul: 73.76; Aug: 73.4; Sep: 69.6; Oct: 60.8; Nov: 50.9; Dec: 46.9
FL | JACKSONVILLE/CRAIG | Jan: 55; Feb: 57.5; Mar: 62; Apr: 68; May: 74.6; Jun: 80; Jul: 82.2; Aug: 81.8; Sep: 78.6; Oct: 71.6; Nov: 62.9; Dec: 57.2; Jan: 49.1; Feb: 52.34; Mar: 53.6; Apr: 55.4; May: 65.5; Jun: 71.06; Jul: 75.02; Aug: 71.96; Sep: 69.8; Oct: 63.14; Nov: 60.4; Dec: 47.5
NY | JAMESTOWN (AWOS) | Jan: 23; Feb: 24.7; Mar: 32.6; Apr: 44.9; May: 55.5; Jun: 63.9; Jul: 67.5; Aug: 65.9; Sep: 59.3; Oct: 49; Nov: 37.8; Dec: 28.4; Jan: 25.7; Feb: 14; Mar: 27; Apr: 29.3; May: 39.4; Jun: 53.6; Jul: 57.2; Aug: 55.04; Sep: 45.1; Oct: 39.56; Nov: 28.9; Dec: 26.2
ND | JAMESTOWN MUNICIPAL ARPT | Jan: 10.5; Feb: 15.1; Mar: 27.2; Apr: 42.1; May: 54.9; Jun: 64.7; Jul: 69.6; Aug: 68.1; Sep: 58.8; Oct: 44.6; Nov: 28.5; Dec: 15.3; Jan: -0.8; Feb: 13.46; Mar: 22.1; Apr: 35.42; May: 38.1; Jun: 55.76; Jul: 60.8; Aug: 60.44; Sep: 48.7; Oct: 28.4; Nov: 25; Dec: 3.9
WI | JANESVILLE/ROCK CO. | Jan: 22.5; Feb: 25.4; Mar: 36.6; Apr: 49; May: 58.1; Jun: 67.4; Jul: 71.7; Aug: 71; Sep: 63.7; Oct: 52; Nov: 40.8; Dec: 25.1; Jan: 24.8; Feb: 26.42; Mar: 24.3; Apr: 27.86; May: 40.8; Jun: 52.7; Jul: 57.56; Aug: 58.1; Sep: 50.2; Oct: 36.68; Nov: 29.5; Dec: 28.8
MO | JEFFERSON CITY MEM | Jan: 32.3; Feb: 36.2; Mar: 46; Apr: 57.1; May: 65.8; Jun: 74.6; Jul: 78.7; Aug: 77.2; Sep: 68.6; Oct: 57.6; Nov: 46.5; Dec: 35.2; Jan: 26.6; Feb: 31.46; Mar: 33.8; Apr: 45.86; May: 52.2; Jun: 64.4; Jul: 67.28; Aug: 68.72; Sep: 62.6; Oct: 47.66; Nov: 39; Dec: 26.1
PA | JOHNSTOWN CAMBRIA COUNTY AP | Jan: 26.2; Feb: 27.7; Mar: 36.3; Apr: 48.2; May: 57.5; Jun: 65.6; Jul: 69.3; Aug: 67.9; Sep: 60.9; Oct: 50.3; Nov: 39.9; Dec: 30.2; Jan: 18.5; Feb: 19.04; Mar: 28.6; Apr: 40.1; May: 45; Jun: 55.94; Jul: 61.88; Aug: 60.26; Sep: 53.8; Oct: 38.3; Nov: 32.9; Dec: 13.6
AR | JONESBORO MUNI | Jan: 38.7; Feb: 42.3; Mar: 50.7; Apr: 61; May: 69.9; Jun: 78.7; Jul: 81; Aug: 80.5; Sep: 73.2; Oct: 61.7; Nov: 49.9; Dec: 40.6; Jan: 24.1; Feb: 31.64; Mar: 40.8; Apr: 52.7; May: 57.7; Jun: 64.58; Jul: 69.8; Aug: 66.38; Sep: 64.6; Oct: 49.82; Nov: 37.6; Dec: 21.6
QC | JONQUIERE | Jan: 5.4; Feb: 9.5; Mar: 21.6; Apr: 36.9; May: 51; Jun: 61.2; Jul: 65.6; Aug: 63.3; Sep: 54.8; Oct: 43.1; Nov: 30.1; Dec: 15.5; Jan: -2; Feb: 1.76; Mar: 12; Apr: 24.44; May: 35.4; Jun: 48.92; Jul: 55.58; Aug: 54.5; Sep: 47.5; Oct: 35.78; Nov: 25.9; Dec: 7.9
MO | JOPLIN MUNICIPAL AP | Jan: 35.6; Feb: 40; Mar: 48.6; Apr: 58.3; May: 66.7; Jun: 75.5; Jul: 80; Aug: 79.5; Sep: 70.5; Oct: 59.6; Nov: 48.3; Dec: 38.2; Jan: 21.7; Feb: 30.74; Mar: 41; Apr: 48.92; May: 59.4; Jun: 64.58; Jul: 65.12; Aug: 66.92; Sep: 64.6; Oct: 46.76; Nov: 43.5; Dec: 29.5
ID | JOSLIN FLD MAGIC VA [TWIN FALLS - UO] | Jan: 30.4; Feb: 33.7; Mar: 41.8; Apr: 47.2; May: 56.4; Jun: 64.9; Jul: 75.4; Aug: 72.9; Sep: 63.9; Oct: 50.8; Nov: 38.5; Dec: 30.1; Jan: 25.3; Feb: 24.98; Mar: 33.1; Apr: 30.02; May: 34.9; Jun: 40.46; Jul: 42.26; Aug: 46.58; Sep: 33.1; Oct: 27.32; Nov: 23; Dec: 25.2
AK | JUNEAU INT ARPT | Jan: 28.1; Feb: 30.2; Mar: 33; Apr: 40.8; May: 48.7; Jun: 54.6; Jul: 56.9; Aug: 56; Sep: 50.2; Oct: 42.2; Nov: 33.5; Dec: 29.7; Jan: 20.5; Feb: 21.02; Mar: 23.4; Apr: 36.5; May: 42.4; Jun: 48.02; Jul: 52.16; Aug: 49.46; Sep: 47.7; Oct: 39.38; Nov: 23; Dec: 25.3
HI | KAHULUI AIRPORT | Jan: 72; Feb: 71.9; Mar: 72.7; Apr: 74.1; May: 75.9; Jun: 77.9; Jul: 78.9; Aug: 79.5; Sep: 79.1; Oct: 78.1; Nov: 75.7; Dec: 73.4; Jan: 64.2; Feb: 64.04; Mar: 62.8; Apr: 65.66; May: 64.8; Jun: 65.66; Jul: 67.28; Aug: 67.28; Sep: 69.3; Oct: 66.2; Nov: 66; Dec: 65.5
MO | KAISER MEM (AWOS) | Jan: 32.2; Feb: 36.2; Mar: 45.3; Apr: 56.2; May: 64.7; Jun: 73.2; Jul: 77.7; Aug: 77.2; Sep: 68.1; Oct: 56.9; Nov: 45.9; Dec: 36.5; Jan: 27.5; Feb: 28.04; Mar: 30.4; Apr: 40.82; May: 55.2; Jun: 64.4; Jul: 67.82; Aug: 66.74; Sep: 61.3; Oct: 45.14; Nov: 37; Dec: 23.5
AK | KAKE SEAPLANE BASE | Jan: 32.4; Feb: 33.3; Mar: 34.8; Apr: 40.5; May: 46.8; Jun: 52.5; Jul: 55.7; Aug: 55.5; Sep: 50.8; Oct: 43.6; Nov: 36.5; Dec: 33.2; Jan: 23.4; Feb: 27.68; Mar: 26.2; Apr: 31.82; May: 34.2; Jun: 44.6; Jul: 46.58; Aug: 46.94; Sep: 42.6; Oct: 37.04; Nov: 28.6; Dec: 26.4
MI | KALAMAZOO BATTLE CR | Jan: 24.6; Feb: 27; Mar: 36.7; Apr: 49.3; May: 59.9; Jun: 69.1; Jul: 72.7; Aug: 70.9; Sep: 63.4; Oct: 51.7; Nov: 41; Dec: 29.7; Jan: 18; Feb: 16.7; Mar: 32.9; Apr: 37.76; May: 43.2; Jun: 55.94; Jul: 61.16; Aug: 62.24; Sep: 54.7; Oct: 41; Nov: 38.1; Dec: 20.8
MT | KALISPELL GLACIER PK INT AR | Jan: 24.3; Feb: 27.4; Mar: 35.2; Apr: 43.2; May: 51.7; Jun: 57.6; Jul: 65.4; Aug: 64.3; Sep: 55.2; Oct: 42.4; Nov: 32.1; Dec: 24; Jan: 18.3; Feb: 23.54; Mar: 22.5; Apr: 32.18; May: 39.4; Jun: 45.14; Jul: 46.22; Aug: 48.2; Sep: 41.5; Oct: 30.2; Nov: 26.2; Dec: 20.7
BC | KAMLOOPS AP | Jan: 26.9; Feb: 32.1; Mar: 40.9; Apr: 49.7; May: 58.3; Jun: 64.6; Jul: 71.4; Aug: 70.1; Sep: 60.9; Oct: 47.5; Nov: 35.9; Dec: 27.9; Jan: 21.2; Feb: 23; Mar: 25.5; Apr: 29.84; May: 37.8; Jun: 44.24; Jul: 47.3; Aug: 46.94; Sep: 43.5; Oct: 36.14; Nov: 28.8; Dec: 21.2
HI | KANEOHE BAY MCAS | Jan: 73.3; Feb: 73.1; Mar: 73.6; Apr: 74.8; May: 76.3; Jun: 77.9; Jul: 78.8; Aug: 79.6; Sep: 79.7; Oct: 78.9; Nov: 76.9; Dec: 74.7; Jan: 62.1; Feb: 63.86; Mar: 63; Apr: 64.4; May: 65.7; Jun: 68; Jul: 68.36; Aug: 68.72; Sep: 69.4; Oct: 67.64; Nov: 67.6; Dec: 62.4
MO | KANSAS CITY DOWNTOWN AP | Jan: 31.7; Feb: 36.3; Mar: 46.3; Apr: 56.7; May: 66.5; Jun: 75.8; Jul: 80.6; Aug: 79.3; Sep: 70.2; Oct: 58.7; Nov: 45.9; Dec: 35; Jan: 23; Feb: 33.08; Mar: 35.1; Apr: 46.94; May: 57.6; Jun: 64.22; Jul: 70.7; Aug: 69.08; Sep: 64.9; Oct: 44.42; Nov: 31.5; Dec: 28.8
MO | KANSAS CITY INT ARPT | Jan: 29.3; Feb: 34.1; Mar: 44.4; Apr: 54.9; May: 64.7; Jun: 73.9; Jul: 78.3; Aug: 77.2; Sep: 68.1; Oct: 56.8; Nov: 44; Dec: 32.8; Jan: 18.3; Feb: 18.32; Mar: 31.1; Apr: 41; May: 54.3; Jun: 63.5; Jul: 65.48; Aug: 65.84; Sep: 56.8; Oct: 45.32; Nov: 27.5; Dec: 19
NE | KEARNEY MUNI (AWOS) | Jan: 25.7; Feb: 29; Mar: 39.5; Apr: 49.7; May: 60.6; Jun: 70.5; Jul: 75.4; Aug: 73.1; Sep: 64.8; Oct: 52; Nov: 38.2; Dec: 27.8; Jan: 14; Feb: 21.56; Mar: 16.3; Apr: 36.32; May: 49.5; Jun: 56.84; Jul: 64.76; Aug: 61.88; Sep: 53.1; Oct: 34.34; Nov: 24.8; Dec: 17.6
MS | KEESLER AFB | Jan: 52; Feb: 55.6; Mar: 60.8; Apr: 68; May: 75.6; Jun: 81.5; Jul: 83; Aug: 83.1; Sep: 79; Oct: 69.9; Nov: 60.2; Dec: 55.2; Jan: 40.8; Feb: 44.96; Mar: 45.5; Apr: 55.76; May: 63.9; Jun: 72.32; Jul: 74.84; Aug: 72.68; Sep: 68; Oct: 55.58; Nov: 51.6; Dec: 44.2
BC | KELOWNA AP | Jan: 27.3; Feb: 30.4; Mar: 38.7; Apr: 46.3; May: 54.6; Jun: 61.1; Jul: 67.8; Aug: 66.4; Sep: 57.3; Oct: 44.8; Nov: 34.6; Dec: 27.3; Jan: 21.4; Feb: 21.38; Mar: 25.3; Apr: 29.66; May: 38.5; Jun: 44.6; Jul: 47.48; Aug: 46.58; Sep: 42.6; Oct: 35.78; Nov: 28.6; Dec: 21.9
WA | KELSO WB AP | Jan: 40.8; Feb: 42.2; Mar: 46.3; Apr: 49.9; May: 55.8; Jun: 60.2; Jul: 65.6; Aug: 65.8; Sep: 61.5; Oct: 52.8; Nov: 45.2; Dec: 40.3; Jan: 35.2; Feb: 36.32; Mar: 41.2; Apr: 41.36; May: 44.1; Jun: 49.46; Jul: 52.7; Aug: 54.5; Sep: 51.1; Oct: 45.14; Nov: 41; Dec: 34.9
AK | KENAI MUNICIPAL AP | Jan: 15.1; Feb: 19.5; Mar: 23.9; Apr: 36.1; May: 45.6; Jun: 52.2; Jul: 55.9; Aug: 54.7; Sep: 47.9; Oct: 35.5; Nov: 22.4; Dec: 17.7; Jan: 24.1; Feb: 27.86; Mar: 20.8; Apr: 28.22; May: 31.6; Jun: 43.16; Jul: 48.38; Aug: 44.78; Sep: 36; Oct: 23.54; Nov: 16.9; Dec: 22.6
IA | KEOKUK MUNI | Jan: 27.4; Feb: 30.7; Mar: 42.5; Apr: 54.1; May: 64.3; Jun: 72.9; Jul: 77.3; Aug: 75.8; Sep: 66.8; Oct: 55.6; Nov: 43.5; Dec: 31.5; Jan: 11.1; Feb: 21.38; Mar: 24.4; Apr: 46.58; May: 54.9; Jun: 56.12; Jul: 67.28; Aug: 64.58; Sep: 59; Oct: 44.78; Nov: 33.1; Dec: 24.8
AK | KETCHIKAN INTL AP | Jan: 34.9; Feb: 35.9; Mar: 37.5; Apr: 42.9; May: 49.2; Jun: 54.7; Jul: 58.1; Aug: 58.5; Sep: 53.2; Oct: 45.7; Nov: 39; Dec: 35.7; Jan: 27; Feb: 24.44; Mar: 21.4; Apr: 32.36; May: 39.2; Jun: 47.48; Jul: 51.62; Aug: 57.02; Sep: 47.1; Oct: 39.74; Nov: 27.7; Dec: 20.7
FL | KEY WEST INTL ARPT | Jan: 69.9; Feb: 71.5; Mar: 73.5; Apr: 76.9; May: 80.5; Jun: 83.5; Jul: 84.8; Aug: 84.9; Sep: 83.5; Oct: 80.5; Nov: 75.6; Dec: 72; Jan: 56.7; Feb: 57.56; Mar: 64.8; Apr: 66.56; May: 69.6; Jun: 73.76; Jul: 74.48; Aug: 74.66; Sep: 75.2; Oct: 72.32; Nov: 69.1; Dec: 63.9
FL | KEY WEST NAS | Jan: 70.1; Feb: 72; Mar: 73.8; Apr: 77.3; May: 80.7; Jun: 83.6; Jul: 84.7; Aug: 84.9; Sep: 83.6; Oct: 80.6; Nov: 75.4; Dec: 72.4; Jan: 59.2; Feb: 61.52; Mar: 63.9; Apr: 65.12; May: 73.2; Jun: 73.4; Jul: 74.48; Aug: 76.1; Sep: 75; Oct: 72.68; Nov: 67.3; Dec: 63.9
TX | KILLEEN MUNI AWOS | Jan: 50; Feb: 53; Mar: 60; Apr: 68; May: 75; Jun: 82; Jul: 85; Aug: 85; Sep: 79; Oct: 69; Nov: 59; Dec: 50; Jan: 31.5; Feb: 32.9; Mar: 34.7; Apr: 43.7; May: 65.1; Jun: 66.56; Jul: 66.92; Aug: 67.64; Sep: 57.9; Oct: 47.84; Nov: 42.1; Dec: 34.5
AK | KING SALMON ARPT | Jan: 15.8; Feb: 19.8; Mar: 22.1; Apr: 34.8; May: 44.5; Jun: 51.5; Jul: 55.4; Aug: 54.8; Sep: 47.8; Oct: 34.7; Nov: 23.3; Dec: 17.4; Jan: 16.5; Feb: 12.56; Mar: 13.3; Apr: 28.22; May: 34.7; Jun: 43.16; Jul: 49.28; Aug: 46.94; Sep: 41.5; Oct: 29.84; Nov: 18.9; Dec: 18
AZ | KINGMAN (AMOS) | Jan: 44; Feb: 47; Mar: 52.6; Apr: 58.7; May: 68.6; Jun: 78; Jul: 83.6; Aug: 82.2; Sep: 75.4; Oct: 63.2; Nov: 51.4; Dec: 42.7; Jan: 18.3; Feb: 26.24; Mar: 30.4; Apr: 23.54; May: 27.7; Jun: 28.94; Jul: 45.5; Aug: 47.48; Sep: 41.7; Oct: 34.52; Nov: 33.4; Dec: 28.2
TX | KINGSVILLE | Jan: 57.8; Feb: 61.8; Mar: 66.9; Apr: 73.6; May: 79.6; Jun: 84.6; Jul: 85.6; Aug: 85.8; Sep: 81.6; Oct: 74.7; Nov: 65.3; Dec: 60; Jan: 51.3; Feb: 42.98; Mar: 57; Apr: 64.4; May: 68; Jun: 71.96; Jul: 74.66; Aug: 72.14; Sep: 66; Oct: 63.14; Nov: 61.5; Dec: 51.1
MO | KIRKSVILLE REGIONAL AP | Jan: 26.7; Feb: 30.2; Mar: 41.6; Apr: 52.9; May: 62.3; Jun: 71.4; Jul: 75.4; Aug: 73.8; Sep: 65.6; Oct: 53.6; Nov: 41.9; Dec: 30; Jan: 15.8; Feb: 21.74; Mar: 31.1; Apr: 41; May: 58.3; Jun: 61.34; Jul: 69.26; Aug: 66.38; Sep: 53.8; Oct: 44.42; Nov: 28.8; Dec: 9
OR | KLAMATH FALLS INTL AP [UO] | Jan: 31.4; Feb: 34.8; Mar: 39.4; Apr: 43.5; May: 51.6; Jun: 58.4; Jul: 67.4; Aug: 65.4; Sep: 59.2; Oct: 47.7; Nov: 37; Dec: 30.3; Jan: 24.1; Feb: 31.46; Mar: 27.7; Apr: 30.92; May: 36.5; Jun: 41; Jul: 47.3; Aug: 44.78; Sep: 40.8; Oct: 34.52; Nov: 29.8; Dec: 26.6
IA | KNOXVILLE | Jan: 25.2; Feb: 28.3; Mar: 39.9; Apr: 52.9; May: 63; Jun: 72; Jul: 76.4; Aug: 74.7; Sep: 66.1; Oct: 53.8; Nov: 42.4; Dec: 29.7; Jan: 17.1; Feb: 14.36; Mar: 25.7; Apr: 43.52; May: 52.9; Jun: 64.04; Jul: 62.6; Aug: 63.68; Sep: 63.5; Oct: 41.9; Nov: 30; Dec: 19.9
TN | KNOXVILLE MCGHEE TYSON AP | Jan: 39.3; Feb: 43; Mar: 50.5; Apr: 59.6; May: 67.6; Jun: 75.1; Jul: 78.2; Aug: 77.6; Sep: 71.3; Oct: 59.9; Nov: 49.1; Dec: 41.6; Jan: 25.3; Feb: 27.86; Mar: 38.1; Apr: 43.16; May: 55.6; Jun: 65.48; Jul: 66.56; Aug: 68; Sep: 59.5; Oct: 49.46; Nov: 40.5; Dec: 29.3
AK | KODIAK AIRPORT | Jan: 30.4; Feb: 31.1; Mar: 32; Apr: 38.1; May: 44.8; Jun: 50.3; Jul: 54.7; Aug: 55.4; Sep: 49.7; Oct: 41; Nov: 34.4; Dec: 30.8; Jan: 25.7; Feb: 26.96; Mar: 24.8; Apr: 30.74; May: 35.2; Jun: 44.24; Jul: 48.74; Aug: 49.46; Sep: 43.9; Oct: 35.06; Nov: 25.3; Dec: 25.3
HI | KONA INTL AT KEAHOL | Jan: 74.7; Feb: 74.7; Mar: 75.6; Apr: 76.6; May: 77.8; Jun: 78.6; Jul: 79.6; Aug: 80.6; Sep: 80.2; Oct: 79.6; Nov: 77.7; Dec: 75.9; Jan: 64.9; Feb: 60.08; Mar: 63.1; Apr: 65.84; May: 64.9; Jun: 69.62; Jul: 69.26; Aug: 67.1; Sep: 68.7; Oct: 68.72; Nov: 65.3; Dec: 62.6
AK | KOTZEBUE RALPH WEIN MEMORIAL | Jan: -3.3; Feb: -0.8; Mar: 0.8; Apr: 15.1; May: 32; Jun: 46.4; Jul: 54.9; Aug: 52.1; Sep: 42.7; Oct: 25.7; Nov: 9.7; Dec: 1.3; Jan: -5.4; Feb: -6.16; Mar: -3.1; Apr: 5.36; May: 27; Jun: 39.38; Jul: 48.56; Aug: 47.84; Sep: 38.3; Oct: 19.76; Nov: 4.5; Dec: -1.3
QC | LA BAIE | Jan: 4.6; Feb: 9; Mar: 19.9; Apr: 36; May: 50.5; Jun: 59.4; Jul: 64; Aug: 62.3; Sep: 54.1; Oct: 42.2; Nov: 29.9; Dec: 14.3; Jan: -0.8; Feb: 2.84; Mar: 13.3; Apr: 25.34; May: 36.1; Jun: 48.56; Jul: 55.76; Aug: 54.68; Sep: 47.8; Oct: 36.32; Nov: 26.6; Dec: 9.9
WI | LA CROSSE MUNICIPAL ARPT | Jan: 18.4; Feb: 22.9; Mar: 34.8; Apr: 48.4; May: 60; Jun: 69.8; Jul: 73.8; Aug: 71.7; Sep: 63.3; Oct: 50.9; Nov: 36.8; Dec: 23.6; Jan: 5.7; Feb: 14.18; Mar: 23.9; Apr: 35.6; May: 44.1; Jun: 59.72; Jul: 65.48; Aug: 61.16; Sep: 50.5; Oct: 35.6; Nov: 26.4; Dec: 8.6
OR | LA GRANDE MUNI AP | Jan: 32.7; Feb: 35.3; Mar: 41.6; Apr: 46.2; May: 53.7; Jun: 60.3; Jul: 69.4; Aug: 67.4; Sep: 59.7; Oct: 48.4; Nov: 38.4; Dec: 32.2; Jan: 24.8; Feb: 27.86; Mar: 27.9; Apr: 33.26; May: 38.8; Jun: 42.8; Jul: 40.1; Aug: 42.98; Sep: 44.4; Oct: 34.34; Nov: 27.5; Dec: 24.6
CO | LA JUNTA MUNICIPAL AP | Jan: 31.9; Feb: 35.5; Mar: 45; Apr: 53; May: 63.3; Jun: 73.7; Jul: 78.5; Aug: 76.5; Sep: 67.9; Oct: 54.6; Nov: 41.5; Dec: 31.7; Jan: 16.7; Feb: 20.84; Mar: 29.3; Apr: 32.9; May: 45.5; Jun: 48.02; Jul: 53.42; Aug: 51.62; Sep: 45.5; Oct: 28.22; Nov: 19.8; Dec: 20.5
QC | LACADIE | Jan: 15.2; Feb: 17.6; Mar: 28.5; Apr: 43; May: 56.5; Jun: 66.1; Jul: 69.5; Aug: 67.3; Sep: 59.8; Oct: 47.8; Nov: 36.3; Dec: 23.4; Jan: 7.3; Feb: 9.5; Mar: 19.4; Apr: 32; May: 43.3; Jun: 55.04; Jul: 60.08; Aug: 59.18; Sep: 52.3; Oct: 40.28; Nov: 31.5; Dec: 15.4
AB | LACOMBE | Jan: 10.8; Feb: 15.4; Mar: 23.9; Apr: 38.2; May: 49.1; Jun: 56.2; Jul: 60.9; Aug: 58.9; Sep: 50.9; Oct: 39.2; Nov: 23.5; Dec: 13.7; Jan: 7; Feb: 9.32; Mar: 16.2; Apr: 26.24; May: 34.3; Jun: 45.5; Jul: 52.16; Aug: 49.1; Sep: 40.6; Oct: 29.3; Nov: 19; Dec: 7.3
NH | LACONIA MUNI (AWOS) | Jan: 20.8; Feb: 23; Mar: 32.5; Apr: 44.4; May: 55.1; Jun: 65.3; Jul: 70; Aug: 68.2; Sep: 60.2; Oct: 48.6; Nov: 38.3; Dec: 28.1; Jan: 18.9; Feb: 12.2; Mar: 25.2; Apr: 25.88; May: 37.2; Jun: 53.6; Jul: 53.06; Aug: 55.58; Sep: 48; Oct: 36.32; Nov: 30.7; Dec: 20.5
IN | LAFAYETTE PURDUE UNIV AP | Jan: 27.4; Feb: 31.1; Mar: 41.3; Apr: 52.7; May: 62.6; Jun: 71.7; Jul: 74.5; Aug: 73.2; Sep: 66.1; Oct: 54.7; Nov: 42.7; Dec: 31.8; Jan: 19; Feb: 19.04; Mar: 35.1; Apr: 45.86; May: 50.5; Jun: 60.62; Jul: 64.76; Aug: 65.3; Sep: 55.4; Oct: 42.44; Nov: 39.9; Dec: 14
LA | LAFAYETTE REGIONAL AP | Jan: 52.8; Feb: 56; Mar: 61.9; Apr: 68.7; May: 76.1; Jun: 81.3; Jul: 82.7; Aug: 83; Sep: 78.8; Oct: 69.8; Nov: 60.3; Dec: 54.4; Jan: 48.4; Feb: 37.76; Mar: 45.3; Apr: 55.4; May: 66; Jun: 70.34; Jul: 74.48; Aug: 75.02; Sep: 67.6; Oct: 58.1; Nov: 55.8; Dec: 40.5
ON | LAGOON CITY | Jan: 16.5; Feb: 18.2; Mar: 27.4; Apr: 40.7; May: 53.9; Jun: 64; Jul: 68.6; Aug: 67.3; Sep: 60; Oct: 48.7; Nov: 36.9; Dec: 25.6; Jan: 11.8; Feb: 13.1; Mar: 20.8; Apr: 32.18; May: 45; Jun: 56.84; Jul: 61.52; Aug: 61.52; Sep: 55.8; Oct: 43.7; Nov: 34; Dec: 19.2
LA | LAKE CHARLES REGIONAL ARPT | Jan: 52.8; Feb: 55.9; Mar: 61.8; Apr: 68.3; May: 75.7; Jun: 81.4; Jul: 82.9; Aug: 83.1; Sep: 79; Oct: 70.2; Nov: 60.5; Dec: 54.3; Jan: 42.1; Feb: 42.62; Mar: 55; Apr: 60.62; May: 65.8; Jun: 72.14; Jul: 74.12; Aug: 74.3; Sep: 71.1; Oct: 58.46; Nov: 53.4; Dec: 43
AK | LAKE HOOD SEAPLANE | Jan: 17.5; Feb: 22.1; Mar: 25.6; Apr: 37.7; May: 49.5; Jun: 57.5; Jul: 60.8; Aug: 58.5; Sep: 50.3; Oct: 37.3; Nov: 23.4; Dec: 19; Jan: 18.9; Feb: 26.06; Mar: 20.3; Apr: 24.98; May: 32.9; Jun: 40.28; Jul: 46.22; Aug: 46.58; Sep: 35.8; Oct: 28.04; Nov: 30.9; Dec: 20.8
OR | LAKEVIEW (AWOS) | Jan: 28.5; Feb: 30.9; Mar: 37.1; Apr: 41.5; May: 50.2; Jun: 57.3; Jul: 66.1; Aug: 63.7; Sep: 56.9; Oct: 45.3; Nov: 34.9; Dec: 27.7; Jan: 22.5; Feb: 22.28; Mar: 25.3; Apr: 31.28; May: 33.4; Jun: 37.04; Jul: 39.92; Aug: 37.04; Sep: 31.8; Oct: 26.6; Nov: 28.9; Dec: 24.1
CO | LAMAR MUNICIPAL | Jan: 30.1; Feb: 33.7; Mar: 43.4; Apr: 52.4; May: 62.9; Jun: 73.4; Jul: 79; Aug: 76.3; Sep: 67.6; Oct: 53.7; Nov: 41; Dec: 30.5; Jan: 23.9; Feb: 26.06; Mar: 15.3; Apr: 28.76; May: 45; Jun: 51.98; Jul: 60.62; Aug: 55.94; Sep: 53.1; Oct: 35.6; Nov: 24.4; Dec: 15.6
HI | LANAI AP | Jan: 68; Feb: 69; Mar: 69; Apr: 71; May: 71; Jun: 73; Jul: 75; Aug: 75; Sep: 75; Oct: 74; Nov: 72; Dec: 70; Jan: 61.7; Feb: 62.78; Mar: 61.2; Apr: 62.96; May: 62.4; Jun: 65.3; Jul: 65.12; Aug: 66.56; Sep: 67.8; Oct: 65.3; Nov: 63.3; Dec: 59.5
PA | LANCASTER | Jan: 29.9; Feb: 31.8; Mar: 41.4; Apr: 51.8; May: 61.8; Jun: 70.9; Jul: 74.7; Aug: 73.2; Sep: 66; Oct: 54.3; Nov: 44.4; Dec: 34.5; Jan: 24.4; Feb: 22.28; Mar: 31.1; Apr: 39.56; May: 54.5; Jun: 61.34; Jul: 60.08; Aug: 60.62; Sep: 58.3; Oct: 44.24; Nov: 36.5; Dec: 22.8
CA | LANCASTER GEN WM FOX FIELD | Jan: 45; Feb: 47.7; Mar: 53.9; Apr: 58.9; May: 67.8; Jun: 75.8; Jul: 82.5; Aug: 81.1; Sep: 74.2; Oct: 62.8; Nov: 51.2; Dec: 43.7; Jan: 25.5; Feb: 27.14; Mar: 38.8; Apr: 35.42; May: 38.7; Jun: 39.92; Jul: 42.26; Aug: 42.08; Sep: 39.7; Oct: 38.12; Nov: 24.6; Dec: 31.1
WY | LANDER HUNT FIELD | Jan: 22.8; Feb: 25.9; Mar: 36.5; Apr: 43.9; May: 53.6; Jun: 63.3; Jul: 72.2; Aug: 70.5; Sep: 60.4; Oct: 46.3; Nov: 32.7; Dec: 22.2; Jan: 12.2; Feb: 7.52; Mar: 18.9; Apr: 22.46; May: 29.3; Jun: 36.5; Jul: 42.44; Aug: 38.48; Sep: 31.3; Oct: 23.54; Nov: 17.1; Dec: 11.7
VA | LANGLEY AFB | Jan: 40.4; Feb: 43; Mar: 49.2; Apr: 58.6; May: 66.7; Jun: 75; Jul: 79.3; Aug: 77.4; Sep: 71.9; Oct: 61.4; Nov: 51.5; Dec: 44.3; Jan: 34.5; Feb: 29.66; Mar: 30.9; Apr: 40.64; May: 55; Jun: 63.68; Jul: 71.96; Aug: 66.2; Sep: 59.7; Oct: 47.48; Nov: 36.9; Dec: 26.1
MI | LANSING CAPITAL CITY ARPT | Jan: 23.5; Feb: 25.5; Mar: 34.8; Apr: 46.8; May: 57.6; Jun: 67.4; Jul: 70.8; Aug: 69.2; Sep: 61.5; Oct: 50.2; Nov: 39.1; Dec: 28.7; Jan: 14.9; Feb: 15.8; Mar: 27.7; Apr: 32.9; May: 47.5; Jun: 55.58; Jul: 61.88; Aug: 59.9; Sep: 54.3; Oct: 41.9; Nov: 33.1; Dec: 21.7
WY | LARAMIE GENERAL BREES FIELD | Jan: 22.4; Feb: 23.7; Mar: 31.9; Apr: 38.1; May: 47.7; Jun: 57.7; Jul: 64.5; Aug: 62.6; Sep: 54.1; Oct: 42.4; Nov: 30.2; Dec: 21.6; Jan: 13.6; Feb: 15.98; Mar: 19.8; Apr: 22.46; May: 33.3; Jun: 35.06; Jul: 45.86; Aug: 41.36; Sep: 40.3; Oct: 24.08; Nov: 17.4; Dec: 14.2
TX | LAREDO INTL AP [UT] | Jan: 58.5; Feb: 62.9; Mar: 69.5; Apr: 76.9; May: 83; Jun: 87.8; Jul: 88.2; Aug: 88.6; Sep: 83.1; Oct: 76.3; Nov: 66.4; Dec: 58.9; Jan: 38.3; Feb: 30.02; Mar: 41.2; Apr: 50.36; May: 61.9; Jun: 69.44; Jul: 68.54; Aug: 69.08; Sep: 63.7; Oct: 55.76; Nov: 50.2; Dec: 38.1
NM | LAS CRUCES INTL AP | Jan: 44; Feb: 48; Mar: 56; Apr: 63; May: 70; Jun: 81; Jul: 82; Aug: 80; Sep: 74; Oct: 64; Nov: 52; Dec: 44; Jan: 26.4; Feb: 29.48; Mar: 31.3; Apr: 26.24; May: 32.7; Jun: 23; Jul: 49.1; Aug: 45.5; Sep: 43; Oct: 42.08; Nov: 26.2; Dec: 12.4
NV | LAS VEGAS MCCARRAN INTL AP | Jan: 48.7; Feb: 52.5; Mar: 60; Apr: 66.9; May: 77; Jun: 86.5; Jul: 92.5; Aug: 90.7; Sep: 82.9; Oct: 69.7; Nov: 56.5; Dec: 47.4; Jan: 23.2; Feb: 24.08; Mar: 29.1; Apr: 25.88; May: 31.5; Jun: 38.12; Jul: 40.64; Aug: 44.6; Sep: 35.4; Oct: 30.56; Nov: 25.7; Dec: 18.9
NM | LAS VEGAS MUNICIPAL ARPT | Jan: 33.2; Feb: 34.1; Mar: 41.6; Apr: 48.9; May: 57.2; Jun: 66.7; Jul: 69.2; Aug: 67.4; Sep: 61.1; Oct: 51.5; Nov: 40.8; Dec: 32.8; Jan: 15.3; Feb: 15.62; Mar: 19.4; Apr: 19.22; May: 28.8; Jun: 35.24; Jul: 51.8; Aug: 50.36; Sep: 46.9; Oct: 30.2; Nov: 18.3; Dec: 9.7
QC | LASSOMPTION | Jan: 13.2; Feb: 16.3; Mar: 27.2; Apr: 42.4; May: 55.8; Jun: 65.2; Jul: 69; Aug: 67.1; Sep: 59.2; Oct: 46.8; Nov: 34.8; Dec: 21.2; Jan: 4.1; Feb: 6.62; Mar: 17.2; Apr: 29.3; May: 41.7; Jun: 53.78; Jul: 59; Aug: 58.1; Sep: 51.3; Oct: 38.84; Nov: 29.5; Dec: 12.7
MA | LAWRENCE MUNI | Jan: 27.5; Feb: 29.6; Mar: 37.3; Apr: 48.4; May: 58; Jun: 66.9; Jul: 72.8; Aug: 71.3; Sep: 64; Oct: 52.3; Nov: 42.7; Dec: 32.8; Jan: 12.7; Feb: 15.62; Mar: 30.9; Apr: 35.96; May: 48.9; Jun: 53.24; Jul: 61.34; Aug: 61.7; Sep: 55.9; Oct: 40.1; Nov: 35.6; Dec: 22.5
OK | LAWTON MUNICIPAL | Jan: 40.8; Feb: 44.5; Mar: 53.7; Apr: 61.9; May: 71.4; Jun: 80.1; Jul: 84.4; Aug: 84.3; Sep: 75.5; Oct: 63.6; Nov: 51.5; Dec: 41.4; Jan: 28; Feb: 36.5; Mar: 34.3; Apr: 55.04; May: 61.2; Jun: 66.38; Jul: 66.38; Aug: 67.1; Sep: 58.6; Oct: 50.36; Nov: 45.3; Dec: 33.3
IA | LE MARS | Jan: 21.1; Feb: 25; Mar: 36.8; Apr: 49.4; May: 60.6; Jun: 71.1; Jul: 74.9; Aug: 72.6; Sep: 63.2; Oct: 51.4; Nov: 36.5; Dec: 24.4; Jan: 16.3; Feb: 12.74; Mar: 35.1; Apr: 41.36; May: 55.9; Jun: 59; Jul: 61.88; Aug: 65.66; Sep: 55.2; Oct: 47.12; Nov: 35.6; Dec: 20.3
CO | LEADVILLE/LAKE CO. | Jan: 17.4; Feb: 17.4; Mar: 24.4; Apr: 31.6; May: 41.3; Jun: 50.8; Jul: 56.3; Aug: 53.6; Sep: 47.2; Oct: 37; Nov: 25.8; Dec: 17.4; Jan: 8.4; Feb: 8.06; Mar: 12.9; Apr: 15.44; May: 18.3; Jun: 27.68; Jul: 38.84; Aug: 28.76; Sep: 37.2; Oct: 20.48; Nov: 10.2; Dec: 5.7
NH | LEBANON MUNICIPAL | Jan: 20.1; Feb: 22.1; Mar: 31.8; Apr: 44.7; May: 56; Jun: 64.9; Jul: 69.8; Aug: 68.2; Sep: 60.6; Oct: 48.1; Nov: 37.7; Dec: 26.6; Jan: 8.1; Feb: 14; Mar: 19.6; Apr: 30.2; May: 38.1; Jun: 55.4; Jul: 59; Aug: 59.18; Sep: 55.2; Oct: 39.38; Nov: 30; Dec: 19
VA | LEESBURG/GODFREY | Jan: 34.8; Feb: 36.9; Mar: 45.5; Apr: 55.7; May: 64.7; Jun: 73.9; Jul: 77.9; Aug: 76.8; Sep: 69.1; Oct: 57.4; Nov: 46.5; Dec: 37.9; Jan: 25; Feb: 21.02; Mar: 26.4; Apr: 34.7; May: 51.6; Jun: 62.06; Jul: 66.2; Aug: 63.68; Sep: 53.1; Oct: 43.34; Nov: 30.2; Dec: 26.4
CA | LEMOORE REEVES NAS | Jan: 47.4; Feb: 52; Mar: 57.4; Apr: 61.8; May: 68.8; Jun: 74.7; Jul: 80.6; Aug: 79.3; Sep: 75.2; Oct: 66; Nov: 54.6; Dec: 46.2; Jan: 39.4; Feb: 43.34; Mar: 38.1; Apr: 40.82; May: 43.2; Jun: 49.1; Jul: 56.12; Aug: 55.58; Sep: 45.7; Oct: 46.94; Nov: 40.1; Dec: 39
QC | LENNOXVILLE | Jan: 15.3; Feb: 18.3; Mar: 28; Apr: 41.8; May: 54; Jun: 63.1; Jul: 67.2; Aug: 65.7; Sep: 58.2; Oct: 46.1; Nov: 35.4; Dec: 22.8; Jan: 7; Feb: 8.96; Mar: 18.5; Apr: 30.2; May: 42.3; Jun: 51.98; Jul: 56.84; Aug: 58.82; Sep: 51.4; Oct: 39.02; Nov: 30.4; Dec: 14.5
AB | LETHBRIDGE | Jan: 20.6; Feb: 24.6; Mar: 30.6; Apr: 41.8; May: 50.9; Jun: 57.9; Jul: 64; Aug: 63.9; Sep: 56; Oct: 43.5; Nov: 30.2; Dec: 22.8; Jan: 12.2; Feb: 13.82; Mar: 18.9; Apr: 25.88; May: 32.4; Jun: 39.74; Jul: 47.84; Aug: 45.14; Sep: 38.8; Oct: 29.12; Nov: 20.3; Dec: 12.7
WV | LEWISBURG/GREENBRIE | Jan: 30.2; Feb: 32.2; Mar: 41; Apr: 51.8; May: 59; Jun: 66.5; Jul: 69.6; Aug: 69.4; Sep: 62.7; Oct: 51.9; Nov: 42.4; Dec: 33.3; Jan: 28.4; Feb: 23; Mar: 31.6; Apr: 37.76; May: 43; Jun: 58.46; Jul: 63.14; Aug: 60.98; Sep: 52.9; Oct: 40.1; Nov: 27.7; Dec: 28.6
ID | LEWISTON NEZ PERCE CNTY AP | Jan: 36.1; Feb: 39.3; Mar: 45.5; Apr: 51.2; May: 59.2; Jun: 65.7; Jul: 75.5; Aug: 74.7; Sep: 66.1; Oct: 52.2; Nov: 41.4; Dec: 34.7; Jan: 27.5; Feb: 29.12; Mar: 30.6; Apr: 35.6; May: 39.9; Jun: 46.4; Jul: 45.5; Aug: 48.2; Sep: 40.1; Oct: 38.84; Nov: 31.5; Dec: 28.2
MT | LEWISTOWN MUNICIPAL ARPT | Jan: 23.4; Feb: 24.4; Mar: 32.4; Apr: 40.4; May: 49.5; Jun: 57.1; Jul: 65.9; Aug: 64.9; Sep: 55.9; Oct: 43.9; Nov: 32.2; Dec: 24.2; Jan: 15.1; Feb: 18.14; Mar: 22.1; Apr: 27.5; May: 36.7; Jun: 46.22; Jul: 45.68; Aug: 45.5; Sep: 40.3; Oct: 31.28; Nov: 22.1; Dec: 14
KY | LEXINGTON BLUEGRASS AP | Jan: 33.6; Feb: 37.1; Mar: 45.5; Apr: 55.8; May: 64.6; Jun: 72.8; Jul: 76.1; Aug: 75.3; Sep: 68.3; Oct: 57.1; Nov: 45.9; Dec: 37.1; Jan: 21.6; Feb: 23.7; Mar: 35.4; Apr: 43.3; May: 55; Jun: 63.7; Jul: 67.1; Aug: 66.9; Sep: 58.6; Oct: 44.1; Nov: 33.3; Dec: 25.9
KS | LIBERAL MUNI | Jan: 33.8; Feb: 36.5; Mar: 45.5; Apr: 54.6; May: 65.1; Jun: 75.1; Jul: 80; Aug: 78; Sep: 69.8; Oct: 57; Nov: 43.9; Dec: 34; Jan: 26.1; Feb: 31.46; Mar: 25.5; Apr: 36.14; May: 52.5; Jun: 57.38; Jul: 60.08; Aug: 64.22; Sep: 57.9; Oct: 41.54; Nov: 32.9; Dec: 23.2
HI | LIHUE AIRPORT | Jan: 71.7; Feb: 71.5; Mar: 72.3; Apr: 73.9; May: 75.7; Jun: 77.9; Jul: 78.9; Aug: 79.5; Sep: 79.4; Oct: 78.3; Nov: 75.7; Dec: 73.4; Jan: 61.3; Feb: 64.4; Mar: 65.3; Apr: 65.84; May: 67.1; Jun: 67.28; Jul: 71.24; Aug: 70.88; Sep: 71.2; Oct: 68.9; Nov: 67.5; Dec: 63.5
CO | LIMON | Jan: 26.9; Feb: 28.7; Mar: 37.6; Apr: 44.9; May: 54.9; Jun: 64.9; Jul: 70.9; Aug: 68.7; Sep: 60.2; Oct: 47.7; Nov: 35.4; Dec: 26.4; Jan: 16.2; Feb: 16.34; Mar: 20.1; Apr: 29.12; May: 43; Jun: 49.64; Jul: 53.96; Aug: 51.44; Sep: 38.7; Oct: 32.54; Nov: 20.7; Dec: 12.4
NE | LINCOLN MUNICIPAL ARPT | Jan: 24.7; Feb: 29.5; Mar: 40.5; Apr: 51.6; May: 62.6; Jun: 72.6; Jul: 77.5; Aug: 75.4; Sep: 66.2; Oct: 53.6; Nov: 39.4; Dec: 27.9; Jan: 13.8; Feb: 20.48; Mar: 30.9; Apr: 42.62; May: 51.1; Jun: 63.32; Jul: 65.84; Aug: 63.5; Sep: 54.3; Oct: 42.08; Nov: 27.7; Dec: 18.7
MN | LITCHFIELD MUNI | Jan: 13; Feb: 17.1; Mar: 29.7; Apr: 44.8; May: 57.2; Jun: 67.1; Jul: 71.7; Aug: 69.1; Sep: 61.1; Oct: 47.6; Nov: 32.9; Dec: 18.8; Jan: 6.8; Feb: 6.62; Mar: 28.9; Apr: 36.68; May: 50.2; Jun: 55.94; Jul: 59.54; Aug: 55.04; Sep: 51.1; Oct: 43.16; Nov: 23.2; Dec: 12.4
MN | LITTLE FALLS (AWOS) | Jan: 11.8; Feb: 16; Mar: 28.6; Apr: 42.8; May: 54.9; Jun: 64.9; Jul: 69.7; Aug: 66.9; Sep: 58.3; Oct: 45.7; Nov: 30.8; Dec: 17.2; Jan: 5.5; Feb: 5.72; Mar: 24.6; Apr: 25.52; May: 43; Jun: 55.4; Jul: 57.56; Aug: 59.18; Sep: 48.6; Oct: 33.08; Nov: 16.5; Dec: 15.8
AR | LITTLE ROCK ADAMS FIELD | Jan: 42.4; Feb: 46.2; Mar: 54; Apr: 63; May: 71.1; Jun: 79.3; Jul: 82.6; Aug: 82.2; Sep: 74.9; Oct: 63.8; Nov: 52.6; Dec: 44.1; Jan: 26.6; Feb: 30.02; Mar: 41.5; Apr: 50.36; May: 61.9; Jun: 68.72; Jul: 70.88; Aug: 69.44; Sep: 64.8; Oct: 49.28; Nov: 43.5; Dec: 30.2
AR | LITTLE ROCK AFB | Jan: 40.8; Feb: 46; Mar: 53.4; Apr: 62.6; May: 70.1; Jun: 79.1; Jul: 82.4; Aug: 81.4; Sep: 73.6; Oct: 63; Nov: 49.9; Dec: 42.5; Jan: 31.3; Feb: 34.34; Mar: 33.1; Apr: 43.7; May: 66.9; Jun: 70.34; Jul: 70.88; Aug: 70.16; Sep: 57; Oct: 53.78; Nov: 36.9; Dec: 32.5
CA | LIVERMORE MUNICIPAL | Jan: 47.7; Feb: 50.2; Mar: 53.9; Apr: 56.8; May: 62.4; Jun: 67.9; Jul: 72.1; Aug: 72; Sep: 70.2; Oct: 63.3; Nov: 54.1; Dec: 48.4; Jan: 38.8; Feb: 41.72; Mar: 46.6; Apr: 43.34; May: 47.5; Jun: 49.46; Jul: 53.42; Aug: 51.44; Sep: 50.9; Oct: 45.14; Nov: 40.6; Dec: 39.7
MT | LIVINGSTON MISSION FIELD | Jan: 29.1; Feb: 27.8; Mar: 36; Apr: 42.3; May: 50.5; Jun: 58.8; Jul: 69.6; Aug: 66.9; Sep: 58; Oct: 46; Nov: 35.4; Dec: 27.3; Jan: 12.9; Feb: 11.84; Mar: 21.6; Apr: 29.66; May: 34.7; Jun: 43.7; Jul: 42.08; Aug: 44.42; Sep: 32.5; Oct: 30.74; Nov: 22.5; Dec: 17.8
CA | LOMPOC (AWOS) | Jan: 52.2; Feb: 53; Mar: 54.5; Apr: 55.5; May: 58.1; Jun: 60.1; Jul: 62.2; Aug: 62.8; Sep: 62.4; Oct: 60.2; Nov: 56.6; Dec: 51.8; Jan: 35.8; Feb: 15.08; Mar: 25.5; Apr: 37.04; May: 19.9; Jun: 50.54; Jul: 51.8; Aug: 50.9; Sep: 52.5; Oct: 48.38; Nov: 14.4; Dec: 40.5
ON | LONDON AP | Jan: 22.7; Feb: 23.6; Mar: 32.3; Apr: 44.7; May: 56; Jun: 65.8; Jul: 69.4; Aug: 67.8; Sep: 60.7; Oct: 49.6; Nov: 38.5; Dec: 28.3; Jan: 17.6; Feb: 17.06; Mar: 24.1; Apr: 33.8; May: 43.9; Jun: 55.4; Jul: 58.82; Aug: 59; Sep: 53.1; Oct: 41.72; Nov: 33.4; Dec: 21.7
KY | LONDON-CORBIN AP | Jan: 36.1; Feb: 39.1; Mar: 47.3; Apr: 57; May: 64.7; Jun: 72.4; Jul: 75.4; Aug: 74.9; Sep: 68.3; Oct: 56.9; Nov: 46.5; Dec: 38.7; Jan: 20.1; Feb: 29.8; Mar: 39; Apr: 48.2; May: 52.7; Jun: 60.1; Jul: 68; Aug: 66.6; Sep: 52; Oct: 52.5; Nov: 37.4; Dec: 25.5
WI | LONE ROCK FAA AP | Jan: 18.9; Feb: 21.5; Mar: 34.9; Apr: 48.1; May: 58.7; Jun: 68.6; Jul: 72.3; Aug: 70.3; Sep: 62; Oct: 49.5; Nov: 37.7; Dec: 23.3; Jan: 11.3; Feb: 18.32; Mar: 28.2; Apr: 38.3; May: 49.1; Jun: 59.36; Jul: 62.24; Aug: 57.38; Sep: 51.4; Oct: 40.64; Nov: 36.9; Dec: 19.6
CA | LONG BEACH DAUGHERTY FLD | Jan: 57.2; Feb: 57.4; Mar: 59.8; Apr: 62.4; May: 65.7; Jun: 68.7; Jul: 72.6; Aug: 73.9; Sep: 72.7; Oct: 67.8; Nov: 61.9; Dec: 56.5; Jan: 45.1; Feb: 45.32; Mar: 47.7; Apr: 51.08; May: 52.7; Jun: 57.56; Jul: 60.98; Aug: 59.36; Sep: 60.3; Oct: 55.22; Nov: 48; Dec: 41.4
TX | LONGVIEW GREGG COUNTY AP [OVERTON - UT] | Jan: 48; Feb: 51.1; Mar: 58.5; Apr: 66.1; May: 73.7; Jun: 80.8; Jul: 83.4; Aug: 84.2; Sep: 77.6; Oct: 66.9; Nov: 56.9; Dec: 48.5; Jan: 40.8; Feb: 37.4; Mar: 42.1; Apr: 53.6; May: 62.4; Jun: 63.14; Jul: 69.8; Aug: 69.8; Sep: 60.8; Oct: 57.2; Nov: 44.4; Dec: 37
CA | LOS ANGELES INTL ARPT | Jan: 57.7; Feb: 57.5; Mar: 58.6; Apr: 60.6; May: 63.4; Jun: 66; Jul: 69; Aug: 69.9; Sep: 69.2; Oct: 66.3; Nov: 62; Dec: 57.3; Jan: 46.9; Feb: 48.56; Mar: 45.5; Apr: 50; May: 53.6; Jun: 57.74; Jul: 59.9; Aug: 60.08; Sep: 61.3; Oct: 53.96; Nov: 48; Dec: 45.3
KY | LOUISVILLE BOWMAN FIELD | Jan: 35.2; Feb: 38.7; Mar: 47.3; Apr: 57.9; May: 66.7; Jun: 75; Jul: 78.2; Aug: 77.4; Sep: 70; Oct: 58.5; Nov: 47.6; Dec: 38.5; Jan: 21.7; Feb: 29.3; Mar: 37.9; Apr: 46.9; May: 61.2; Jun: 65.8; Jul: 68; Aug: 66; Sep: 59.9; Oct: 48.7; Nov: 43.2; Dec: 30.7
KY | LOUISVILLE STANDIFORD FIELD | Jan: 35.4; Feb: 39; Mar: 47.9; Apr: 58.4; May: 67.3; Jun: 75.7; Jul: 79; Aug: 78.4; Sep: 70.9; Oct: 59.4; Nov: 48.1; Dec: 38.8; Jan: 22.3; Feb: 23.36; Mar: 35.2; Apr: 40.64; May: 52.9; Jun: 62.96; Jul: 68.54; Aug: 65.66; Sep: 60.3; Oct: 49.82; Nov: 36.7; Dec: 25.9
NV | LOVELOCK DERBY FIELD | Jan: 31.8; Feb: 37.4; Mar: 44.4; Apr: 50.4; May: 59.8; Jun: 68.4; Jul: 77; Aug: 73.8; Sep: 65.2; Oct: 52.2; Nov: 39.2; Dec: 30.6; Jan: 21.9; Feb: 22.64; Mar: 28.9; Apr: 26.24; May: 29.3; Jun: 35.42; Jul: 43.52; Aug: 37.4; Sep: 37.6; Oct: 21.92; Nov: 23.9; Dec: 22.3
TX | LUBBOCK INTERNATIONAL AP | Jan: 41.2; Feb: 45.1; Mar: 52.6; Apr: 61.2; May: 70.4; Jun: 78.7; Jul: 80.7; Aug: 79.5; Sep: 72; Oct: 61.8; Nov: 50.1; Dec: 41.5; Jan: 24.1; Feb: 25.88; Mar: 29.1; Apr: 34.16; May: 46.9; Jun: 55.76; Jul: 60.26; Aug: 60.8; Sep: 57.4; Oct: 43.88; Nov: 32.5; Dec: 25.3
TX | LUFKIN ANGELINA CO | Jan: 49.8; Feb: 53.7; Mar: 60.1; Apr: 67.1; May: 74.8; Jun: 80.8; Jul: 83; Aug: 83.3; Sep: 78; Oct: 68.2; Nov: 57.9; Dec: 51.1; Jan: 41.7; Feb: 38.84; Mar: 48.7; Apr: 57.56; May: 65.5; Jun: 70.16; Jul: 72.86; Aug: 70.16; Sep: 66.6; Oct: 55.58; Nov: 54; Dec: 38.1
AZ | LUKE AFB | Jan: 53.8; Feb: 57.1; Mar: 63.5; Apr: 70.2; May: 79.1; Jun: 88; Jul: 93.4; Aug: 92.5; Sep: 86.4; Oct: 73.4; Nov: 61.6; Dec: 52.7; Jan: 46.4; Feb: 38.84; Mar: 40.6; Apr: 31.28; May: 33.1; Jun: 28.76; Jul: 47.48; Aug: 47.12; Sep: 50; Oct: 36.32; Nov: 31.3; Dec: 33.3
VA | LYNCHBURG REGIONAL ARPT | Jan: 36.8; Feb: 39.3; Mar: 47; Apr: 56.7; May: 64.2; Jun: 72.2; Jul: 76; Aug: 74.6; Sep: 67.7; Oct: 57; Nov: 47; Dec: 39.2; Jan: 18.1; Feb: 25.7; Mar: 34.7; Apr: 40.64; May: 51.8; Jun: 62.96; Jul: 67.1; Aug: 64.4; Sep: 60.3; Oct: 44.6; Nov: 34.9; Dec: 26.8
FL | MACDILL AFB | Jan: 61.2; Feb: 64; Mar: 67.9; Apr: 72.8; May: 78.5; Jun: 82.2; Jul: 82.9; Aug: 83.2; Sep: 81.9; Oct: 76.3; Nov: 68.4; Dec: 64; Jan: 47.5; Feb: 50.72; Mar: 51.3; Apr: 59.36; May: 70; Jun: 70.88; Jul: 73.94; Aug: 72.5; Sep: 72; Oct: 65.12; Nov: 54.7; Dec: 50.9
GA | MACON MIDDLE GA REGIONAL AP | Jan: 47.2; Feb: 50.5; Mar: 57; Apr: 63.8; May: 72; Jun: 78.8; Jul: 81.6; Aug: 80.7; Sep: 75.2; Oct: 64.9; Nov: 55.1; Dec: 48.6; Jan: 33.8; Feb: 35.96; Mar: 45; Apr: 49.46; May: 59.2; Jun: 69.26; Jul: 68.9; Aug: 69.62; Sep: 68.5; Oct: 53.06; Nov: 48.2; Dec: 34.7
WI | MADISON DANE CO REGIONAL ARPT [ISIS] | Jan: 19.8; Feb: 23.8; Mar: 34.7; Apr: 46.9; May: 58.1; Jun: 68.1; Jul: 71.8; Aug: 69.9; Sep: 61.7; Oct: 49.9; Nov: 37; Dec: 24.9; Jan: 8.4; Feb: 11.84; Mar: 26.6; Apr: 33.26; May: 50; Jun: 55.94; Jul: 65.48; Aug: 61.88; Sep: 52.2; Oct: 39.74; Nov: 25.5; Dec: 14.9
BC | MALAHAT | Jan: 38.1; Feb: 38.8; Mar: 41.8; Apr: 46.2; May: 53.1; Jun: 58.2; Jul: 64.4; Aug: 64.6; Sep: 59.1; Oct: 49.2; Nov: 41.4; Dec: 37.6; Jan: 36; Feb: 35.96; Mar: 38.3; Apr: 40.46; May: 45.1; Jun: 49.28; Jul: 52.7; Aug: 53.42; Sep: 50.5; Oct: 45.86; Nov: 41; Dec: 35.4
VA | MANASSAS MUNI(AWOS) | Jan: 33.3; Feb: 36.2; Mar: 43.4; Apr: 54.4; May: 62.2; Jun: 71.8; Jul: 76; Aug: 74.5; Sep: 67.5; Oct: 55.2; Nov: 45.2; Dec: 35.6; Jan: 26.2; Feb: 21.38; Mar: 24.3; Apr: 34.16; May: 41.5; Jun: 61.16; Jul: 67.46; Aug: 63.68; Sep: 54.9; Oct: 41.36; Nov: 27.9; Dec: 28.6
NH | MANCHESTER AIRPORT | Jan: 25.6; Feb: 28; Mar: 36.3; Apr: 48.1; May: 58.6; Jun: 68; Jul: 73.4; Aug: 71.7; Sep: 63.7; Oct: 52; Nov: 41.7; Dec: 31.5; Jan: 10.9; Feb: 16.34; Mar: 28.9; Apr: 34.88; May: 39.9; Jun: 56.66; Jul: 58.28; Aug: 57.74; Sep: 56.7; Oct: 38.84; Nov: 30.4; Dec: 26.2
KS | MANHATTAN RGNL | Jan: 29.6; Feb: 33.5; Mar: 43.8; Apr: 54.7; May: 65; Jun: 74.5; Jul: 79.9; Aug: 77.8; Sep: 68.3; Oct: 56.3; Nov: 43.2; Dec: 31.7; Jan: 20.7; Feb: 22.28; Mar: 33.6; Apr: 45.32; May: 54.9; Jun: 65.48; Jul: 70.16; Aug: 68.54; Sep: 55.9; Oct: 42.8; Nov: 31.8; Dec: 20.8
MI | MANISTEE (AWOS) | Jan: 23.8; Feb: 24.6; Mar: 31.7; Apr: 43; May: 53.7; Jun: 62.8; Jul: 66.8; Aug: 65.8; Sep: 58.5; Oct: 47.9; Nov: 37.4; Dec: 28.7; Jan: 16.2; Feb: 21.38; Mar: 20.7; Apr: 36.14; May: 40.8; Jun: 58.64; Jul: 62.42; Aug: 61.7; Sep: 50.4; Oct: 39.38; Nov: 31.5; Dec: 14.9
WI | MANITOWOC MUNI AWOS | Jan: 20.2; Feb: 22.7; Mar: 31.9; Apr: 42.8; May: 53.2; Jun: 63.3; Jul: 68.6; Aug: 67.4; Sep: 60; Oct: 48.7; Nov: 37; Dec: 25.3; Jan: 10; Feb: 18.68; Mar: 21.9; Apr: 37.04; May: 43.7; Jun: 53.96; Jul: 59.36; Aug: 60.26; Sep: 51.4; Oct: 40.82; Nov: 34.7; Dec: 18.7
MN | MANKATO(AWOS) | Jan: 14.8; Feb: 19.2; Mar: 31.8; Apr: 46.7; May: 58.3; Jun: 68.2; Jul: 71.8; Aug: 69.5; Sep: 61.4; Oct: 49.1; Nov: 34.4; Dec: 20.5; Jan: 8.4; Feb: 18.14; Mar: 16.3; Apr: 39.2; May: 46.8; Jun: 52.52; Jul: 60.98; Aug: 63.68; Sep: 50.7; Oct: 31.64; Nov: 28.2; Dec: 11.8
OH | MANSFIELD LAHM MUNICIPAL ARPT | Jan: 26.4; Feb: 28.6; Mar: 37.6; Apr: 49.4; May: 59.6; Jun: 68.4; Jul: 71.7; Aug: 70.2; Sep: 63.2; Oct: 52.2; Nov: 41.2; Dec: 31.2; Jan: 13.1; Feb: 17.78; Mar: 28.4; Apr: 38.12; May: 48; Jun: 57.02; Jul: 64.58; Aug: 61.7; Sep: 54.5; Oct: 41.18; Nov: 34.3; Dec: 20.7
FL | MARATHON AIRPORT | Jan: 69.7; Feb: 72.1; Mar: 74.6; Apr: 78; May: 81.5; Jun: 84.4; Jul: 85.2; Aug: 85.6; Sep: 84.2; Oct: 81; Nov: 75.1; Dec: 72.1; Jan: 62.1; Feb: 57.38; Mar: 70; Apr: 67.1; May: 71.6; Jun: 74.12; Jul: 78.8; Aug: 77.36; Sep: 74.3; Oct: 74.3; Nov: 69.6; Dec: 63.5
CA | MARCH AFB | Jan: 53.1; Feb: 53.3; Mar: 56.5; Apr: 60.2; May: 65.9; Jun: 71.4; Jul: 77.4; Aug: 78.9; Sep: 75.6; Oct: 66.7; Nov: 58.2; Dec: 51.9; Jan: 31.6; Feb: 26.96; Mar: 35.1; Apr: 38.84; May: 50.9; Jun: 48.38; Jul: 53.06; Aug: 49.28; Sep: 50.5; Oct: 35.78; Nov: 31.5; Dec: 25.9
TX | MARFA AP | Jan: 41.9; Feb: 45.7; Mar: 51.5; Apr: 58.8; May: 67.1; Jun: 74.1; Jul: 73.4; Aug: 72.6; Sep: 67.8; Oct: 59.7; Nov: 49.3; Dec: 42.5; Jan: 28.8; Feb: 32.72; Mar: 29.5; Apr: 30.74; May: 31.8; Jun: 43.34; Jul: 46.4; Aug: 49.46; Sep: 40.8; Oct: 34.16; Nov: 30.4; Dec: 20.7
GA | MARIETTA DOBBINS AFB | Jan: 42.6; Feb: 46.4; Mar: 53.1; Apr: 62.1; May: 69.5; Jun: 77; Jul: 79.7; Aug: 78.4; Sep: 73; Oct: 61.6; Nov: 51.9; Dec: 45.5; Jan: 26.8; Feb: 32; Mar: 33.3; Apr: 41.18; May: 50.5; Jun: 66.56; Jul: 71.06; Aug: 68.18; Sep: 61.5; Oct: 45.14; Nov: 36.3; Dec: 30.2
VA | MARION / WYTHEVILLE | Jan: 33.3; Feb: 36.1; Mar: 44.9; Apr: 53.8; May: 62.1; Jun: 69.8; Jul: 73.1; Aug: 72.2; Sep: 65.4; Oct: 54.7; Nov: 43.7; Dec: 37; Jan: 18; Feb: 29.48; Mar: 34; Apr: 32.36; May: 45.1; Jun: 57.74; Jul: 60.98; Aug: 62.96; Sep: 52.2; Oct: 48.02; Nov: 36.1; Dec: 21
IL | MARION REGIONAL | Jan: 34.2; Feb: 36.3; Mar: 48.5; Apr: 58.6; May: 67.2; Jun: 75.2; Jul: 77.8; Aug: 77.8; Sep: 70.3; Oct: 58.7; Nov: 49.1; Dec: 37.9; Jan: 30; Feb: 28.22; Mar: 30.6; Apr: 39.38; May: 49.8; Jun: 67.46; Jul: 67.64; Aug: 64.76; Sep: 55.9; Oct: 45.32; Nov: 40.8; Dec: 26.8
MN | MARSHALL MUNI-RYAN FIELD AWOS | Jan: 15; Feb: 19; Mar: 32; Apr: 45; May: 58; Jun: 68; Jul: 72; Aug: 69; Sep: 62; Oct: 49; Nov: 34; Dec: 20; Jan: 10.6; Feb: 20.3; Mar: 14.7; Apr: 35.42; May: 41.5; Jun: 51.62; Jul: 59.72; Aug: 63.86; Sep: 50; Oct: 35.78; Nov: 26.1; Dec: 11.3
WI | MARSHFIELD MUNI | Jan: 14.4; Feb: 18.9; Mar: 30.6; Apr: 44.3; May: 55.8; Jun: 65.3; Jul: 69.7; Aug: 67.8; Sep: 59.5; Oct: 47.1; Nov: 33.4; Dec: 21.1; Jan: 17.1; Feb: 17.78; Mar: 25.5; Apr: 34.88; May: 40.1; Jun: 55.58; Jul: 59.36; Aug: 58.82; Sep: 54; Oct: 38.48; Nov: 26.8; Dec: 10.6
MA | MARTHAS VINEYARD | Jan: 31.4; Feb: 32.1; Mar: 37.6; Apr: 46.1; May: 55.5; Jun: 63.9; Jul: 70.1; Aug: 69; Sep: 62.7; Oct: 53.2; Nov: 45.1; Dec: 36.9; Jan: 28.6; Feb: 21.02; Mar: 31.1; Apr: 37.76; May: 43.5; Jun: 57.02; Jul: 64.04; Aug: 61.88; Sep: 57; Oct: 48.74; Nov: 40.1; Dec: 25.5
WV | MARTINSBURG EASTERN WV REG AP | Jan: 33.1; Feb: 35.3; Mar: 43.3; Apr: 54; May: 62.5; Jun: 71.3; Jul: 75.7; Aug: 73.8; Sep: 66.5; Oct: 55.3; Nov: 45.3; Dec: 36.2; Jan: 22.3; Feb: 30.56; Mar: 30.6; Apr: 40.82; May: 50.2; Jun: 59.36; Jul: 64.04; Aug: 63.86; Sep: 59.2; Oct: 46.4; Nov: 34.2; Dec: 28.4
VA | MARTINSVILLE | Jan: 38.5; Feb: 41.3; Mar: 48.4; Apr: 58.1; May: 65.6; Jun: 73.7; Jul: 77.1; Aug: 76; Sep: 68.8; Oct: 57.9; Nov: 47.5; Dec: 40.4; Jan: 31.6; Feb: 25.52; Mar: 26.8; Apr: 39.02; May: 45.9; Jun: 62.78; Jul: 65.84; Aug: 66.74; Sep: 57.6; Oct: 44.24; Nov: 31.3; Dec: 28.8
IA | MASON CITY MUNICIPAL ARPT | Jan: 16.2; Feb: 21; Mar: 33.1; Apr: 46.5; May: 58.4; Jun: 68.4; Jul: 71.6; Aug: 69.4; Sep: 61.2; Oct: 48.9; Nov: 34.3; Dec: 21.2; Jan: 6.6; Feb: 12.38; Mar: 25.9; Apr: 35.42; May: 49.1; Jun: 56.84; Jul: 62.96; Aug: 61.7; Sep: 53.1; Oct: 36.86; Nov: 27.5; Dec: 10.2
NY | MASSENA AP | Jan: 16.2; Feb: 18.5; Mar: 29.1; Apr: 43.9; May: 56.2; Jun: 65.4; Jul: 69.7; Aug: 67.8; Sep: 59.6; Oct: 48; Nov: 36.5; Dec: 23.9; Jan: 10.2; Feb: 10.58; Mar: 18.9; Apr: 30.2; May: 41.9; Jun: 56.3; Jul: 60.26; Aug: 59.18; Sep: 49.5; Oct: 37.94; Nov: 27.9; Dec: 17.8
AL | MAXWELL AFB | Jan: 48.3; Feb: 52.6; Mar: 58.8; Apr: 65.8; May: 74.1; Jun: 81; Jul: 82.8; Aug: 82.7; Sep: 77.8; Oct: 67.1; Nov: 56; Dec: 51.5; Jan: 32.4; Feb: 36.5; Mar: 39.7; Apr: 47.84; May: 61.3; Jun: 69.98; Jul: 73.58; Aug: 69.8; Sep: 64.9; Oct: 51.44; Nov: 42.3; Dec: 36.1
FL | MAYPORT NS | Jan: 56; Feb: 58.4; Mar: 62.9; Apr: 68.9; May: 75.8; Jun: 80.8; Jul: 82.7; Aug: 82.5; Sep: 79.8; Oct: 73.3; Nov: 63.7; Dec: 58.4; Jan: 42.3; Feb: 46.94; Mar: 58.5; Apr: 56.3; May: 67.1; Jun: 70.52; Jul: 72.68; Aug: 71.96; Sep: 70.5; Oct: 60.98; Nov: 56.3; Dec: 44.8
TX | MC GREGOR (AWOS) | Jan: 48.1; Feb: 51.4; Mar: 57.8; Apr: 66.5; May: 74.5; Jun: 81.6; Jul: 84.7; Aug: 85.2; Sep: 78.2; Oct: 67.8; Nov: 57.4; Dec: 49.1; Jan: 34; Feb: 35.42; Mar: 34.2; Apr: 44.42; May: 62.6; Jun: 69.08; Jul: 64.58; Aug: 65.66; Sep: 59.2; Oct: 46.22; Nov: 43.2; Dec: 37.8
QC | MC TAVISH | Jan: 17.6; Feb: 20.1; Mar: 30.5; Apr: 44.4; May: 57.4; Jun: 66.9; Jul: 71.3; Aug: 69.7; Sep: 61.7; Oct: 49.3; Nov: 37.5; Dec: 24.7; Jan: 7.3; Feb: 9.32; Mar: 18.3; Apr: 28.76; May: 41.2; Jun: 53.78; Jul: 58.46; Aug: 57.92; Sep: 51.4; Oct: 39.38; Nov: 30; Dec: 14.5
OK | MCALESTER MUNICIPAL AP | Jan: 41.4; Feb: 45.6; Mar: 53.7; Apr: 61.8; May: 69.8; Jun: 78.1; Jul: 82.4; Aug: 82; Sep: 73.9; Oct: 63.2; Nov: 52.1; Dec: 43.3; Jan: 26.8; Feb: 36.68; Mar: 43; Apr: 49.82; May: 61.5; Jun: 70.34; Jul: 70.7; Aug: 68; Sep: 63.1; Oct: 50.54; Nov: 42.1; Dec: 24.8
TX | MCALLEN MILLER INTL AP [EDINBURG - UT] | Jan: 61.9; Feb: 65.6; Mar: 71.1; Apr: 76.9; May: 82; Jun: 86.1; Jul: 86.9; Aug: 87.4; Sep: 83.2; Oct: 77.3; Nov: 69; Dec: 62.6; Jan: 50.5; Feb: 56.12; Mar: 55.8; Apr: 62.06; May: 68.7; Jun: 71.78; Jul: 71.42; Aug: 74.66; Sep: 72.3; Oct: 63.68; Nov: 57.6; Dec: 47.3
MS | MCCOMB PIKE COUNTY AP | Jan: 49.6; Feb: 52.9; Mar: 59.1; Apr: 65.7; May: 73.3; Jun: 79.4; Jul: 81; Aug: 81.3; Sep: 76.8; Oct: 67.1; Nov: 57; Dec: 51.2; Jan: 40.1; Feb: 43.52; Mar: 45.9; Apr: 58.64; May: 62.2; Jun: 69.44; Jul: 71.42; Aug: 73.22; Sep: 72; Oct: 56.84; Nov: 46; Dec: 38.7
KS | MCCONNELL AFB | Jan: 33.9; Feb: 38.7; Mar: 47.8; Apr: 56.7; May: 66.9; Jun: 76.4; Jul: 80.8; Aug: 80.1; Sep: 71.6; Oct: 59.6; Nov: 46.4; Dec: 36.4; Jan: 27.9; Feb: 29.66; Mar: 32.7; Apr: 39.74; May: 56.1; Jun: 63.14; Jul: 60.08; Aug: 61.16; Sep: 48.6; Oct: 40.28; Nov: 32.9; Dec: 28.4
NE | MCCOOK MUNICIPAL | Jan: 29.5; Feb: 31.7; Mar: 41.9; Apr: 51.1; May: 61.9; Jun: 72.4; Jul: 78.7; Aug: 76; Sep: 66.8; Oct: 52.9; Nov: 40.3; Dec: 29.4; Jan: 22.5; Feb: 19.04; Mar: 27.3; Apr: 33.8; May: 47.5; Jun: 55.94; Jul: 60.26; Aug: 60.26; Sep: 55.8; Oct: 35.6; Nov: 26.1; Dec: 15.8
AK | MCGRATH ARPT | Jan: -6.5; Feb: 2.7; Mar: 11; Apr: 31.3; May: 47.3; Jun: 57.8; Jul: 59.8; Aug: 55; Sep: 45; Oct: 26.9; Nov: 6.5; Dec: -3.9; Jan: -5.6; Feb: -5.8; Mar: 0.3; Apr: 16.34; May: 32.4; Jun: 42.08; Jul: 48.74; Aug: 48.74; Sep: 34; Oct: 20.84; Nov: -1.7; Dec: -9.8
NJ | MCGUIRE AFB | Jan: 32.9; Feb: 35; Mar: 42.4; Apr: 52.7; May: 62.1; Jun: 71.2; Jul: 76.3; Aug: 74.4; Sep: 67.3; Oct: 56.4; Nov: 46.3; Dec: 37.5; Jan: 22.3; Feb: 22.1; Mar: 35.2; Apr: 35.6; May: 47.3; Jun: 59; Jul: 64.4; Aug: 63.5; Sep: 57.6; Oct: 46.94; Nov: 31.6; Dec: 29.8
OR | MEDFORD ROGUE VALLEY INTL AP [ASHLAND - UO] | Jan: 40.1; Feb: 44.2; Mar: 48.2; Apr: 52.5; May: 59.8; Jun: 66.1; Jul: 75; Aug: 73.9; Sep: 68; Oct: 55.9; Nov: 44.9; Dec: 38.9; Jan: 32.4; Feb: 34.88; Mar: 37.6; Apr: 39.56; May: 42.3; Jun: 46.4; Jul: 48.74; Aug: 50.36; Sep: 46.2; Oct: 40.64; Nov: 36.9; Dec: 33.6
AB | MEDICINE AP | Jan: 16.5; Feb: 21.6; Mar: 31.5; Apr: 43.3; May: 53.3; Jun: 60.9; Jul: 67.6; Aug: 66.7; Sep: 57.3; Oct: 44.1; Nov: 29.7; Dec: 18.9; Jan: 10.4; Feb: 11.66; Mar: 18.1; Apr: 26.24; May: 35.2; Jun: 46.04; Jul: 50; Aug: 46.94; Sep: 40.3; Oct: 30.02; Nov: 20.5; Dec: 10.2
AK | MEKORYUK | Jan: 10.9; Feb: 15.2; Mar: 14.8; Apr: 24.5; May: 34.7; Jun: 43.2; Jul: 48.5; Aug: 50.2; Sep: 45.4; Oct: 34.3; Nov: 25.6; Dec: 16.3; Jan: 10.2; Feb: 22.64; Mar: 22.6; Apr: 24.26; May: 30.7; Jun: 35.96; Jul: 42.8; Aug: 42.44; Sep: 36.7; Oct: 23.72; Nov: 25.5; Dec: 21.9
FL | MELBOURNE REGIONAL AP | Jan: 62.3; Feb: 64.4; Mar: 67.6; Apr: 71.8; May: 77.1; Jun: 80.6; Jul: 81.9; Aug: 82; Sep: 80.9; Oct: 76.2; Nov: 69.2; Dec: 64.6; Jan: 57.4; Feb: 53.24; Mar: 60.8; Apr: 65.3; May: 65.7; Jun: 72.32; Jul: 73.22; Aug: 74.12; Sep: 71.8; Oct: 66.56; Nov: 57.7; Dec: 56.5
VA | MELFA/ACCOMACK ARPT | Jan: 40; Feb: 41.2; Mar: 47.6; Apr: 56.9; May: 65.9; Jun: 74.7; Jul: 79.2; Aug: 77.1; Sep: 70.7; Oct: 61.4; Nov: 50.8; Dec: 43.2; Jan: 27.9; Feb: 28.04; Mar: 29.7; Apr: 46.76; May: 57; Jun: 64.22; Jul: 68; Aug: 70.7; Sep: 59.2; Oct: 51.8; Nov: 42.8; Dec: 37.2
TN | MEMPHIS INTERNATIONAL AP | Jan: 42.3; Feb: 46.1; Mar: 54.1; Apr: 63.3; May: 71.8; Jun: 79.7; Jul: 82.4; Aug: 82.1; Sep: 75.4; Oct: 64.2; Nov: 52.8; Dec: 44.5; Jan: 30.7; Feb: 29.48; Mar: 42.1; Apr: 47.12; May: 60.8; Jun: 66.2; Jul: 69.08; Aug: 66.92; Sep: 65.5; Oct: 48.38; Nov: 42.3; Dec: 30
MI | MENOMINEE (AWOS) | Jan: 17.9; Feb: 21; Mar: 29.8; Apr: 41.3; May: 53.3; Jun: 63.6; Jul: 68.2; Aug: 66.7; Sep: 58.8; Oct: 47.6; Nov: 35.5; Dec: 23.9; Jan: 8.1; Feb: 12.92; Mar: 17.8; Apr: 35.96; May: 36.9; Jun: 51.8; Jul: 56.12; Aug: 52.34; Sep: 51.4; Oct: 37.22; Nov: 27.7; Dec: 16.9
CA | MERCED/MACREADY FLD | Jan: 45.7; Feb: 49.8; Mar: 54.9; Apr: 59.2; May: 67.8; Jun: 74.2; Jul: 79.2; Aug: 77.4; Sep: 73.4; Oct: 63.9; Nov: 53.3; Dec: 46.3; Jan: 37.9; Feb: 46.4; Mar: 48.4; Apr: 41.18; May: 44.1; Jun: 52.52; Jul: 53.78; Aug: 54.68; Sep: 48.9; Oct: 45.14; Nov: 43.2; Dec: 41.9
NV | MERCURY DESERT ROCK AP [SURFRAD] | Jan: 45.2; Feb: 47.9; Mar: 54.5; Apr: 60.4; May: 70; Jun: 79.3; Jul: 86.1; Aug: 84.3; Sep: 76.8; Oct: 64.4; Nov: 52; Dec: 43.7; Jan: 27.3; Feb: 24.08; Mar: 22.8; Apr: 24.62; May: 33.4; Jun: 35.78; Jul: 41.72; Aug: 39.2; Sep: 32.4; Oct: 33.98; Nov: 25.5; Dec: 20.5
MS | MERIDIAN KEY FIELD | Jan: 46.6; Feb: 50.1; Mar: 57; Apr: 64.1; May: 71.9; Jun: 78.5; Jul: 80.9; Aug: 80.7; Sep: 75.5; Oct: 64.7; Nov: 54.5; Dec: 48.4; Jan: 34.3; Feb: 36.5; Mar: 45.7; Apr: 51.8; May: 61.3; Jun: 67.1; Jul: 72.5; Aug: 69.8; Sep: 63.3; Oct: 52.88; Nov: 44.8; Dec: 35.6
MS | MERIDIAN NAAS | Jan: 46.4; Feb: 50.2; Mar: 57.5; Apr: 63.9; May: 72.3; Jun: 79.4; Jul: 81.4; Aug: 80.8; Sep: 75.8; Oct: 64.7; Nov: 53.8; Dec: 49.3; Jan: 34.2; Feb: 40.46; Mar: 47.5; Apr: 55.4; May: 64.6; Jun: 67.46; Jul: 71.96; Aug: 71.42; Sep: 64.6; Oct: 52.7; Nov: 49.1; Dec: 38.3
FL | MIAMI INTL AP | Jan: 68.8; Feb: 70.5; Mar: 72.7; Apr: 76.2; May: 80.1; Jun: 82.5; Jul: 83.9; Aug: 84.1; Sep: 82.8; Oct: 79.7; Nov: 74.4; Dec: 70.8; Jan: 56.5; Feb: 57.02; Mar: 59.2; Apr: 63.32; May: 69.3; Jun: 72.86; Jul: 73.04; Aug: 73.4; Sep: 72.7; Oct: 69.98; Nov: 65.3; Dec: 60.3
FL | MIAMI/KENDALL-TAMIA | Jan: 67.1; Feb: 69; Mar: 71.1; Apr: 74.8; May: 78.7; Jun: 81.7; Jul: 82.8; Aug: 83.1; Sep: 81.8; Oct: 78.7; Nov: 72.8; Dec: 69.1; Jan: 56.7; Feb: 60.8; Mar: 58.1; Apr: 62.96; May: 67.5; Jun: 72.68; Jul: 73.76; Aug: 73.58; Sep: 73; Oct: 66.56; Nov: 63.5; Dec: 58.1
FL | MIAMI/OPA LOCKA | Jan: 66.9; Feb: 69.7; Mar: 72; Apr: 75.5; May: 79.2; Jun: 82.2; Jul: 83.2; Aug: 83.9; Sep: 82.4; Oct: 79.4; Nov: 73.1; Dec: 70; Jan: 56.8; Feb: 58.1; Mar: 60.4; Apr: 60.44; May: 67.8; Jun: 73.04; Jul: 77.36; Aug: 73.58; Sep: 75; Oct: 68.72; Nov: 63.7; Dec: 57.9
AK | MIDDLETON ISLAND AUT | Jan: 35.5; Feb: 35.3; Mar: 35.8; Apr: 40.6; May: 44.8; Jun: 50.4; Jul: 54.6; Aug: 55.3; Sep: 51.6; Oct: 44.8; Nov: 38.8; Dec: 36.8; Jan: 28.9; Feb: 30.92; Mar: 24.8; Apr: 24.44; May: 30.9; Jun: 44.06; Jul: 28.76; Aug: 37.76; Sep: 34.9; Oct: 33.44; Nov: 27.9; Dec: 24.6
PA | MIDDLETOWN HARRISBURG INTL AP | Jan: 31.2; Feb: 33.4; Mar: 42.1; Apr: 53.2; May: 63.1; Jun: 72.4; Jul: 76.8; Aug: 74.8; Sep: 67.3; Oct: 55.5; Nov: 44.9; Dec: 35.6; Jan: 14; Feb: 21.02; Mar: 25.3; Apr: 40.64; May: 48.7; Jun: 63.68; Jul: 62.78; Aug: 63.86; Sep: 57; Oct: 44.06; Nov: 35.6; Dec: 21.4
TX | MIDLAND INTERNATIONAL AP | Jan: 44.9; Feb: 49.1; Mar: 56.5; Apr: 65.1; May: 74.1; Jun: 81.6; Jul: 82.5; Aug: 81.6; Sep: 74.7; Oct: 65.3; Nov: 53.2; Dec: 45.3; Jan: 25.7; Feb: 29.12; Mar: 28; Apr: 40.64; May: 48.2; Jun: 57.02; Jul: 59; Aug: 58.46; Sep: 57.2; Oct: 47.12; Nov: 40.6; Dec: 29.5
MT | MILES CITY MUNICIPAL ARPT | Jan: 20.2; Feb: 25.2; Mar: 35.4; Apr: 46.2; May: 56.1; Jun: 65.8; Jul: 74.6; Aug: 73.4; Sep: 62.1; Oct: 47.5; Nov: 33; Dec: 22.6; Jan: 7.7; Feb: 8.78; Mar: 21; Apr: 29.48; May: 37.4; Jun: 47.12; Jul: 50.36; Aug: 48.38; Sep: 36.1; Oct: 31.64; Nov: 19; Dec: 12.4
ME | MILLINOCKET MUNICIPAL AP | Jan: 15.9; Feb: 19.1; Mar: 28.6; Apr: 41.1; May: 53.5; Jun: 62.9; Jul: 68.6; Aug: 66.5; Sep: 58.8; Oct: 46.6; Nov: 35.1; Dec: 23.3; Jan: 13.1; Feb: 7.88; Mar: 21.9; Apr: 28.58; May: 42.4; Jun: 51.44; Jul: 55.4; Aug: 55.58; Sep: 53.4; Oct: 37.22; Nov: 25.5; Dec: 18.3
NJ | MILLVILLE MUNICIPAL AP | Jan: 33.8; Feb: 35; Mar: 42.4; Apr: 52.5; May: 61.7; Jun: 71.2; Jul: 76.2; Aug: 74.3; Sep: 67.3; Oct: 56; Nov: 46; Dec: 37.6; Jan: 21.6; Feb: 27.32; Mar: 26.6; Apr: 42.8; May: 57.7; Jun: 60.8; Jul: 68.18; Aug: 66.02; Sep: 57.9; Oct: 48.74; Nov: 38.7; Dec: 30.2
WI | MILWAUKEE MITCHELL INTL AP | Jan: 23.4; Feb: 26.6; Mar: 35.7; Apr: 45.8; May: 56.2; Jun: 66.8; Jul: 72.2; Aug: 71.4; Sep: 63.7; Oct: 52.2; Nov: 39.6; Dec: 28.3; Jan: 13.3; Feb: 13.82; Mar: 27.5; Apr: 33.08; May: 46.4; Jun: 53.96; Jul: 59.9; Aug: 61.7; Sep: 55; Oct: 42.08; Nov: 27.9; Dec: 17.1
AK | MINCHUMINA | Jan: -4; Feb: 3.5; Mar: 11; Apr: 31; May: 48; Jun: 58; Jul: 60; Aug: 55; Sep: 45; Oct: 26; Nov: 6.8; Dec: -1; Jan: -16.6; Feb: 5.18; Mar: 9.3; Apr: 24.26; May: 28.9; Jun: 39.02; Jul: 43.7; Aug: 41.72; Sep: 28; Oct: 26.24; Nov: 5.2; Dec: -24.2
TX | MINERAL WELLS MUNICIPAL AP | Jan: 45.4; Feb: 47.9; Mar: 57.5; Apr: 65.9; May: 72.9; Jun: 80.7; Jul: 83.8; Aug: 84.4; Sep: 76.5; Oct: 65.9; Nov: 55.8; Dec: 46; Jan: 33.8; Feb: 37.58; Mar: 29.7; Apr: 41.9; May: 59.5; Jun: 67.82; Jul: 67.46; Aug: 66.74; Sep: 60.6; Oct: 57.92; Nov: 38.7; Dec: 34.5
MN | MINNEAPOLIS-ST PAUL INT ARP | Jan: 16; Feb: 20.9; Mar: 32.9; Apr: 47.1; May: 59; Jun: 69.1; Jul: 73.7; Aug: 71.5; Sep: 62.9; Oct: 49.6; Nov: 34.5; Dec: 21.2; Jan: 2.5; Feb: 12.2; Mar: 22.8; Apr: 33.44; May: 45.9; Jun: 52.52; Jul: 62.06; Aug: 58.82; Sep: 49.3; Oct: 37.04; Nov: 23.7; Dec: 10.4
MN | MINNEAPOLIS/CRYSTAL | Jan: 15.8; Feb: 20.2; Mar: 32; Apr: 46.8; May: 58.2; Jun: 67.7; Jul: 73.7; Aug: 70.9; Sep: 62.5; Oct: 48.8; Nov: 34.8; Dec: 20.9; Jan: 7; Feb: 6.26; Mar: 19.9; Apr: 30.56; May: 42.1; Jun: 54.68; Jul: 60.8; Aug: 55.22; Sep: 53.8; Oct: 33.62; Nov: 27.3; Dec: -0.4
WI | MINOCQUA/WOODRUFF | Jan: 14.7; Feb: 16.7; Mar: 27.7; Apr: 41.1; May: 53.4; Jun: 62.7; Jul: 66.9; Aug: 65.1; Sep: 57.3; Oct: 45; Nov: 32.7; Dec: 19.1; Jan: 6.4; Feb: 12.38; Mar: 19.4; Apr: 32.54; May: 35.8; Jun: 51.8; Jul: 55.76; Aug: 56.12; Sep: 49.1; Oct: 38.66; Nov: 27.1; Dec: 5.5
ND | MINOT AFB | Jan: 8.6; Feb: 15.1; Mar: 26.4; Apr: 40.3; May: 54.1; Jun: 63.3; Jul: 67.8; Aug: 67.8; Sep: 57.6; Oct: 42.9; Nov: 26.1; Dec: 12.8; Jan: 14.7; Feb: 16.52; Mar: 19.8; Apr: 29.3; May: 37.8; Jun: 50.72; Jul: 56.66; Aug: 52.16; Sep: 43.7; Oct: 33.08; Nov: 28.2; Dec: 19.2
ND | MINOT FAA AP | Jan: 12.3; Feb: 16.8; Mar: 27.6; Apr: 42.3; May: 54.3; Jun: 63.7; Jul: 69.4; Aug: 68.7; Sep: 59.1; Oct: 44.7; Nov: 28.5; Dec: 16; Jan: 2.7; Feb: 11.12; Mar: 18.7; Apr: 29.48; May: 42.6; Jun: 49.28; Jul: 50.18; Aug: 52.34; Sep: 41; Oct: 30.92; Nov: 21.7; Dec: 8.4
MT | MISSOULA INTERNATIONAL AP | Jan: 25.7; Feb: 29.4; Mar: 38; Apr: 44.7; May: 53; Jun: 59.8; Jul: 69.1; Aug: 67.6; Sep: 58.4; Oct: 44.9; Nov: 32.8; Dec: 24.7; Jan: 21.4; Feb: 24.62; Mar: 24.1; Apr: 29.12; May: 37.6; Jun: 44.06; Jul: 47.12; Aug: 45.14; Sep: 39.2; Oct: 33.26; Nov: 28; Dec: 20.8
SD | MITCHELL (AWOS) | Jan: 18.1; Feb: 22.7; Mar: 33.7; Apr: 47.1; May: 59; Jun: 68.9; Jul: 74.6; Aug: 71.8; Sep: 63.3; Oct: 50.1; Nov: 34.7; Dec: 22.1; Jan: 12.6; Feb: 13.46; Mar: 15.8; Apr: 38.12; May: 45.3; Jun: 56.48; Jul: 64.22; Aug: 63.32; Sep: 51.6; Oct: 34.34; Nov: 18.9; Dec: 18.7
UT | MOAB/CANYONLANDS [UO] | Jan: 26.7; Feb: 35; Mar: 45.6; Apr: 53.3; May: 63.7; Jun: 74.6; Jul: 81.9; Aug: 77.8; Sep: 68.8; Oct: 54.6; Nov: 40.1; Dec: 27.8; Jan: 18.3; Feb: 19.04; Mar: 29.3; Apr: 23.18; May: 26.6; Jun: 35.78; Jul: 36.32; Aug: 40.82; Sep: 45.3; Oct: 31.28; Nov: 21.4; Dec: 19.8
AL | MOBILE DOWNTOWN AP | Jan: 51; Feb: 53.9; Mar: 60.3; Apr: 67.1; May: 74.4; Jun: 80.4; Jul: 82; Aug: 82.4; Sep: 78.8; Oct: 69.5; Nov: 59.6; Dec: 53; Jan: 48.2; Feb: 47.48; Mar: 47.3; Apr: 56.48; May: 67.8; Jun: 66.56; Jul: 74.12; Aug: 72.32; Sep: 67.5; Oct: 55.04; Nov: 50.2; Dec: 40.3
AL | MOBILE REGIONAL AP | Jan: 51.3; Feb: 54.5; Mar: 60.3; Apr: 66.7; May: 74.2; Jun: 79.9; Jul: 81.6; Aug: 81.7; Sep: 77.7; Oct: 68.3; Nov: 58.8; Dec: 53; Jan: 38.5; Feb: 44.06; Mar: 51.3; Apr: 53.6; May: 65.1; Jun: 71.24; Jul: 72.32; Aug: 71.6; Sep: 66.2; Oct: 57.92; Nov: 50.4; Dec: 42.3
SD | MOBRIDGE | Jan: 16; Feb: 20.3; Mar: 31.1; Apr: 44.9; May: 55.8; Jun: 65.9; Jul: 73.6; Aug: 72; Sep: 62.2; Oct: 47.3; Nov: 32.4; Dec: 19.5; Jan: 10.2; Feb: 18.68; Mar: 22.3; Apr: 32.36; May: 42.3; Jun: 52.7; Jul: 62.6; Aug: 58.28; Sep: 47.5; Oct: 29.48; Nov: 19.2; Dec: 7.2
CA | MODESTO CITY-COUNTY AP | Jan: 47; Feb: 51.4; Mar: 56.4; Apr: 60.6; May: 68.6; Jun: 74.5; Jul: 79.1; Aug: 77.7; Sep: 73.9; Oct: 64.5; Nov: 54.2; Dec: 47.4; Jan: 41.4; Feb: 39.92; Mar: 46.6; Apr: 42.62; May: 42.8; Jun: 50.72; Jul: 51.44; Aug: 52.16; Sep: 50.2; Oct: 47.12; Nov: 44.2; Dec: 42.1
IL | MOLINE QUAD CITY INTL AP | Jan: 23.5; Feb: 27.9; Mar: 39.5; Apr: 51.4; May: 62; Jun: 71.4; Jul: 75; Aug: 73.3; Sep: 65.2; Oct: 53.3; Nov: 40.3; Dec: 28; Jan: 9.9; Feb: 14.9; Mar: 27.3; Apr: 37.94; May: 46.9; Jun: 57.02; Jul: 63.68; Aug: 64.58; Sep: 55.4; Oct: 40.82; Nov: 28.6; Dec: 17.4
HI | MOLOKAI (AMOS) | Jan: 71.2; Feb: 71; Mar: 71.6; Apr: 73; May: 74.8; Jun: 76.9; Jul: 77.8; Aug: 78.7; Sep: 78.4; Oct: 77.4; Nov: 75.1; Dec: 72.8; Jan: 62.6; Feb: 60.8; Mar: 60.3; Apr: 38.48; May: 49.6; Jun: 64.76; Jul: 66.02; Aug: 69.98; Sep: 70; Oct: 67.46; Nov: 66.4; Dec: 62.4
NB | MONCTON AP | Jan: 17.2; Feb: 18.8; Mar: 27.5; Apr: 38.7; May: 50; Jun: 59.8; Jul: 66.4; Aug: 65.4; Sep: 57.5; Oct: 46.6; Nov: 36; Dec: 24.9; Jan: 10.2; Feb: 11.84; Mar: 19.8; Apr: 29.66; May: 39.7; Jun: 50.72; Jul: 58.1; Aug: 57.2; Sep: 50; Oct: 40.28; Nov: 31.5; Dec: 18.5
IN | MONROE CO | Jan: 30.1; Feb: 33; Mar: 43.8; Apr: 55.2; May: 63.8; Jun: 72; Jul: 74.5; Aug: 73.7; Sep: 66.3; Oct: 55.1; Nov: 44.5; Dec: 33.8; Jan: 21.4; Feb: 24.44; Mar: 34; Apr: 45.86; May: 54; Jun: 62.42; Jul: 66.92; Aug: 69.08; Sep: 57.7; Oct: 45.86; Nov: 40.3; Dec: 22.8
LA | MONROE REGIONAL AP | Jan: 47.4; Feb: 50.9; Mar: 58; Apr: 65.9; May: 73.9; Jun: 80.5; Jul: 82.7; Aug: 82.6; Sep: 76.9; Oct: 66.2; Nov: 55.7; Dec: 48.8; Jan: 36.7; Feb: 44.96; Mar: 45.3; Apr: 51.08; May: 62.1; Jun: 69.08; Jul: 73.4; Aug: 73.22; Sep: 60.4; Oct: 57.74; Nov: 49.1; Dec: 37.6
QC | MONT JOLI AB | Jan: 11.8; Feb: 13.9; Mar: 23.6; Apr: 36.2; May: 48.1; Jun: 58.5; Jul: 64.1; Aug: 62.7; Sep: 54.7; Oct: 43.3; Nov: 32.6; Dec: 20.5; Jan: 4.8; Feb: 7.34; Mar: 16; Apr: 26.96; May: 37.4; Jun: 48.38; Jul: 55.22; Aug: 53.96; Sep: 47.1; Oct: 36.32; Nov: 27; Dec: 14.2
QC | MONT-ORFORD | Jan: 10.3; Feb: 12.8; Mar: 21.7; Apr: 34.3; May: 47.7; Jun: 58.7; Jul: 61.7; Aug: 60.6; Sep: 52.7; Oct: 39.7; Nov: 29.1; Dec: 17.4; Jan: 1.6; Feb: 2.84; Mar: 11.7; Apr: 23.72; May: 35.8; Jun: 47.3; Jul: 51.98; Aug: 51.98; Sep: 45; Oct: 32.72; Nov: 23.9; Dec: 9.9
CA | MONTAGUE SISKIYOU COUNTY AP | Jan: 36.1; Feb: 39.3; Mar: 43.5; Apr: 48.3; May: 55.9; Jun: 63.4; Jul: 73.3; Aug: 71.2; Sep: 64.3; Oct: 52.2; Nov: 41; Dec: 35.1; Jan: 30.9; Feb: 28.04; Mar: 26.1; Apr: 35.96; May: 39.9; Jun: 39.74; Jul: 45.14; Aug: 43.7; Sep: 37; Oct: 34.16; Nov: 32.9; Dec: 26.4
CA | MONTEREY NAF | Jan: 51.6; Feb: 52.2; Mar: 53.3; Apr: 54.2; May: 56.7; Jun: 59.2; Jul: 60.3; Aug: 61; Sep: 61.1; Oct: 59; Nov: 55; Dec: 51.4; Jan: 40.5; Feb: 42.26; Mar: 48; Apr: 43.16; May: 48; Jun: 50.9; Jul: 54.14; Aug: 53.24; Sep: 52.9; Oct: 47.3; Nov: 44.1; Dec: 43.2
AL | MONTGOMERY DANNELLY FIELD | Jan: 47.7; Feb: 51.6; Mar: 58.2; Apr: 65; May: 72.8; Jun: 79.5; Jul: 82; Aug: 81.8; Sep: 76.8; Oct: 66.2; Nov: 55.9; Dec: 49.5; Jan: 34.5; Feb: 38.12; Mar: 48; Apr: 55.22; May: 61; Jun: 68.36; Jul: 71.96; Aug: 70.7; Sep: 64; Oct: 50; Nov: 45.5; Dec: 35.2
IA | MONTICELLO MUNI | Jan: 20.5; Feb: 23.9; Mar: 37.3; Apr: 48.6; May: 60.4; Jun: 69.9; Jul: 73; Aug: 71.2; Sep: 62.3; Oct: 50.5; Nov: 38; Dec: 24.8; Jan: 11.8; Feb: 16.52; Mar: 30.9; Apr: 42.62; May: 48.6; Jun: 57.92; Jul: 62.42; Aug: 64.4; Sep: 55.4; Oct: 45.14; Nov: 28; Dec: 16.2
NY | MONTICELLO(AWOS) | Jan: 22.9; Feb: 25; Mar: 34.1; Apr: 45.7; May: 55.9; Jun: 64.5; Jul: 68.6; Aug: 67.3; Sep: 59.3; Oct: 48.6; Nov: 37.7; Dec: 28.1; Jan: 19.2; Feb: 15.08; Mar: 18.1; Apr: 37.04; May: 42.1; Jun: 54.14; Jul: 59.9; Aug: 57.56; Sep: 53.2; Oct: 38.66; Nov: 29.3; Dec: 16.7
VT | MONTPELIER AP | Jan: 17.7; Feb: 19.8; Mar: 29.1; Apr: 42.1; May: 53.8; Jun: 63; Jul: 67; Aug: 65.5; Sep: 57.7; Oct: 46.3; Nov: 35.4; Dec: 24; Jan: 19.9; Feb: 6.8; Mar: 22.8; Apr: 32.54; May: 37.9; Jun: 54.32; Jul: 54.32; Aug: 58.46; Sep: 52.5; Oct: 41.36; Nov: 30.6; Dec: 15.3
QC | MONTREAL | Jan: 15.9; Feb: 18.5; Mar: 29; Apr: 43.6; May: 56.8; Jun: 66.4; Jul: 70.6; Aug: 69; Sep: 60.7; Oct: 48.3; Nov: 36.5; Dec: 23.6; Jan: 8.1; Feb: 9.5; Mar: 17.6; Apr: 29.48; May: 42.1; Jun: 53.96; Jul: 59.18; Aug: 58.64; Sep: 52.2; Oct: 40.1; Nov: 30.2; Dec: 16.7
QC | MONTREAL-MIRABEL | Jan: 12.6; Feb: 15.5; Mar: 26.5; Apr: 41.9; May: 55; Jun: 64.3; Jul: 68.2; Aug: 66.6; Sep: 58.1; Oct: 46; Nov: 34; Dec: 20.5; Jan: 4.8; Feb: 6.62; Mar: 16.2; Apr: 28.94; May: 41.2; Jun: 53.42; Jul: 58.46; Aug: 57.38; Sep: 50.5; Oct: 38.12; Nov: 28.2; Dec: 13.8
CO | MONTROSE CO. ARPT | Jan: 27.7; Feb: 33.3; Mar: 42.1; Apr: 49; May: 58.7; Jun: 68.6; Jul: 74.3; Aug: 71.3; Sep: 62.8; Oct: 50.6; Nov: 38.3; Dec: 27.5; Jan: 15.8; Feb: 20.66; Mar: 25.9; Apr: 24.8; May: 29.7; Jun: 32.9; Jul: 51.08; Aug: 46.58; Sep: 42.8; Oct: 37.58; Nov: 17.6; Dec: 16.7
GA | MOODY AFB/VALDOSTA | Jan: 52.6; Feb: 56.1; Mar: 61.3; Apr: 67.4; May: 75.3; Jun: 80.8; Jul: 82.5; Aug: 81.9; Sep: 78; Oct: 69.2; Nov: 59.5; Dec: 55; Jan: 33.4; Feb: 42.44; Mar: 44.1; Apr: 50.54; May: 59.4; Jun: 69.44; Jul: 72.86; Aug: 69.44; Sep: 66; Oct: 52.34; Nov: 46; Dec: 38.1
SK | MOOSE JAW AP | Jan: 10.9; Feb: 12.9; Mar: 24.1; Apr: 40.3; May: 51.2; Jun: 59.8; Jul: 66.1; Aug: 64.5; Sep: 55.6; Oct: 41.1; Nov: 26.4; Dec: 13.2; Jan: 2.1; Feb: 3.74; Mar: 16.3; Apr: 27.5; May: 34.5; Jun: 46.94; Jul: 54.32; Aug: 51.08; Sep: 42.1; Oct: 29.48; Nov: 18.5; Dec: 4.1
MN | MORA MUNI (AWOS) | Jan: 12.1; Feb: 16.5; Mar: 28.6; Apr: 42.7; May: 54.3; Jun: 63.9; Jul: 68.6; Aug: 66.4; Sep: 57.7; Oct: 45.5; Nov: 32.6; Dec: 18.4; Jan: 9.3; Feb: 0.32; Mar: 25.3; Apr: 30.74; May: 39; Jun: 49.64; Jul: 58.64; Aug: 60.44; Sep: 55.4; Oct: 38.48; Nov: 26.4; Dec: -1.1
WV | MORGANTOWN HART FIELD | Jan: 32.5; Feb: 34.6; Mar: 42.6; Apr: 53.8; May: 62; Jun: 70; Jul: 73.6; Aug: 72.5; Sep: 65.6; Oct: 54.9; Nov: 45; Dec: 36.4; Jan: 19.2; Feb: 26.6; Mar: 32.7; Apr: 42.26; May: 50.2; Jun: 59.9; Jul: 64.04; Aug: 62.42; Sep: 56.7; Oct: 48.02; Nov: 32.5; Dec: 30.2
MN | MORRIS MUNI (AWOS) | Jan: 10.6; Feb: 14.7; Mar: 27.8; Apr: 43.6; May: 55.9; Jun: 66; Jul: 70; Aug: 67.4; Sep: 59.5; Oct: 46.5; Nov: 30.5; Dec: 16.5; Jan: 8.8; Feb: 17.78; Mar: 22.1; Apr: 30.74; May: 38.8; Jun: 56.48; Jul: 63.14; Aug: 59.54; Sep: 49.5; Oct: 34.34; Nov: 25.5; Dec: 15.1
WA | MOSES LAKE GRANT COUNTY AP | Jan: 30.2; Feb: 36; Mar: 43.6; Apr: 50.1; May: 58.7; Jun: 65.9; Jul: 74.1; Aug: 72.5; Sep: 63.6; Oct: 50.3; Nov: 37.8; Dec: 29.7; Jan: 26.8; Feb: 31.28; Mar: 34.3; Apr: 35.6; May: 39.2; Jun: 45.68; Jul: 48.92; Aug: 50.54; Sep: 41.2; Oct: 36.5; Nov: 33.4; Dec: 29.5
WI | MOSINEE/CENTRAL WI | Jan: 14.8; Feb: 20.6; Mar: 29.2; Apr: 42.7; May: 53.5; Jun: 63.8; Jul: 68.4; Aug: 66.5; Sep: 59.1; Oct: 46.4; Nov: 32; Dec: 20.6; Jan: 3; Feb: 16.88; Mar: 19.9; Apr: 29.84; May: 40.3; Jun: 55.04; Jul: 57.74; Aug: 58.46; Sep: 48.2; Oct: 35.78; Nov: 24.1; Dec: 3.9
MI | MOUNT CLEMENS SELFRIDGE FLD | Jan: 25.1; Feb: 28.1; Mar: 35; Apr: 46.9; May: 57.8; Jun: 68; Jul: 72; Aug: 70.5; Sep: 63.1; Oct: 51.9; Nov: 40.5; Dec: 30.7; Jan: 30.2; Feb: 30.56; Mar: 31.5; Apr: 31.64; May: 42.6; Jun: 54.86; Jul: 56.84; Aug: 58.82; Sep: 49.6; Oct: 39.92; Nov: 33.3; Dec: 29.7
IL | MOUNT VERNON (AWOS) | Jan: 31.3; Feb: 35.1; Mar: 44.6; Apr: 55.6; May: 64.7; Jun: 73.7; Jul: 77; Aug: 75.8; Sep: 67.5; Oct: 55.8; Nov: 44.4; Dec: 34.8; Jan: 25.9; Feb: 24.26; Mar: 26.1; Apr: 36.14; May: 60.4; Jun: 61.52; Jul: 60.26; Aug: 65.48; Sep: 62.6; Oct: 47.12; Nov: 37.9; Dec: 26.4
NH | MOUNT WASHINGTON | Jan: 7.1; Feb: 7; Mar: 13.8; Apr: 24.2; May: 35.9; Jun: 45.5; Jul: 49.2; Aug: 48.2; Sep: 42.1; Oct: 31.3; Nov: 21.3; Dec: 12.1; Jan: 8.4; Feb: 3.38; Mar: 14.7; Apr: 21.02; May: 28.6; Jun: 36.86; Jul: 42.26; Aug: 40.46; Sep: 35.2; Oct: 27.68; Nov: 18.5; Dec: 9.1
ID | MOUNTAIN HOME AFB | Jan: 30.5; Feb: 35.6; Mar: 43.2; Apr: 49.1; May: 58.1; Jun: 65.9; Jul: 75.9; Aug: 74.6; Sep: 65.2; Oct: 51; Nov: 38.4; Dec: 29.5; Jan: 28; Feb: 24.44; Mar: 29.8; Apr: 30.38; May: 32.7; Jun: 33.44; Jul: 32.72; Aug: 35.42; Sep: 33.4; Oct: 29.3; Nov: 28.2; Dec: 25
CA | MOUNTAIN VIEW MOFFETT FLD NAS | Jan: 51; Feb: 53.2; Mar: 56; Apr: 58.9; May: 62.5; Jun: 65.9; Jul: 68; Aug: 68.3; Sep: 67.8; Oct: 63.8; Nov: 56.7; Dec: 50.7; Jan: 43.7; Feb: 41.72; Mar: 47.8; Apr: 41.54; May: 45.5; Jun: 50.72; Jul: 55.4; Aug: 56.66; Sep: 55.2; Oct: 48.92; Nov: 43.7; Dec: 42.6
IA | MUSCATINE | Jan: 24.4; Feb: 28.3; Mar: 39.4; Apr: 52.2; May: 62.7; Jun: 72.3; Jul: 76.6; Aug: 74; Sep: 66; Oct: 53.6; Nov: 40.5; Dec: 28.6; Jan: 10.8; Feb: 15.8; Mar: 29.8; Apr: 35.96; May: 53.6; Jun: 59.72; Jul: 60.62; Aug: 67.46; Sep: 60.1; Oct: 40.46; Nov: 30.2; Dec: 23.5
AL | MUSCLE SHOALS REGIONAL AP | Jan: 42.5; Feb: 45.8; Mar: 53.2; Apr: 62.3; May: 70.1; Jun: 77.3; Jul: 80.3; Aug: 79.7; Sep: 73.7; Oct: 62.4; Nov: 51.7; Dec: 44.1; Jan: 39.2; Feb: 32.36; Mar: 41.5; Apr: 49.64; May: 60.4; Jun: 64.76; Jul: 73.04; Aug: 66.38; Sep: 61; Oct: 58.64; Nov: 47.1; Dec: 39.9
MI | MUSKEGON COUNTY ARPT | Jan: 25.8; Feb: 26.9; Mar: 34.9; Apr: 46.1; May: 56.8; Jun: 66.3; Jul: 70.6; Aug: 69.5; Sep: 61.9; Oct: 50.8; Nov: 40; Dec: 30.7; Jan: 18; Feb: 15.26; Mar: 25; Apr: 31.28; May: 44.4; Jun: 54.68; Jul: 61.52; Aug: 62.24; Sep: 53.2; Oct: 41.72; Nov: 30.2; Dec: 22.6
SC | MYRTLE BEACH AFB | Jan: 46.8; Feb: 49.7; Mar: 55.4; Apr: 62.4; May: 70.2; Jun: 76.7; Jul: 80.6; Aug: 78.7; Sep: 74.6; Oct: 65.3; Nov: 56.4; Dec: 48.8; Jan: 29.5; Feb: 37.76; Mar: 49.3; Apr: 50.9; May: 60.1; Jun: 66.2; Jul: 73.22; Aug: 70.88; Sep: 65.1; Oct: 48.74; Nov: 49.8; Dec: 34.3
TX | NACOGDOCHES (AWOS) | Jan: 48.1; Feb: 51.8; Mar: 58.1; Apr: 65.5; May: 73.5; Jun: 79.7; Jul: 82.3; Aug: 82.3; Sep: 76.7; Oct: 66.3; Nov: 56.1; Dec: 49; Jan: 34.7; Feb: 38.3; Mar: 36.9; Apr: 48.92; May: 61.5; Jun: 70.52; Jul: 69.26; Aug: 69.08; Sep: 60.8; Oct: 55.76; Nov: 47.8; Dec: 39.9
MA | NANTUCKET MEMORIAL AP | Jan: 32.8; Feb: 33.4; Mar: 38.1; Apr: 45.6; May: 53.8; Jun: 62; Jul: 69; Aug: 68.7; Sep: 63.9; Oct: 55.1; Nov: 46.5; Dec: 38.3; Jan: 23; Feb: 31.1; Mar: 32.5; Apr: 40.46; May: 43.9; Jun: 55.4; Jul: 63.68; Aug: 64.4; Sep: 58.8; Oct: 47.48; Nov: 37.9; Dec: 34.9
CA | NAPA CO. AIRPORT | Jan: 46.8; Feb: 49.4; Mar: 52.5; Apr: 54.7; May: 59.7; Jun: 64.2; Jul: 65.7; Aug: 65.9; Sep: 65; Oct: 59.7; Nov: 52.4; Dec: 47; Jan: 38.1; Feb: 44.06; Mar: 47.3; Apr: 44.96; May: 49.5; Jun: 51.44; Jul: 55.04; Aug: 55.76; Sep: 52.2; Oct: 48.02; Nov: 46.4; Dec: 43.5
FL | NAPLES MUNICIPAL | Jan: 64.5; Feb: 66.4; Mar: 69.6; Apr: 73.5; May: 78.1; Jun: 81.3; Jul: 82.2; Aug: 82.6; Sep: 81.7; Oct: 78; Nov: 71.1; Dec: 66.7; Jan: 52; Feb: 51.08; Mar: 61; Apr: 57.92; May: 64.4; Jun: 71.42; Jul: 73.94; Aug: 74.84; Sep: 71.4; Oct: 65.48; Nov: 59.9; Dec: 55.6
FL | NASA SHUTTLE FCLTY | Jan: 61.4; Feb: 63.5; Mar: 66.2; Apr: 70.3; May: 75.9; Jun: 79.7; Jul: 81.3; Aug: 81.2; Sep: 79.9; Oct: 75.1; Nov: 68.7; Dec: 63.3; Jan: 44.8; Feb: 50.72; Mar: 55.4; Apr: 59.9; May: 66.2; Jun: 73.04; Jul: 74.3; Aug: 72.32; Sep: 71.6; Oct: 64.22; Nov: 63.5; Dec: 56.1
TN | NASHVILLE INTERNATIONAL AP | Jan: 39.2; Feb: 42.8; Mar: 50.7; Apr: 60.2; May: 68.4; Jun: 76.3; Jul: 79.8; Aug: 79.2; Sep: 72.2; Oct: 60.8; Nov: 49.8; Dec: 41.8; Jan: 27.3; Feb: 26.24; Mar: 40.3; Apr: 42.98; May: 56.3; Jun: 64.76; Jul: 68.72; Aug: 68.72; Sep: 60.3; Oct: 50.18; Nov: 35.4; Dec: 31.1
MS | NATCHEZ/HARDY(AWOS) | Jan: 47.9; Feb: 51.5; Mar: 57.7; Apr: 64.8; May: 72.9; Jun: 78.8; Jul: 80.8; Aug: 80.5; Sep: 75.3; Oct: 65.7; Nov: 56.2; Dec: 49.8; Jan: 38.7; Feb: 45.14; Mar: 51.8; Apr: 59.72; May: 59.2; Jun: 67.82; Jul: 73.04; Aug: 70.16; Sep: 62.1; Oct: 53.06; Nov: 45.3; Dec: 38.5
CA | NEEDLES AIRPORT | Jan: 55.2; Feb: 58.1; Mar: 65.7; Apr: 72.6; May: 83; Jun: 92.4; Jul: 98; Aug: 95.7; Sep: 89.1; Oct: 75.9; Nov: 63.6; Dec: 53.6; Jan: 32; Feb: 32.54; Mar: 26.2; Apr: 35.42; May: 33.3; Jun: 38.3; Jul: 51.08; Aug: 54.32; Sep: 45.1; Oct: 41.72; Nov: 33.3; Dec: 28.6
NV | NELLIS AFB | Jan: 47.7; Feb: 52; Mar: 59.7; Apr: 66.7; May: 76.6; Jun: 86; Jul: 92; Aug: 90.4; Sep: 82.6; Oct: 68.9; Nov: 55.4; Dec: 46.3; Jan: 31.8; Feb: 27.32; Mar: 34; Apr: 25.88; May: 31.8; Jun: 35.42; Jul: 42.08; Aug: 39.92; Sep: 36.5; Oct: 30.74; Nov: 33.6; Dec: 28.4
AK | NENANA MUNICIPAL AP | Jan: -4.7; Feb: 1.7; Mar: 9.9; Apr: 31.6; May: 48.2; Jun: 59; Jul: 60.6; Aug: 55.6; Sep: 44.7; Oct: 25.2; Nov: 4.2; Dec: -2.9; Jan: 5.9; Feb: 3.02; Mar: 9.3; Apr: 13.64; May: 29.5; Jun: 30.02; Jul: 34.88; Aug: 31.1; Sep: 23.4; Oct: 15.8; Nov: 13.8; Dec: -15.7
MA | NEW BEDFORD RGNL | Jan: 30; Feb: 32.1; Mar: 38.2; Apr: 47.7; May: 56.9; Jun: 65.9; Jul: 72.1; Aug: 70.5; Sep: 63.4; Oct: 52.8; Nov: 43.4; Dec: 35.4; Jan: 16.3; Feb: 17.06; Mar: 30.4; Apr: 35.06; May: 47.1; Jun: 57.2; Jul: 61.88; Aug: 60.8; Sep: 55.9; Oct: 44.42; Nov: 37; Dec: 30.6
NC | NEW BERN CRAVEN CO REGL AP | Jan: 45.1; Feb: 47.2; Mar: 53.5; Apr: 62.1; May: 69.6; Jun: 77.3; Jul: 80.5; Aug: 79.1; Sep: 74; Oct: 64.2; Nov: 54.8; Dec: 47.9; Jan: 40.1; Feb: 37.76; Mar: 49.5; Apr: 51.8; May: 58.5; Jun: 67.46; Jul: 71.24; Aug: 71.06; Sep: 65.8; Oct: 60.08; Nov: 40.3; Dec: 44.4
CT | NEW HAVEN TWEED AIRPORT | Jan: 30.5; Feb: 32; Mar: 39; Apr: 49.4; May: 58.6; Jun: 68.2; Jul: 74.4; Aug: 72.8; Sep: 66.4; Oct: 55.1; Nov: 45.2; Dec: 36.3; Jan: 19.4; Feb: 18.32; Mar: 28.4; Apr: 34.34; May: 48; Jun: 57.56; Jul: 63.32; Aug: 63.5; Sep: 57.6; Oct: 45.14; Nov: 41; Dec: 22.6
LA | NEW IBERIA NAAS | Jan: 53.1; Feb: 55.9; Mar: 62.5; Apr: 69.4; May: 76.2; Jun: 81.3; Jul: 82.4; Aug: 83; Sep: 79.1; Oct: 70.2; Nov: 60.9; Dec: 54.2; Jan: 38.8; Feb: 51.44; Mar: 45; Apr: 57.92; May: 66.7; Jun: 72.32; Jul: 74.48; Aug: 74.12; Sep: 68.5; Oct: 56.66; Nov: 54.5; Dec: 45
LA | NEW ORLEANS ALVIN CALLENDER F | Jan: 53.4; Feb: 56.4; Mar: 61.9; Apr: 67.9; May: 75.2; Jun: 80.5; Jul: 81.9; Aug: 82.2; Sep: 78.7; Oct: 69.9; Nov: 59.9; Dec: 55.9; Jan: 44.1; Feb: 49.82; Mar: 48.4; Apr: 60.98; May: 70; Jun: 72.86; Jul: 74.48; Aug: 70.88; Sep: 69.1; Oct: 56.66; Nov: 56.5; Dec: 46.9
LA | NEW ORLEANS INTL ARPT | Jan: 54.1; Feb: 57.1; Mar: 62.7; Apr: 69.3; May: 76.6; Jun: 81.7; Jul: 83.1; Aug: 83.2; Sep: 79.9; Oct: 71.4; Nov: 61.7; Dec: 55.9; Jan: 41; Feb: 47.3; Mar: 53.8; Apr: 60.44; May: 66; Jun: 72.14; Jul: 74.3; Aug: 74.48; Sep: 66.9; Oct: 59.9; Nov: 57; Dec: 45.3
LA | NEW ORLEANS LAKEFRONT AP | Jan: 54.8; Feb: 58.4; Mar: 64.1; Apr: 71; May: 78.2; Jun: 83.3; Jul: 84.8; Aug: 85.3; Sep: 81.7; Oct: 73.1; Nov: 63.2; Dec: 57.2; Jan: 48.7; Feb: 49.64; Mar: 50.4; Apr: 55.22; May: 69.6; Jun: 73.76; Jul: 73.94; Aug: 73.4; Sep: 70.3; Oct: 62.24; Nov: 50.7; Dec: 47.1
NC | NEW RIVER MCAF | Jan: 45.8; Feb: 48; Mar: 54.3; Apr: 62.6; May: 70.1; Jun: 77.1; Jul: 80.5; Aug: 79; Sep: 74; Oct: 64.3; Nov: 54.8; Dec: 48.3; Jan: 31.5; Feb: 31.82; Mar: 34.9; Apr: 50; May: 61.2; Jun: 67.28; Jul: 69.08; Aug: 71.78; Sep: 68; Oct: 57.92; Nov: 49.3; Dec: 31.1
MN | NEW ULM MUNI (AWOS) | Jan: 14.4; Feb: 18.9; Mar: 31.4; Apr: 46.2; May: 58.1; Jun: 68.2; Jul: 71.9; Aug: 69.4; Sep: 61.5; Oct: 48.9; Nov: 33.5; Dec: 19.9; Jan: 13.5; Feb: 10.22; Mar: 16.9; Apr: 37.04; May: 43.7; Jun: 55.4; Jul: 63.32; Aug: 64.04; Sep: 53.6; Oct: 39.38; Nov: 27; Dec: 21.6
NY | NEW YORK CENTRAL PRK OBS BELV | Jan: 33.5; Feb: 35.6; Mar: 42.7; Apr: 53.4; May: 62.3; Jun: 71.3; Jul: 76.5; Aug: 75.1; Sep: 68.4; Oct: 57.3; Nov: 47.5; Dec: 38.5; Jan: 15.8; Feb: 21.74; Mar: 28.4; Apr: 39.38; May: 52.2; Jun: 57.92; Jul: 65.48; Aug: 62.96; Sep: 56.7; Oct: 43.16; Nov: 34.9; Dec: 23.4
NY | NEW YORK J F KENNEDY INT AR | Jan: 33.4; Feb: 34.9; Mar: 41.6; Apr: 51.2; May: 60.6; Jun: 70.3; Jul: 76.1; Aug: 74.9; Sep: 68.4; Oct: 57.6; Nov: 47.4; Dec: 38.5; Jan: 24.3; Feb: 18.68; Mar: 32.5; Apr: 40.46; May: 48.4; Jun: 60.44; Jul: 68.54; Aug: 62.78; Sep: 55.8; Oct: 46.22; Nov: 35.8; Dec: 27
NY | NEW YORK LAGUARDIA ARPT | Jan: 34.2; Feb: 35.9; Mar: 42.6; Apr: 53.2; May: 62.8; Jun: 72.7; Jul: 78.1; Aug: 76.8; Sep: 69.8; Oct: 59; Nov: 48.6; Dec: 39.5; Jan: 22.1; Feb: 17.42; Mar: 30.6; Apr: 38.48; May: 45.5; Jun: 57.56; Jul: 67.82; Aug: 64.04; Sep: 56.3; Oct: 43.52; Nov: 36.1; Dec: 25.9
NJ | NEWARK INTERNATIONAL ARPT | Jan: 33.3; Feb: 35.3; Mar: 42.9; Apr: 53.6; May: 63.3; Jun: 73; Jul: 78.1; Aug: 76.3; Sep: 69; Oct: 57.7; Nov: 47.4; Dec: 38.2; Jan: 17.4; Feb: 22.64; Mar: 30.2; Apr: 37.76; May: 48; Jun: 57.92; Jul: 63.68; Aug: 62.78; Sep: 55.4; Oct: 45.14; Nov: 32.4; Dec: 24.4
VA | NEWPORT NEWS | Jan: 40.8; Feb: 42.6; Mar: 49.4; Apr: 59; May: 66.9; Jun: 75.3; Jul: 79.9; Aug: 77.9; Sep: 71.8; Oct: 61.5; Nov: 51.5; Dec: 44.1; Jan: 31.8; Feb: 29.66; Mar: 40.1; Apr: 44.24; May: 57.4; Jun: 64.76; Jul: 71.6; Aug: 64.94; Sep: 65.5; Oct: 51.26; Nov: 35.4; Dec: 37.6
KS | NEWTON (AWOS) | Jan: 30.6; Feb: 35.1; Mar: 44.3; Apr: 54.1; May: 64.4; Jun: 74.2; Jul: 79.1; Aug: 77.9; Sep: 68.4; Oct: 57.3; Nov: 43.9; Dec: 33.2; Jan: 23.2; Feb: 24.62; Mar: 22.3; Apr: 45.14; May: 54.3; Jun: 57.74; Jul: 64.58; Aug: 60.8; Sep: 60.3; Oct: 39.02; Nov: 25.5; Dec: 25.9
IA | NEWTON MUNI | Jan: 22.8; Feb: 25.7; Mar: 37.9; Apr: 50.7; May: 61.3; Jun: 70.7; Jul: 75.1; Aug: 72.6; Sep: 64.2; Oct: 52.6; Nov: 38.9; Dec: 26.4; Jan: 20.8; Feb: 17.42; Mar: 37.8; Apr: 43.88; May: 50.2; Jun: 62.42; Jul: 64.22; Aug: 60.8; Sep: 52.7; Oct: 47.12; Nov: 26.8; Dec: 18.1
NY | NIAGARA FALLS AF | Jan: 25; Feb: 25.8; Mar: 33.7; Apr: 45.8; May: 57.1; Jun: 67.2; Jul: 71.5; Aug: 70; Sep: 62.3; Oct: 51.2; Nov: 40.3; Dec: 30.8; Jan: 25.7; Feb: 17.96; Mar: 19.2; Apr: 39.02; May: 38.5; Jun: 59.72; Jul: 60.08; Aug: 59.54; Sep: 55.9; Oct: 42.8; Nov: 37.8; Dec: 24.4
QC | NICOLET | Jan: 12.5; Feb: 15.2; Mar: 26.3; Apr: 41.3; May: 55; Jun: 64.2; Jul: 68.4; Aug: 66.3; Sep: 58.5; Oct: 46.8; Nov: 34.9; Dec: 21.4; Jan: 4.1; Feb: 6.98; Mar: 16.7; Apr: 29.3; May: 42.1; Jun: 53.96; Jul: 59.36; Aug: 58.46; Sep: 51.3; Oct: 39.2; Nov: 29.3; Dec: 12.9
AK | NOME MUNICIPAL ARPT | Jan: 4.9; Feb: 7.4; Mar: 9.3; Apr: 22; May: 36.5; Jun: 47.6; Jul: 51.9; Aug: 50.5; Sep: 43.1; Oct: 29.6; Nov: 17.4; Dec: 8.2; Jan: 8.2; Feb: -0.22; Mar: 0.3; Apr: 10.22; May: 31.8; Jun: 40.28; Jul: 45.68; Aug: 46.58; Sep: 36.7; Oct: 20.48; Nov: 10.8; Dec: 0.9
VA | NORFOLK INTERNATIONAL AP | Jan: 42.1; Feb: 43.7; Mar: 50.2; Apr: 59.4; May: 67.3; Jun: 75.8; Jul: 80.2; Aug: 78.4; Sep: 72.9; Oct: 62.8; Nov: 52.9; Dec: 45.6; Jan: 26.1; Feb: 26.96; Mar: 34.7; Apr: 46.22; May: 54.9; Jun: 63.68; Jul: 68.9; Aug: 69.44; Sep: 61.5; Oct: 51.8; Nov: 43.5; Dec: 36.7
NE | NORFOLK KARL STEFAN MEM ARPT | Jan: 23; Feb: 27.4; Mar: 38.1; Apr: 49.6; May: 60.8; Jun: 70.5; Jul: 75.1; Aug: 73.1; Sep: 64.6; Oct: 51.7; Nov: 37.1; Dec: 25.6; Jan: 8.4; Feb: 16.34; Mar: 24.4; Apr: 35.6; May: 45.3; Jun: 55.4; Jul: 60.8; Aug: 62.42; Sep: 53.4; Oct: 37.58; Nov: 23.4; Dec: 11.3
VA | NORFOLK NAS | Jan: 42.9; Feb: 44.5; Mar: 51; Apr: 60.5; May: 68.5; Jun: 76.8; Jul: 81.2; Aug: 79.3; Sep: 74; Oct: 64; Nov: 53.9; Dec: 46.7; Jan: 31.8; Feb: 31.46; Mar: 43.3; Apr: 50.9; May: 55.4; Jun: 64.4; Jul: 68.72; Aug: 69.98; Sep: 61.3; Oct: 51.44; Nov: 38.7; Dec: 38.5
MA | NORTH ADAMS | Jan: 23.1; Feb: 26.4; Mar: 34.1; Apr: 46.2; May: 56.7; Jun: 65.3; Jul: 69.1; Aug: 67.6; Sep: 60.8; Oct: 49.5; Nov: 39.7; Dec: 29.8; Jan: 17.1; Feb: 20.3; Mar: 27.7; Apr: 33.98; May: 43; Jun: 55.22; Jul: 57.38; Aug: 58.64; Sep: 55.2; Oct: 42.26; Nov: 33.1; Dec: 19.8
ON | NORTH BAY AP | Jan: 10.4; Feb: 13.6; Mar: 24.5; Apr: 38.8; May: 52.6; Jun: 62.1; Jul: 65.9; Aug: 64.3; Sep: 55.8; Oct: 43.7; Nov: 31.2; Dec: 18.1; Jan: 4.8; Feb: 6.08; Mar: 13.6; Apr: 25.52; May: 38.7; Jun: 51.62; Jul: 55.94; Aug: 55.58; Sep: 49.8; Oct: 37.4; Nov: 27.3; Dec: 13.3
OR | NORTH BEND MUNI AIRPORT | Jan: 46.7; Feb: 47.1; Mar: 47.9; Apr: 49.7; May: 53.5; Jun: 56.8; Jul: 59.2; Aug: 59.7; Sep: 58.2; Oct: 54.1; Nov: 49.6; Dec: 45.9; Jan: 40.1; Feb: 42.08; Mar: 41.9; Apr: 42.98; May: 47.7; Jun: 50.18; Jul: 51.26; Aug: 53.42; Sep: 50.5; Oct: 48.74; Nov: 45; Dec: 40.3
SC | NORTH MYRTLE BEACH-GRAND STRAND FIELD | Jan: 46; Feb: 50; Mar: 55; Apr: 62; May: 71; Jun: 77; Jul: 80; Aug: 79; Sep: 75; Oct: 66; Nov: 56; Dec: 49; Jan: 30.9; Feb: 42.98; Mar: 48.6; Apr: 53.42; May: 60.1; Jun: 68.54; Jul: 72.68; Aug: 69.26; Sep: 64.8; Oct: 52.34; Nov: 49.1; Dec: 36.9
NE | NORTH PLATTE REGIONAL AP | Jan: 26; Feb: 29.4; Mar: 38.8; Apr: 47.7; May: 58.3; Jun: 68.7; Jul: 74.8; Aug: 72.8; Sep: 63.3; Oct: 49.7; Nov: 36.3; Dec: 26.8; Jan: 13.8; Feb: 17.42; Mar: 24.6; Apr: 32.54; May: 43.9; Jun: 54.14; Jul: 58.82; Aug: 60.26; Sep: 47.5; Oct: 33.8; Nov: 25.2; Dec: 17.4
BC | NORTH VANCOUVER | Jan: 41.1; Feb: 42.3; Mar: 45.2; Apr: 50.1; May: 56.1; Jun: 60.9; Jul: 65.7; Aug: 65.5; Sep: 60.2; Oct: 51.7; Nov: 45; Dec: 41; Jan: 32.2; Feb: 33.26; Mar: 36.7; Apr: 39.56; May: 45.3; Jun: 50.36; Jul: 54.5; Aug: 54.68; Sep: 51.4; Oct: 44.96; Nov: 38.8; Dec: 31.5
ME | NORTHERN AROOSTOOK | Jan: 9.9; Feb: 13.9; Mar: 23.7; Apr: 36.8; May: 50.5; Jun: 59.4; Jul: 64.7; Aug: 62.9; Sep: 54.7; Oct: 42.9; Nov: 30.7; Dec: 17.9; Jan: 5.5; Feb: 4.82; Mar: 18.7; Apr: 26.24; May: 36.1; Jun: 45.14; Jul: 57.2; Aug: 53.6; Sep: 50.7; Oct: 31.28; Nov: 23.4; Dec: 8.8
AK | NORTHWAY AIRPORT | Jan: -14.5; Feb: -4.6; Mar: 6.9; Apr: 29.6; May: 46.1; Jun: 56.4; Jul: 58.8; Aug: 54.2; Sep: 42.3; Oct: 22; Nov: -2; Dec: -11.8; Jan: -16.4; Feb: -8.32; Mar: 2.1; Apr: 8.42; May: 29.1; Jun: 37.04; Jul: 46.94; Aug: 39.92; Sep: 29.3; Oct: 22.64; Nov: -8.5; Dec: -13.9
MA | NORWOOD MEMORIAL | Jan: 27.2; Feb: 29.5; Mar: 37.1; Apr: 47.9; May: 57.4; Jun: 66.6; Jul: 71.9; Aug: 70.1; Sep: 62.5; Oct: 51.3; Nov: 42.4; Dec: 33; Jan: 13.3; Feb: 14.72; Mar: 28.9; Apr: 36.86; May: 44.6; Jun: 59; Jul: 60.98; Aug: 64.22; Sep: 59.4; Oct: 37.94; Nov: 33.8; Dec: 27.9
MI | OAKLAND CO INTL | Jan: 24.1; Feb: 25.9; Mar: 34.7; Apr: 47.3; May: 58.1; Jun: 68.1; Jul: 72; Aug: 70.3; Sep: 62.5; Oct: 51.1; Nov: 39.2; Dec: 28.8; Jan: 20.5; Feb: 12.92; Mar: 30.6; Apr: 39.38; May: 45.9; Jun: 61.34; Jul: 61.7; Aug: 60.44; Sep: 55.2; Oct: 43.88; Nov: 37.2; Dec: 24.8
CA | OAKLAND METROPOLITAN ARPT | Jan: 49.9; Feb: 52.4; Mar: 55.1; Apr: 57.1; May: 59.8; Jun: 62.2; Jul: 63.6; Aug: 64.4; Sep: 64.6; Oct: 61.9; Nov: 55.4; Dec: 50.2; Jan: 41.5; Feb: 43.34; Mar: 48; Apr: 47.3; May: 51.3; Jun: 51.8; Jul: 54.14; Aug: 54.5; Sep: 54.5; Oct: 51.62; Nov: 46.4; Dec: 43.9
FL | OCALA MUNI (AWOS) | Jan: 56.7; Feb: 58.4; Mar: 63.1; Apr: 68.2; May: 75.2; Jun: 79.7; Jul: 81; Aug: 80.7; Sep: 79; Oct: 71.9; Nov: 63.7; Dec: 58.1; Jan: 47.7; Feb: 45.68; Mar: 59.5; Apr: 54.68; May: 61.2; Jun: 69.26; Jul: 71.24; Aug: 71.06; Sep: 68; Oct: 62.06; Nov: 50.7; Dec: 38.3
VA | OCEANA NAS | Jan: 42; Feb: 43.5; Mar: 49.8; Apr: 58.6; May: 66.4; Jun: 74.8; Jul: 79.3; Aug: 77.5; Sep: 72; Oct: 62.4; Nov: 52.4; Dec: 45.4; Jan: 29.1; Feb: 36.86; Mar: 43.3; Apr: 47.66; May: 56.7; Jun: 67.46; Jul: 69.62; Aug: 70.88; Sep: 64; Oct: 53.96; Nov: 43.5; Dec: 31.6
IA | OELWEN | Jan: 19.5; Feb: 22.7; Mar: 35.8; Apr: 49.1; May: 60.3; Jun: 69.7; Jul: 72.1; Aug: 70.4; Sep: 63.8; Oct: 49.8; Nov: 36.5; Dec: 24.7; Jan: 18.3; Feb: 24.08; Mar: 32.4; Apr: 39.2; May: 49.1; Jun: 60.26; Jul: 60.26; Aug: 63.5; Sep: 50.9; Oct: 44.6; Nov: 31.1; Dec: 19.4
UT | OGDEN HILL AFB | Jan: 28.5; Feb: 32.8; Mar: 42.2; Apr: 48.3; May: 58; Jun: 67.3; Jul: 76.7; Aug: 75.1; Sep: 65.1; Oct: 51.5; Nov: 38.7; Dec: 29.3; Jan: 23.7; Feb: 22.64; Mar: 26.1; Apr: 28.22; May: 32; Jun: 33.98; Jul: 34.7; Aug: 35.78; Sep: 33.4; Oct: 28.22; Nov: 28.4; Dec: 24.1
UT | OGDEN HINKLEY AIRPORT | Jan: 28; Feb: 32.7; Mar: 42.7; Apr: 49.2; May: 58.4; Jun: 68.2; Jul: 78.9; Aug: 75.7; Sep: 65.8; Oct: 52.3; Nov: 40.1; Dec: 29.8; Jan: 19.2; Feb: 23.18; Mar: 21.6; Apr: 31.28; May: 32; Jun: 38.48; Jul: 40.46; Aug: 49.28; Sep: 35.2; Oct: 36.32; Nov: 27.7; Dec: 24.1
OH | OHIO STATE UNIVERSI | Jan: 28.8; Feb: 31.2; Mar: 40.7; Apr: 52.8; May: 62.7; Jun: 70.9; Jul: 74.1; Aug: 72.9; Sep: 65.8; Oct: 53.8; Nov: 43.2; Dec: 33.1; Jan: 23; Feb: 23; Mar: 33.1; Apr: 40.64; May: 46; Jun: 60.26; Jul: 66.02; Aug: 69.44; Sep: 56.8; Oct: 44.96; Nov: 35.8; Dec: 26.2
OK | OKLAHOMA CITY TINKER AFB | Jan: 39.3; Feb: 43.8; Mar: 51.9; Apr: 60.5; May: 69; Jun: 77.5; Jul: 82.2; Aug: 81.7; Sep: 73.5; Oct: 62.3; Nov: 50.4; Dec: 41; Jan: 32.4; Feb: 30.92; Mar: 28.9; Apr: 37.04; May: 57.9; Jun: 66.56; Jul: 66.56; Aug: 64.58; Sep: 60.3; Oct: 44.24; Nov: 38.1; Dec: 30.6
OK | OKLAHOMA CITY WILL ROGERS WOR | Jan: 39.3; Feb: 43.5; Mar: 51.8; Apr: 60.3; May: 69.3; Jun: 77.8; Jul: 82.4; Aug: 81.8; Sep: 73.5; Oct: 62.1; Nov: 50.2; Dec: 40.7; Jan: 18.3; Feb: 32.36; Mar: 38.3; Apr: 48.56; May: 56.7; Jun: 64.76; Jul: 65.48; Aug: 64.22; Sep: 59.7; Oct: 49.28; Nov: 40.1; Dec: 28.2
OK | OKLAHOMA CITY/WILEY | Jan: 39.1; Feb: 43.2; Mar: 51.6; Apr: 60.3; May: 69.6; Jun: 78.3; Jul: 83.2; Aug: 82.5; Sep: 73.7; Oct: 62.1; Nov: 50.1; Dec: 40.4; Jan: 29.8; Feb: 28.76; Mar: 36; Apr: 36.68; May: 57.9; Jun: 63.14; Jul: 65.66; Aug: 62.6; Sep: 59.7; Oct: 43.7; Nov: 36.9; Dec: 30.2
KS | OLATHE-JOHNSON COUNTY INDUSTRIAL AP | Jan: 31; Feb: 34; Mar: 45; Apr: 55; May: 65; Jun: 75; Jul: 79; Aug: 78; Sep: 70; Oct: 57; Nov: 45; Dec: 34; Jan: 21.6; Feb: 24.62; Mar: 36.7; Apr: 47.12; May: 57; Jun: 65.3; Jul: 67.64; Aug: 64.04; Sep: 60.3; Oct: 44.6; Nov: 34.5; Dec: 19.2
KS | OLATHE/JOHNSON CO. | Jan: 30.6; Feb: 34.7; Mar: 45.1; Apr: 55.6; May: 65; Jun: 73.8; Jul: 79; Aug: 77.8; Sep: 68.8; Oct: 57.2; Nov: 44.9; Dec: 33.5; Jan: 22.6; Feb: 23.72; Mar: 31.1; Apr: 46.58; May: 52.5; Jun: 62.06; Jul: 66.2; Aug: 66.38; Sep: 64.2; Oct: 45.14; Nov: 36.9; Dec: 23.2
WA | OLYMPIA AIRPORT | Jan: 39.6; Feb: 40.8; Mar: 44.3; Apr: 48.2; May: 54; Jun: 58.8; Jul: 64.1; Aug: 64.2; Sep: 59.4; Oct: 50.5; Nov: 43.4; Dec: 38.8; Jan: 37.9; Feb: 34.34; Mar: 37.9; Apr: 40.82; May: 45; Jun: 49.46; Jul: 52.16; Aug: 51.44; Sep: 51.8; Oct: 47.12; Nov: 42.3; Dec: 36.9
NE | OMAHA EPPLEY AIRFIELD | Jan: 23.7; Feb: 28.7; Mar: 40; Apr: 51.9; May: 62.8; Jun: 72.6; Jul: 77; Aug: 75; Sep: 66.3; Oct: 53.9; Nov: 39.5; Dec: 27.5; Jan: 17.6; Feb: 16.16; Mar: 25.3; Apr: 42.62; May: 52.5; Jun: 64.76; Jul: 65.3; Aug: 68.9; Sep: 57.4; Oct: 42.44; Nov: 32.9; Dec: 20.5
NE | OMAHA WSFO | Jan: 27.3; Feb: 28.5; Mar: 41; Apr: 52.2; May: 63.8; Jun: 73; Jul: 75.7; Aug: 73.3; Sep: 65.6; Oct: 52.4; Nov: 37.5; Dec: 27.5; Jan: 11.3; Feb: 16.16; Mar: 27.9; Apr: 43.16; May: 43.9; Jun: 60.44; Jul: 65.3; Aug: 64.58; Sep: 52; Oct: 39.56; Nov: 22.6; Dec: 15.6
NE | ONEILL-BAKER FIELD | Jan: 24; Feb: 27; Mar: 37; Apr: 48; May: 58; Jun: 69; Jul: 75; Aug: 72; Sep: 64; Oct: 50; Nov: 37; Dec: 26; Jan: 7; Feb: 17.6; Mar: 25; Apr: 37.04; May: 45.7; Jun: 54.14; Jul: 61.34; Aug: 57.38; Sep: 48.6; Oct: 35.24; Nov: 20.3; Dec: 7.9
IA | ORANGE CITY | Jan: 19.7; Feb: 24.1; Mar: 35.7; Apr: 49.6; May: 60.7; Jun: 70.5; Jul: 74.7; Aug: 72.4; Sep: 64.3; Oct: 51; Nov: 36.5; Dec: 22.5; Jan: 12.6; Feb: 18.14; Mar: 37.2; Apr: 37.58; May: 44.4; Jun: 59; Jul: 64.94; Aug: 67.64; Sep: 52.3; Oct: 34.88; Nov: 25.3; Dec: 21.7
NE | ORD-SHARP FIELD | Jan: 25; Feb: 26; Mar: 39; Apr: 49; May: 59; Jun: 70; Jul: 75; Aug: 73; Sep: 64; Oct: 50; Nov: 37; Dec: 26; Jan: 16.7; Feb: 17.42; Mar: 26.2; Apr: 38.84; May: 50.5; Jun: 57.2; Jul: 61.7; Aug: 58.1; Sep: 46.9; Oct: 37.94; Nov: 24.8; Dec: 21.9
FL | ORLANDO EXECUTIVE AP | Jan: 61.4; Feb: 63.9; Mar: 67.4; Apr: 72.2; May: 77.9; Jun: 81.5; Jul: 83.1; Aug: 83.1; Sep: 81.3; Oct: 75.9; Nov: 68.3; Dec: 63.4; Jan: 42.8; Feb: 52.34; Mar: 58.5; Apr: 62.96; May: 66.9; Jun: 70.52; Jul: 72.5; Aug: 72.68; Sep: 70.9; Oct: 69.08; Nov: 55; Dec: 48.9
FL | ORLANDO INTL ARPT | Jan: 61; Feb: 63.5; Mar: 67.1; Apr: 71.8; May: 77.4; Jun: 81; Jul: 82.5; Aug: 82.6; Sep: 80.8; Oct: 75.2; Nov: 67.9; Dec: 63.1; Jan: 51.1; Feb: 50.9; Mar: 53.4; Apr: 59.36; May: 66; Jun: 72.5; Jul: 73.58; Aug: 74.12; Sep: 71.4; Oct: 66.38; Nov: 61.2; Dec: 53.8
FL | ORLANDO SANFORD AIRPORT | Jan: 60; Feb: 62.4; Mar: 66.2; Apr: 71.5; May: 77.2; Jun: 81.2; Jul: 82.8; Aug: 82.8; Sep: 80.6; Oct: 74.8; Nov: 67.4; Dec: 62.2; Jan: 51.1; Feb: 52.7; Mar: 47.7; Apr: 55.4; May: 63.1; Jun: 68.72; Jul: 73.04; Aug: 72.68; Sep: 69.1; Oct: 64.94; Nov: 54.9; Dec: 50
MN | ORR | Jan: 6.5; Feb: 11.7; Mar: 24.3; Apr: 38.7; May: 51.2; Jun: 60.7; Jul: 65.5; Aug: 63.6; Sep: 55.3; Oct: 42.7; Nov: 26.8; Dec: 12.7; Jan: -8.5; Feb: 9.86; Mar: 1.8; Apr: 23; May: 38.1; Jun: 52.88; Jul: 53.6; Aug: 54.68; Sep: 50.7; Oct: 29.48; Nov: 18.7; Dec: 3
MI | OSCODA WURTSMITH AFB | Jan: 21.9; Feb: 23.1; Mar: 31; Apr: 42.4; May: 53.5; Jun: 63.8; Jul: 68.4; Aug: 67.2; Sep: 59.8; Oct: 48.4; Nov: 37.7; Dec: 26.9; Jan: 22.6; Feb: 14; Mar: 26.1; Apr: 35.42; May: 39.4; Jun: 54.14; Jul: 60.62; Aug: 55.76; Sep: 51.4; Oct: 41.54; Nov: 30; Dec: 18.5
MA | OTIS ANGB | Jan: 30.6; Feb: 31.8; Mar: 37.3; Apr: 45.9; May: 55.3; Jun: 64.8; Jul: 70.4; Aug: 69.8; Sep: 62.8; Oct: 52.9; Nov: 44.7; Dec: 35.8; Jan: 28; Feb: 25.88; Mar: 30.6; Apr: 31.64; May: 43.3; Jun: 55.94; Jul: 62.24; Aug: 68.18; Sep: 51.6; Oct: 46.4; Nov: 29.8; Dec: 27.9
ON | OTTAWA | Jan: 14.5; Feb: 17.6; Mar: 28.3; Apr: 43.2; May: 56.3; Jun: 65.8; Jul: 69.7; Aug: 68; Sep: 59.4; Oct: 47.2; Nov: 35.2; Dec: 22; Jan: 7; Feb: 8.6; Mar: 17.1; Apr: 29.12; May: 41.9; Jun: 54.32; Jul: 58.46; Aug: 57.74; Sep: 51.6; Oct: 39.38; Nov: 29.5; Dec: 16
IA | OTTUMWA INDUSTRIAL AP | Jan: 23.4; Feb: 27.9; Mar: 39.5; Apr: 51.3; May: 61.9; Jun: 71.4; Jul: 75.1; Aug: 73.3; Sep: 64.8; Oct: 53.2; Nov: 39.8; Dec: 27.7; Jan: 17.2; Feb: 15.8; Mar: 30.6; Apr: 42.44; May: 48; Jun: 62.96; Jul: 66.56; Aug: 59.9; Sep: 53.4; Oct: 41.54; Nov: 33.1; Dec: 7
MN | OWATONNA (AWOS) | Jan: 14.9; Feb: 18.8; Mar: 31.8; Apr: 46.3; May: 58.1; Jun: 68.1; Jul: 71.8; Aug: 69.3; Sep: 61.5; Oct: 49; Nov: 34.6; Dec: 21; Jan: 11.3; Feb: 13.1; Mar: 28.6; Apr: 32.9; May: 43.2; Jun: 58.82; Jul: 60.98; Aug: 62.42; Sep: 54; Oct: 35.6; Nov: 26.2; Dec: 19.2
CT | OXFORD (AWOS) | Jan: 26.3; Feb: 28.5; Mar: 35.9; Apr: 46.9; May: 55.9; Jun: 65.9; Jul: 70.2; Aug: 68.8; Sep: 61.6; Oct: 50.3; Nov: 41.3; Dec: 31.4; Jan: 14.7; Feb: 22.1; Mar: 20.5; Apr: 35.6; May: 45.1; Jun: 57.38; Jul: 61.88; Aug: 61.16; Sep: 57.9; Oct: 45.14; Nov: 30.9; Dec: 22.3
CA | OXNARD AIRPORT | Jan: 55.8; Feb: 55; Mar: 56.1; Apr: 57.1; May: 60.2; Jun: 62.9; Jul: 65.7; Aug: 65.5; Sep: 64.9; Oct: 62.5; Nov: 58.8; Dec: 55.1; Jan: 41.2; Feb: 40.82; Mar: 50.4; Apr: 48.74; May: 55.2; Jun: 52.34; Jul: 57.74; Aug: 56.12; Sep: 57; Oct: 54.5; Nov: 42.8; Dec: 40.8
KY | PADUCAH BARKLEY REGIONAL AP | Jan: 35.9; Feb: 39.9; Mar: 48.7; Apr: 58.6; May: 67.6; Jun: 75.9; Jul: 78.8; Aug: 77.6; Sep: 70; Oct: 59; Nov: 47.8; Dec: 38.7; Jan: 30.4; Feb: 26.1; Mar: 38.1; Apr: 47.3; May: 56.3; Jun: 66.6; Jul: 69.8; Aug: 67.1; Sep: 56.3; Oct: 49.6; Nov: 41; Dec: 36.1
AZ | PAGE MUNI (AMOS) | Jan: 37.1; Feb: 42.3; Mar: 50.8; Apr: 58.1; May: 68.7; Jun: 78.6; Jul: 84.4; Aug: 81; Sep: 73.7; Oct: 60.2; Nov: 46.3; Dec: 36.3; Jan: 20.7; Feb: 24.62; Mar: 28.2; Apr: 22.82; May: 22.1; Jun: 32; Jul: 38.48; Aug: 50.36; Sep: 39.7; Oct: 35.6; Nov: 30.4; Dec: 19
TX | PALACIOS MUNICIPAL AP | Jan: 55.3; Feb: 58.4; Mar: 63.8; Apr: 70.4; May: 77.2; Jun: 82.8; Jul: 84.2; Aug: 84.4; Sep: 80.3; Oct: 72.8; Nov: 63.6; Dec: 56.8; Jan: 45.7; Feb: 49.82; Mar: 48.6; Apr: 62.24; May: 72; Jun: 75.2; Jul: 75.38; Aug: 74.84; Sep: 68.4; Oct: 61.7; Nov: 54.9; Dec: 48
CA | PALM SPRINGS INTL | Jan: 59.1; Feb: 60.4; Mar: 66.7; Apr: 71.3; May: 80; Jun: 87.3; Jul: 93.6; Aug: 92.6; Sep: 87.7; Oct: 76.7; Nov: 65.9; Dec: 57.3; Jan: 30; Feb: 35.96; Mar: 41.7; Apr: 44.78; May: 49.1; Jun: 50.9; Jul: 56.12; Aug: 55.94; Sep: 48.7; Oct: 44.96; Nov: 32.4; Dec: 23.2
CA | PALM SPRINGS THERMAL AP | Jan: 55.2; Feb: 58.5; Mar: 65.2; Apr: 71.1; May: 79.2; Jun: 86.1; Jul: 91.6; Aug: 90.6; Sep: 85.3; Oct: 73.8; Nov: 61.8; Dec: 53.5; Jan: 36.7; Feb: 42.26; Mar: 44.4; Apr: 37.4; May: 45.7; Jun: 52.88; Jul: 57.92; Aug: 60.26; Sep: 58.3; Oct: 42.62; Nov: 36.9; Dec: 32
CA | PALMDALE AIRPORT | Jan: 45.8; Feb: 48.1; Mar: 53.9; Apr: 58.8; May: 67.9; Jun: 75.2; Jul: 82.3; Aug: 81.6; Sep: 75.1; Oct: 63.6; Nov: 52.4; Dec: 44.8; Jan: 25.2; Feb: 25.52; Mar: 25.3; Apr: 32.18; May: 38.8; Jun: 42.26; Jul: 46.94; Aug: 42.26; Sep: 43.2; Oct: 37.22; Nov: 30.2; Dec: 19.9
AK | PALMER MUNICIPAL | Jan: 16; Feb: 21.4; Mar: 25.5; Apr: 37.8; May: 48.7; Jun: 55.7; Jul: 58.5; Aug: 56; Sep: 48.4; Oct: 35.7; Nov: 21.9; Dec: 17.7; Jan: 22.6; Feb: 25.16; Mar: 19.9; Apr: 26.96; May: 34.7; Jun: 36.86; Jul: 47.3; Aug: 48.38; Sep: 34.3; Oct: 26.42; Nov: 29.8; Dec: 19.2
FL | PANAMA CITY BAY CO | Jan: 54; Feb: 56; Mar: 62.1; Apr: 68.2; May: 75.7; Jun: 81.1; Jul: 82.8; Aug: 82.5; Sep: 79.5; Oct: 71.8; Nov: 62.6; Dec: 55.7; Jan: 48.2; Feb: 49.64; Mar: 48.9; Apr: 54.5; May: 70.3; Jun: 70.88; Jul: 74.3; Aug: 74.66; Sep: 72.5; Oct: 57.02; Nov: 57.2; Dec: 44.2
MN | PARK RAPIDS MUNICIPAL AP | Jan: 7.7; Feb: 13.3; Mar: 25.2; Apr: 41.2; May: 53.6; Jun: 63.3; Jul: 68.8; Aug: 66.7; Sep: 57.5; Oct: 43.8; Nov: 28; Dec: 13.9; Jan: 5.2; Feb: 8.96; Mar: 14.7; Apr: 30.74; May: 43.7; Jun: 54.14; Jul: 57.74; Aug: 54.14; Sep: 51.3; Oct: 32.72; Nov: 23.4; Dec: 9.5
WV | PARKERSBURG WOOD COUNTY AP | Jan: 32.7; Feb: 35.2; Mar: 43.6; Apr: 54.7; May: 62.9; Jun: 70.7; Jul: 74.3; Aug: 73.1; Sep: 66.1; Oct: 54.9; Nov: 44.7; Dec: 36.2; Jan: 16.9; Feb: 23; Mar: 32.2; Apr: 43.34; May: 52.3; Jun: 64.22; Jul: 66.74; Aug: 64.94; Sep: 58.1; Oct: 45.5; Nov: 36; Dec: 25
WA | PASCO | Jan: 35.2; Feb: 39.1; Mar: 46.3; Apr: 53; May: 61.1; Jun: 67.7; Jul: 75.2; Aug: 73.6; Sep: 64.7; Oct: 52.3; Nov: 41.2; Dec: 33.8; Jan: 31.1; Feb: 28.94; Mar: 36.7; Apr: 42.08; May: 42.4; Jun: 50.54; Jul: 51.26; Aug: 51.44; Sep: 45.1; Oct: 38.84; Nov: 37.6; Dec: 30.9
CA | PASO ROBLES MUNICIPAL ARPT | Jan: 48.4; Feb: 50.5; Mar: 54; Apr: 57.4; May: 63.9; Jun: 69.2; Jul: 73.7; Aug: 73.8; Sep: 70.3; Oct: 62.5; Nov: 53.3; Dec: 47.2; Jan: 38.5; Feb: 39.2; Mar: 46; Apr: 39.92; May: 43; Jun: 46.22; Jul: 48.74; Aug: 48.02; Sep: 48.2; Oct: 41.18; Nov: 41; Dec: 36.9
LA | PATTERSON MEMORIAL | Jan: 54.1; Feb: 56.6; Mar: 62.3; Apr: 68.3; May: 75.2; Jun: 80.3; Jul: 81.9; Aug: 82.2; Sep: 78.9; Oct: 69.7; Nov: 60.4; Dec: 55; Jan: 42.4; Feb: 48.38; Mar: 46.4; Apr: 55.94; May: 65.1; Jun: 70.88; Jul: 75.2; Aug: 72.14; Sep: 68.7; Oct: 42.8; Nov: 49.1; Dec: 37.4
MD | PATUXENT RIVER NAS | Jan: 37.1; Feb: 39.1; Mar: 45.9; Apr: 56.1; May: 65.7; Jun: 74.2; Jul: 78.6; Aug: 76.7; Sep: 70.2; Oct: 59.8; Nov: 49.4; Dec: 41.5; Jan: 34.7; Feb: 33.98; Mar: 40.6; Apr: 47.12; May: 60.1; Jun: 63.68; Jul: 69.08; Aug: 70.88; Sep: 63; Oct: 50.18; Nov: 42.3; Dec: 30.7
RI | PAWTUCKET (AWOS) | Jan: 27.8; Feb: 29.4; Mar: 36.9; Apr: 47.7; May: 56.4; Jun: 65.4; Jul: 70.8; Aug: 69.2; Sep: 61.9; Oct: 51.4; Nov: 41.9; Dec: 32.8; Jan: 13.8; Feb: 16.88; Mar: 20.1; Apr: 35.6; May: 45.3; Jun: 54.5; Jul: 58.64; Aug: 59.9; Sep: 56.8; Oct: 41.18; Nov: 24.4; Dec: 23.5
NH | PEASE INTL TRADEPOR | Jan: 25.3; Feb: 28.3; Mar: 35.7; Apr: 46.6; May: 56; Jun: 65.8; Jul: 71.4; Aug: 70.3; Sep: 62.5; Oct: 51.5; Nov: 41.5; Dec: 31.8; Jan: 23; Feb: 17.06; Mar: 25.3; Apr: 29.66; May: 41.4; Jun: 53.78; Jul: 58.46; Aug: 58.64; Sep: 52.3; Oct: 40.1; Nov: 30.2; Dec: 24.4
MI | PELLSTON EMMET COUNTY AP | Jan: 18.6; Feb: 19; Mar: 27.7; Apr: 40.7; May: 52.8; Jun: 62.6; Jul: 66.3; Aug: 65; Sep: 57.2; Oct: 46.2; Nov: 35.7; Dec: 25.3; Jan: 18.5; Feb: 18.68; Mar: 27.9; Apr: 33.98; May: 43.2; Jun: 53.06; Jul: 59.9; Aug: 57.56; Sep: 52.9; Oct: 39.02; Nov: 29.8; Dec: 19.2
OR | PENDLETON E OR REGIONAL AP | Jan: 35.4; Feb: 38.5; Mar: 45; Apr: 50.4; May: 57.8; Jun: 64.4; Jul: 73.3; Aug: 72.1; Sep: 64.5; Oct: 51.9; Nov: 41.2; Dec: 34.3; Jan: 26.1; Feb: 31.46; Mar: 33.6; Apr: 37.4; May: 39.6; Jun: 43.88; Jul: 43.7; Aug: 41.36; Sep: 40.1; Oct: 36.14; Nov: 33.4; Dec: 28.4
FL | PENSACOLA FOREST SHERMAN NAS | Jan: 52.3; Feb: 55.4; Mar: 60.4; Apr: 66.7; May: 74.4; Jun: 80.4; Jul: 82.1; Aug: 81.9; Sep: 78.7; Oct: 69.6; Nov: 60; Dec: 55.1; Jan: 41.7; Feb: 42.26; Mar: 52; Apr: 62.06; May: 68.2; Jun: 70.88; Jul: 74.66; Aug: 73.76; Sep: 69.3; Oct: 60.08; Nov: 49.1; Dec: 43
FL | PENSACOLA REGIONAL AP | Jan: 52.6; Feb: 55.6; Mar: 61.3; Apr: 67.4; May: 75.2; Jun: 81; Jul: 82.4; Aug: 82.2; Sep: 78.9; Oct: 70; Nov: 60.4; Dec: 54.4; Jan: 43; Feb: 48.38; Mar: 53.2; Apr: 62.42; May: 70.7; Jun: 70.34; Jul: 74.12; Aug: 73.22; Sep: 64.8; Oct: 63.14; Nov: 55.9; Dec: 50.4
BC | PENTICTON AP | Jan: 30.8; Feb: 33.6; Mar: 40.6; Apr: 48.1; May: 56.9; Jun: 63.3; Jul: 70.5; Aug: 69.1; Sep: 60; Oct: 48.1; Nov: 37.7; Dec: 30.9; Jan: 24.6; Feb: 25.52; Mar: 27.9; Apr: 31.82; May: 38.8; Jun: 45.32; Jul: 48.2; Aug: 48.02; Sep: 43.5; Oct: 36.86; Nov: 30.6; Dec: 24.8
IL | PEORIA GREATER PEORIA AP | Jan: 25.5; Feb: 29.9; Mar: 41; Apr: 52.5; May: 62.6; Jun: 71.9; Jul: 75.5; Aug: 74; Sep: 66.1; Oct: 54.2; Nov: 41.6; Dec: 30; Jan: 14.7; Feb: 17.78; Mar: 28.8; Apr: 41.9; May: 48.6; Jun: 57.92; Jul: 64.04; Aug: 64.22; Sep: 55; Oct: 41.9; Nov: 30.4; Dec: 22.6
ON | PETERBOROUGH AP | Jan: 18.4; Feb: 20.6; Mar: 29.6; Apr: 42.9; May: 54.5; Jun: 63.8; Jul: 67.4; Aug: 65.7; Sep: 58.1; Oct: 46.9; Nov: 35.9; Dec: 25.2; Jan: 12; Feb: 12.38; Mar: 19.8; Apr: 31.46; May: 43.2; Jun: 55.22; Jul: 59; Aug: 58.64; Sep: 52.3; Oct: 40.1; Nov: 31.3; Dec: 19.2
AK | PETERSBURG | Jan: 30.5; Feb: 33; Mar: 34.4; Apr: 40.6; May: 47.4; Jun: 53.3; Jul: 55.9; Aug: 55.3; Sep: 50.5; Oct: 43.4; Nov: 35.8; Dec: 32.2; Jan: 23.5; Feb: 28.4; Mar: 26.1; Apr: 32.54; May: 35.4; Jun: 46.76; Jul: 50.36; Aug: 49.46; Sep: 42.4; Oct: 36.32; Nov: 30.2; Dec: 25.7
PA | PHILADELPHIA INTERNATIONAL AP | Jan: 34.3; Feb: 36.2; Mar: 44.1; Apr: 54.8; May: 64.4; Jun: 73.7; Jul: 78.7; Aug: 76.9; Sep: 69.7; Oct: 58.4; Nov: 47.9; Dec: 38.8; Jan: 19; Feb: 20.12; Mar: 31.1; Apr: 37.94; May: 50.2; Jun: 60.8; Jul: 65.66; Aug: 63.5; Sep: 58.3; Oct: 42.8; Nov: 36.1; Dec: 24.8
PA | PHILADELPHIA NE PHILADELPHIA | Jan: 33.6; Feb: 35.5; Mar: 42.9; Apr: 53.6; May: 63.1; Jun: 72.3; Jul: 77.4; Aug: 75.5; Sep: 68.2; Oct: 56.8; Nov: 46.7; Dec: 38; Jan: 17.8; Feb: 18.68; Mar: 33.1; Apr: 44.06; May: 48.4; Jun: 58.46; Jul: 64.76; Aug: 65.66; Sep: 57.6; Oct: 45.5; Nov: 35.4; Dec: 29.5
WI | PHILLIPS/PRICE CO. | Jan: 12.6; Feb: 16.5; Mar: 28; Apr: 41.4; May: 53.9; Jun: 63.5; Jul: 67.5; Aug: 65.9; Sep: 57.5; Oct: 45.4; Nov: 31.3; Dec: 18.6; Jan: 8.4; Feb: 3.74; Mar: 17.8; Apr: 35.6; May: 37; Jun: 51.26; Jul: 58.46; Aug: 58.46; Sep: 53.8; Oct: 35.24; Nov: 28.4; Dec: 17.4
AZ | PHOENIX SKY HARBOR INTL AP | Jan: 56.7; Feb: 59.5; Mar: 65.6; Apr: 72.6; May: 81.9; Jun: 90.9; Jul: 94.8; Aug: 93.6; Sep: 88.8; Oct: 76.9; Nov: 64.6; Dec: 55.6; Jan: 28; Feb: 39.38; Mar: 36.5; Apr: 29.12; May: 36.1; Jun: 42.62; Jul: 56.48; Aug: 56.3; Sep: 48; Oct: 43.52; Nov: 35.4; Dec: 32.9
SD | PIERRE MUNICIPAL AP | Jan: 20.1; Feb: 24.5; Mar: 34.7; Apr: 46.7; May: 57.7; Jun: 67.8; Jul: 75.2; Aug: 73.6; Sep: 64.2; Oct: 49.4; Nov: 34.3; Dec: 23; Jan: 9.3; Feb: 14.9; Mar: 26.1; Apr: 33.8; May: 43.7; Jun: 57.02; Jul: 57.38; Aug: 58.28; Sep: 46; Oct: 33.08; Nov: 25.9; Dec: 9.5
AR | PINE BLUFF FAA AP | Jan: 43.5; Feb: 47.3; Mar: 54.8; Apr: 63.8; May: 72; Jun: 79.7; Jul: 82.3; Aug: 81.5; Sep: 74.8; Oct: 64; Nov: 53; Dec: 45.3; Jan: 31.3; Feb: 38.84; Mar: 35.4; Apr: 55.22; May: 64.4; Jun: 68.36; Jul: 72.32; Aug: 70.16; Sep: 67.8; Oct: 55.94; Nov: 40.5; Dec: 27
MN | PIPESTONE (AWOS) | Jan: 15.3; Feb: 19.4; Mar: 31.2; Apr: 44.9; May: 57.1; Jun: 67.3; Jul: 71.9; Aug: 69.3; Sep: 61.2; Oct: 48.6; Nov: 32.9; Dec: 20.1; Jan: 6.6; Feb: 7.16; Mar: 26.8; Apr: 31.1; May: 40.3; Jun: 56.48; Jul: 65.84; Aug: 61.52; Sep: 53.4; Oct: 32.72; Nov: 25.5; Dec: 6.8
NC | PITT GREENVILLE ARP | Jan: 43.2; Feb: 45.6; Mar: 52.4; Apr: 61.5; May: 69.5; Jun: 77.3; Jul: 80.3; Aug: 79; Sep: 72.8; Oct: 62.4; Nov: 52.2; Dec: 45.5; Jan: 29.1; Feb: 27.68; Mar: 30.2; Apr: 41; May: 53.2; Jun: 63.32; Jul: 67.82; Aug: 64.58; Sep: 57.7; Oct: 51.62; Nov: 45; Dec: 42.1
BC | PITT MEADOWS | Jan: 38.2; Feb: 40.3; Mar: 43.8; Apr: 48.8; May: 55; Jun: 60.1; Jul: 65.3; Aug: 65.1; Sep: 59.9; Oct: 50.5; Nov: 42.5; Dec: 37.4; Jan: 31.5; Feb: 33.26; Mar: 37.2; Apr: 40.1; May: 46.4; Jun: 51.44; Jul: 55.58; Aug: 55.94; Sep: 52.3; Oct: 46.04; Nov: 39.4; Dec: 31.3
PA | PITTSBURGH ALLEGHENY CO AP | Jan: 30; Feb: 32.1; Mar: 40.7; Apr: 52.5; May: 61.6; Jun: 69.8; Jul: 73.4; Aug: 72.2; Sep: 64.9; Oct: 54.1; Nov: 43.6; Dec: 34.2; Jan: 23.7; Feb: 19.04; Mar: 32.9; Apr: 40.46; May: 47.8; Jun: 58.28; Jul: 63.32; Aug: 60.44; Sep: 55.6; Oct: 44.24; Nov: 35.2; Dec: 27.1
PA | PITTSBURGH INTERNATIONAL AP | Jan: 29.4; Feb: 31.5; Mar: 40.2; Apr: 51.9; May: 60.9; Jun: 69.5; Jul: 73; Aug: 71.8; Sep: 64.5; Oct: 53.4; Nov: 42.9; Dec: 33.7; Jan: 17.6; Feb: 15.44; Mar: 25.9; Apr: 34.34; May: 46.8; Jun: 58.46; Jul: 61.16; Aug: 60.44; Sep: 54.1; Oct: 38.66; Nov: 34.9; Dec: 22.1
MA | PLYMOUTH MUNICIPAL | Jan: 28.8; Feb: 30.6; Mar: 36.8; Apr: 46.3; May: 56.1; Jun: 65.5; Jul: 71.8; Aug: 70.2; Sep: 63.1; Oct: 52.3; Nov: 43.1; Dec: 34.2; Jan: 22.1; Feb: 18.86; Mar: 31.5; Apr: 38.12; May: 47.7; Jun: 56.3; Jul: 62.24; Aug: 61.7; Sep: 57.9; Oct: 47.66; Nov: 36.3; Dec: 30.7
ID | POCATELLO REGIONAL AP | Jan: 25.6; Feb: 29.5; Mar: 38.9; Apr: 45.7; May: 54.3; Jun: 62.1; Jul: 70.9; Aug: 69.5; Sep: 60.2; Oct: 47.5; Nov: 35; Dec: 25.8; Jan: 16.7; Feb: 20.84; Mar: 23.4; Apr: 28.94; May: 33.3; Jun: 41.54; Jul: 42.98; Aug: 39.2; Sep: 34.9; Oct: 27.32; Nov: 29.5; Dec: 19.9
AK | POINT HOPE (AWOS) | Jan: -4.2; Feb: -3.7; Mar: -0.3; Apr: 10.1; May: 27.8; Jun: 37.8; Jul: 46; Aug: 46.4; Sep: 40.3; Oct: 26.4; Nov: 14.8; Dec: 3.3; Jan: 3.2; Feb: -5.08; Mar: 1.9; Apr: 4.82; May: 27.1; Jun: 30.38; Jul: 30.38; Aug: 39.74; Sep: 30.6; Oct: 26.42; Nov: 14.2; Dec: 8.8
CA | POINT MUGU NF | Jan: 55.6; Feb: 55; Mar: 55.9; Apr: 57; May: 59.3; Jun: 62.1; Jul: 65.1; Aug: 65.8; Sep: 65.3; Oct: 63; Nov: 59.4; Dec: 54.9; Jan: 42.6; Feb: 43.7; Mar: 48.6; Apr: 49.64; May: 55; Jun: 53.78; Jul: 58.28; Aug: 58.46; Sep: 57.4; Oct: 56.84; Nov: 47.3; Dec: 40.3
QC | POINT-AU-PERE | Jan: 14.1; Feb: 16.6; Mar: 24.8; Apr: 36.6; May: 46.7; Jun: 54.9; Jul: 60.2; Aug: 58.9; Sep: 52.8; Oct: 43.2; Nov: 33.9; Dec: 22.5; Jan: 4.8; Feb: 7.88; Mar: 16.5; Apr: 27.32; May: 37.4; Jun: 47.3; Jul: 53.96; Aug: 52.88; Sep: 46.4; Oct: 36.68; Nov: 27.3; Dec: 14
OK | PONCA CITY MUNICIPAL AP [SGP - ARM] | Jan: 36.7; Feb: 41; Mar: 49.9; Apr: 59.3; May: 68.8; Jun: 78.1; Jul: 82.9; Aug: 82; Sep: 72.9; Oct: 61.3; Nov: 48.8; Dec: 38.5; Jan: 21.9; Feb: 25.52; Mar: 37.4; Apr: 46.94; May: 55.8; Jun: 63.86; Jul: 68.36; Aug: 63.68; Sep: 64.2; Oct: 46.22; Nov: 41.7; Dec: 28.8
MO | POPLAR BLUFF(AMOS) | Jan: 36.1; Feb: 40.2; Mar: 48.8; Apr: 59.6; May: 68; Jun: 76.3; Jul: 79.3; Aug: 77.9; Sep: 70.2; Oct: 59.4; Nov: 48.1; Dec: 38.6; Jan: 26.2; Feb: 28.76; Mar: 41; Apr: 52.16; May: 55.9; Jun: 67.28; Jul: 71.96; Aug: 68.54; Sep: 59; Oct: 53.78; Nov: 35.4; Dec: 27.1
TX | PORT ARTHUR JEFFERSON COUNTY | Jan: 53.5; Feb: 56.8; Mar: 62.5; Apr: 68.9; May: 76.2; Jun: 81.7; Jul: 83; Aug: 83.3; Sep: 79.4; Oct: 70.9; Nov: 61.3; Dec: 55; Jan: 42.1; Feb: 45.14; Mar: 55.9; Apr: 61.34; May: 68.5; Jun: 73.04; Jul: 74.48; Aug: 73.94; Sep: 70.5; Oct: 59.36; Nov: 56.7; Dec: 45.9
AK | PORT HEIDEN | Jan: 24; Feb: 24.8; Mar: 26.3; Apr: 33.4; May: 40.2; Jun: 46.6; Jul: 51; Aug: 52.5; Sep: 47.5; Oct: 38.4; Nov: 31.9; Dec: 27.6; Jan: 28.8; Feb: 17.42; Mar: 20.8; Apr: 25.7; May: 27.7; Jun: 30.74; Jul: 35.06; Aug: 36.5; Sep: 29.7; Oct: 28.04; Nov: 28.4; Dec: 19
ON | PORT WELLER | Jan: 27.5; Feb: 28.3; Mar: 34.8; Apr: 44.2; May: 54.3; Jun: 65.3; Jul: 71.2; Aug: 71.1; Sep: 64.7; Oct: 53.1; Nov: 42.3; Dec: 33.3; Jan: 19.8; Feb: 19.76; Mar: 26.2; Apr: 35.6; May: 46.4; Jun: 57.2; Jul: 60.98; Aug: 60.98; Sep: 55.4; Oct: 44.6; Nov: 35.6; Dec: 24.3
CA | PORTERVILLE (AWOS) | Jan: 47.2; Feb: 50.6; Mar: 55.2; Apr: 59.5; May: 67.6; Jun: 74.5; Jul: 80.2; Aug: 78.9; Sep: 74.3; Oct: 64.2; Nov: 53.3; Dec: 46.7; Jan: 32; Feb: 37.4; Mar: 41; Apr: 37.4; May: 42.3; Jun: 37.94; Jul: 47.66; Aug: 51.44; Sep: 49.5; Oct: 43.88; Nov: 41.2; Dec: 41.5
OR | PORTLAND INTERNATIONAL AP | Jan: 41.5; Feb: 43.8; Mar: 47.9; Apr: 52.3; May: 58.4; Jun: 63.2; Jul: 69.5; Aug: 69.9; Sep: 65.3; Oct: 55.3; Nov: 46.7; Dec: 40.9; Jan: 36.9; Feb: 37.22; Mar: 38.3; Apr: 44.06; May: 46.9; Jun: 51.8; Jul: 54.5; Aug: 55.76; Sep: 52.9; Oct: 45.68; Nov: 41.9; Dec: 35.8
ME | PORTLAND INTL JETPORT | Jan: 23.5; Feb: 25.7; Mar: 33.8; Apr: 44.3; May: 54; Jun: 63.7; Jul: 69.5; Aug: 68.4; Sep: 60.6; Oct: 49.9; Nov: 39.9; Dec: 30.1; Jan: 9.5; Feb: 12.38; Mar: 20.5; Apr: 34.7; May: 44.6; Jun: 52.7; Jul: 60.08; Aug: 58.46; Sep: 48.9; Oct: 37.22; Nov: 26.1; Dec: 14.4
OR | PORTLAND/HILLSBORO | Jan: 40.7; Feb: 42.7; Mar: 46.5; Apr: 50.2; May: 56.3; Jun: 60.9; Jul: 67.2; Aug: 67; Sep: 62.4; Oct: 52.7; Nov: 44.6; Dec: 39.6; Jan: 37.6; Feb: 38.12; Mar: 41.2; Apr: 43.88; May: 43.7; Jun: 49.64; Jul: 52.52; Aug: 55.04; Sep: 46.6; Oct: 44.42; Nov: 40.1; Dec: 37
OR | PORTLAND/TROUTDALE | Jan: 41; Feb: 43.4; Mar: 47.3; Apr: 51.4; May: 57.2; Jun: 62.5; Jul: 68.8; Aug: 68.9; Sep: 64.1; Oct: 54.8; Nov: 46.7; Dec: 40.7; Jan: 34.2; Feb: 34.88; Mar: 35.2; Apr: 41; May: 44.1; Jun: 51.62; Jul: 54.68; Aug: 52.34; Sep: 46; Oct: 45.32; Nov: 41.5; Dec: 36
NY | POUGHKEEPSIE DUTCHESS CO AP | Jan: 27.2; Feb: 29.1; Mar: 37.7; Apr: 49.2; May: 59.1; Jun: 68.3; Jul: 73.4; Aug: 71.6; Sep: 63.7; Oct: 52.1; Nov: 41.7; Dec: 32.2; Jan: 15.3; Feb: 19.94; Mar: 30; Apr: 38.66; May: 49.5; Jun: 59.54; Jul: 62.24; Aug: 62.24; Sep: 57; Oct: 42.08; Nov: 37; Dec: 22.1
AZ | PRESCOTT LOVE FIELD | Jan: 39.2; Feb: 41.8; Mar: 47.3; Apr: 53.2; May: 62.2; Jun: 71.3; Jul: 76.2; Aug: 74.2; Sep: 68.6; Oct: 57.4; Nov: 46.6; Dec: 38.3; Jan: 24.8; Feb: 23.54; Mar: 25; Apr: 24.44; May: 27; Jun: 33.8; Jul: 48.74; Aug: 53.42; Sep: 38.3; Oct: 35.78; Nov: 25; Dec: 17.4
ME | PRESQUE ISLE MUNICIP | Jan: 11.6; Feb: 13.7; Mar: 25; Apr: 38.2; May: 50.9; Jun: 60.6; Jul: 65.6; Aug: 63.7; Sep: 55.7; Oct: 43.5; Nov: 32.5; Dec: 20.3; Jan: 3.4; Feb: 8.06; Mar: 20.7; Apr: 27.5; May: 34.3; Jun: 45.14; Jul: 51.62; Aug: 51.44; Sep: 40.1; Oct: 33.8; Nov: 28.8; Dec: 17.8
SK | PRINCE ALBERT AP | Jan: 1.1; Feb: 6.8; Mar: 19.2; Apr: 37.2; May: 49.9; Jun: 59.2; Jul: 64.1; Aug: 62.3; Sep: 52.3; Oct: 37.9; Nov: 19.8; Dec: 5.2; Jan: -2.7; Feb: -0.94; Mar: 9.9; Apr: 24.8; May: 32.9; Jun: 46.22; Jul: 54.32; Aug: 51.26; Sep: 42.4; Oct: 28.94; Nov: 17.2; Dec: 0.3
BC | PRINCE GEORGE | Jan: 17.7; Feb: 23.5; Mar: 30.7; Apr: 40.6; May: 49.8; Jun: 56.6; Jul: 60.4; Aug: 59; Sep: 50.9; Oct: 39.7; Nov: 27.8; Dec: 19.7; Jan: 14.4; Feb: 15.8; Mar: 20.3; Apr: 25.7; May: 33.6; Jun: 42.8; Jul: 48.02; Aug: 46.76; Sep: 41.5; Oct: 32.36; Nov: 24.6; Dec: 14.9
RI | PROVIDENCE T F GREEN STATE AR | Jan: 30.3; Feb: 31.9; Mar: 39; Apr: 49.3; May: 58.6; Jun: 68.1; Jul: 74; Aug: 72.5; Sep: 65.1; Oct: 54.4; Nov: 44.7; Dec: 35.6; Jan: 18.9; Feb: 18.14; Mar: 28.4; Apr: 31.82; May: 46.2; Jun: 54.68; Jul: 62.24; Aug: 61.88; Sep: 56.5; Oct: 43.34; Nov: 34.5; Dec: 19.6
MA | PROVINCETOWN (AWOS) | Jan: 32.4; Feb: 32.3; Mar: 37.8; Apr: 45.7; May: 54.9; Jun: 64.3; Jul: 70.8; Aug: 69.4; Sep: 63.2; Oct: 54.1; Nov: 45.2; Dec: 37.7; Jan: 21.2; Feb: 25.16; Mar: 22.8; Apr: 35.24; May: 44.2; Jun: 55.04; Jul: 62.6; Aug: 62.6; Sep: 50.7; Oct: 46.22; Nov: 36.5; Dec: 28
UT | PROVO MUNI (AWOS) | Jan: 29.6; Feb: 33.4; Mar: 42.7; Apr: 48.8; May: 58.4; Jun: 66.7; Jul: 74.8; Aug: 73.4; Sep: 62.7; Oct: 50.4; Nov: 37.5; Dec: 29.6; Jan: 26.1; Feb: 23.18; Mar: 27.9; Apr: 32; May: 36.5; Jun: 42.44; Jul: 47.84; Aug: 51.98; Sep: 38.5; Oct: 30.92; Nov: 30; Dec: 21.9
CO | PUEBLO MEMORIAL AP | Jan: 31.4; Feb: 34.3; Mar: 43.1; Apr: 50.7; May: 60.8; Jun: 70.9; Jul: 76.1; Aug: 73.8; Sep: 65.5; Oct: 52.3; Nov: 39.8; Dec: 30.9; Jan: 17.4; Feb: 18.68; Mar: 24.6; Apr: 35.06; May: 39.6; Jun: 47.84; Jul: 51.98; Aug: 50.36; Sep: 42.1; Oct: 28.22; Nov: 24.4; Dec: 18.9
VA | PULASKI-NEW RIVER VALLEY AP | Jan: 35; Feb: 38; Mar: 46; Apr: 55; May: 64; Jun: 71; Jul: 74; Aug: 73; Sep: 67; Oct: 57; Nov: 46; Dec: 39; Jan: 28.4; Feb: 26.96; Mar: 27.5; Apr: 35.6; May: 42.6; Jun: 54.14; Jul: 55.58; Aug: 53.96; Sep: 53.1; Oct: 44.06; Nov: 30.6; Dec: 25.3
WA | PULLMAN/MOSCOW RGNL | Jan: 32.2; Feb: 34.7; Mar: 40.8; Apr: 46.3; May: 53.2; Jun: 58.9; Jul: 66.7; Aug: 66.4; Sep: 59.5; Oct: 48; Nov: 37.7; Dec: 31.1; Jan: 26.1; Feb: 27.5; Mar: 31.3; Apr: 38.3; May: 39.9; Jun: 44.78; Jul: 42.44; Aug: 41.72; Sep: 48.7; Oct: 37.4; Nov: 26.4; Dec: 29.1
VA | QUANTICO MCAS | Jan: 36.4; Feb: 38.8; Mar: 46.3; Apr: 56.8; May: 65.4; Jun: 74; Jul: 78.4; Aug: 76.7; Sep: 69.7; Oct: 58.3; Nov: 47.9; Dec: 39.6; Jan: 28.6; Feb: 24.44; Mar: 34.7; Apr: 44.06; May: 49.3; Jun: 65.3; Jul: 66.92; Aug: 67.46; Sep: 61.7; Oct: 50.54; Nov: 40.5; Dec: 31.3
QC | QUEBEC AP | Jan: 11.1; Feb: 14; Mar: 24.9; Apr: 39.2; May: 53.1; Jun: 62.7; Jul: 67.3; Aug: 65.5; Sep: 56.9; Oct: 44.8; Nov: 32.5; Dec: 19.2; Jan: 5; Feb: 6.62; Mar: 16.2; Apr: 27.32; May: 39.2; Jun: 51.62; Jul: 57.74; Aug: 56.48; Sep: 49.6; Oct: 37.94; Nov: 28; Dec: 14.2
WA | QUILLAYUTE STATE AIRPORT | Jan: 41.8; Feb: 42.4; Mar: 44; Apr: 46.9; May: 51.5; Jun: 55.4; Jul: 59.2; Aug: 59.7; Sep: 57.2; Oct: 50.5; Nov: 44.9; Dec: 40.9; Jan: 38.3; Feb: 37.94; Mar: 39.7; Apr: 41.54; May: 45.3; Jun: 48.92; Jul: 53.24; Aug: 53.6; Sep: 51.3; Oct: 44.96; Nov: 42.3; Dec: 38.5
IL | QUINCY MUNI BALDWIN FLD | Jan: 26.9; Feb: 31.5; Mar: 42; Apr: 53.3; May: 63.2; Jun: 72.3; Jul: 76; Aug: 74.7; Sep: 66.3; Oct: 55; Nov: 42.5; Dec: 31.1; Jan: 21.4; Feb: 21.02; Mar: 35.4; Apr: 44.42; May: 53.8; Jun: 59; Jul: 65.66; Aug: 66.92; Sep: 60.4; Oct: 43.88; Nov: 36.5; Dec: 27.3
NC | RALEIGH DURHAM INTERNATIONAL | Jan: 41.9; Feb: 44.6; Mar: 51.5; Apr: 60.4; May: 68.1; Jun: 76.1; Jul: 79.8; Aug: 78.1; Sep: 71.7; Oct: 61; Nov: 51.3; Dec: 44.1; Jan: 30; Feb: 25.88; Mar: 35.4; Apr: 46.22; May: 59; Jun: 64.22; Jul: 68.54; Aug: 68; Sep: 63.9; Oct: 51.08; Nov: 39.2; Dec: 32.4
TX | RANDOLPH AFB | Jan: 52.4; Feb: 57; Mar: 62.2; Apr: 68.9; May: 76.4; Jun: 82.6; Jul: 84.5; Aug: 85.1; Sep: 79.5; Oct: 70.7; Nov: 60.4; Dec: 53.6; Jan: 37.6; Feb: 38.66; Mar: 39.9; Apr: 48.74; May: 67.6; Jun: 69.98; Jul: 70.34; Aug: 69.62; Sep: 61.9; Oct: 52.52; Nov: 45; Dec: 37.8
SD | RAPID CITY REGIONAL ARPT | Jan: 25; Feb: 27.4; Mar: 35.7; Apr: 44.6; May: 54.8; Jun: 64.6; Jul: 72.8; Aug: 71.9; Sep: 62; Oct: 48.1; Nov: 35; Dec: 25.9; Jan: 9.9; Feb: 11.66; Mar: 22.3; Apr: 29.48; May: 39.6; Jun: 50.72; Jul: 55.58; Aug: 50.54; Sep: 39.9; Oct: 30.56; Nov: 20.8; Dec: 15.8
WY | RAWLINS MUNICIPAL AP | Jan: 22.4; Feb: 22.9; Mar: 33.2; Apr: 40.7; May: 50; Jun: 60.3; Jul: 69.5; Aug: 66.1; Sep: 56.8; Oct: 43.9; Nov: 31.2; Dec: 21.9; Jan: 18.3; Feb: 19.58; Mar: 19; Apr: 22.46; May: 30; Jun: 37.22; Jul: 38.12; Aug: 41.9; Sep: 34.2; Oct: 26.96; Nov: 20.8; Dec: 16.3
PA | READING SPAATZ FIELD | Jan: 31.3; Feb: 32.4; Mar: 41.6; Apr: 52.7; May: 62.3; Jun: 71.2; Jul: 75.8; Aug: 73.6; Sep: 66.5; Oct: 54.6; Nov: 44.7; Dec: 35.1; Jan: 17.2; Feb: 21.2; Mar: 29.1; Apr: 39.56; May: 52.3; Jun: 60.26; Jul: 63.86; Aug: 64.04; Sep: 57.9; Oct: 46.94; Nov: 36.5; Dec: 27
CA | RED BLUFF MUNICIPAL ARPT | Jan: 47; Feb: 50.5; Mar: 54.9; Apr: 59.3; May: 67.9; Jun: 75.9; Jul: 81.8; Aug: 79.8; Sep: 75; Oct: 64.9; Nov: 53.4; Dec: 46.7; Jan: 40.1; Feb: 35.6; Mar: 38.1; Apr: 42.44; May: 45; Jun: 48.38; Jul: 52.88; Aug: 49.28; Sep: 45.9; Oct: 40.82; Nov: 39; Dec: 38.3
AB | RED DEER AP | Jan: 11; Feb: 15.3; Mar: 24.4; Apr: 38.6; May: 49.1; Jun: 56.4; Jul: 60.9; Aug: 59.2; Sep: 51.2; Oct: 38.6; Nov: 23.6; Dec: 12.8; Jan: 5; Feb: 6.62; Mar: 14.2; Apr: 24.62; May: 32.5; Jun: 44.06; Jul: 50.36; Aug: 47.48; Sep: 39; Oct: 27.32; Nov: 16.9; Dec: 5.5
IA | RED OAK | Jan: 25.2; Feb: 29.6; Mar: 40.6; Apr: 52.9; May: 63.7; Jun: 72.8; Jul: 77; Aug: 74.6; Sep: 65.4; Oct: 54.2; Nov: 41; Dec: 28.9; Jan: 12.6; Feb: 14.9; Mar: 33.3; Apr: 45.68; May: 51.6; Jun: 63.5; Jul: 65.66; Aug: 63.86; Sep: 53.6; Oct: 40.46; Nov: 25.7; Dec: 19.2
MN | RED WING | Jan: 15.5; Feb: 20.2; Mar: 32.2; Apr: 46.4; May: 57.9; Jun: 67.8; Jul: 72.4; Aug: 70; Sep: 61.6; Oct: 49.6; Nov: 34.9; Dec: 21.2; Jan: 10; Feb: 14.72; Mar: 27.3; Apr: 31.64; May: 42.1; Jun: 56.48; Jul: 66.38; Aug: 58.64; Sep: 54.1; Oct: 43.7; Nov: 23.7; Dec: 14.4
CA | REDDING MUNICIPAL ARPT | Jan: 46.7; Feb: 49.7; Mar: 54.1; Apr: 58.7; May: 67.3; Jun: 75.6; Jul: 82.6; Aug: 80; Sep: 74.9; Oct: 64.3; Nov: 52.4; Dec: 46; Jan: 38.5; Feb: 33.98; Mar: 41.5; Apr: 42.26; May: 43.9; Jun: 48.2; Jul: 52.7; Aug: 42.98; Sep: 45.7; Oct: 40.82; Nov: 39; Dec: 37
OR | REDMOND ROBERTS FIELD | Jan: 33.7; Feb: 35.4; Mar: 40.3; Apr: 44.4; May: 51.8; Jun: 58.1; Jul: 66.7; Aug: 65.5; Sep: 58.4; Oct: 47.5; Nov: 38.3; Dec: 31.8; Jan: 22.1; Feb: 24.26; Mar: 26.2; Apr: 31.1; May: 33.3; Jun: 39.74; Jul: 42.8; Aug: 39.38; Sep: 35.1; Oct: 31.82; Nov: 28.6; Dec: 28.8
MN | REDWOOD FALLS MUNI | Jan: 14.9; Feb: 19.5; Mar: 31.4; Apr: 46.1; May: 58.8; Jun: 68.8; Jul: 72.7; Aug: 70.3; Sep: 62.1; Oct: 48.8; Nov: 33; Dec: 19.5; Jan: 13.1; Feb: 7.34; Mar: 27.3; Apr: 36.86; May: 46; Jun: 60.44; Jul: 64.04; Aug: 58.64; Sep: 50.5; Oct: 35.24; Nov: 27.1; Dec: 7.3
SK | REGINA | Jan: 7; Feb: 7.9; Mar: 20.9; Apr: 39.4; May: 50.9; Jun: 59.8; Jul: 66; Aug: 63.7; Sep: 54.8; Oct: 39.7; Nov: 23.1; Dec: 9.8; Jan: 1.8; Feb: 3.74; Mar: 16.9; Apr: 27.86; May: 34.5; Jun: 45.86; Jul: 53.06; Aug: 51.08; Sep: 42.3; Oct: 29.84; Nov: 19.2; Dec: 3.6
NV | RENO TAHOE INTERNATIONAL AP | Jan: 35.5; Feb: 39.2; Mar: 45.6; Apr: 50.4; May: 59.1; Jun: 67.4; Jul: 75.9; Aug: 73.5; Sep: 65.9; Oct: 54.3; Nov: 42.8; Dec: 34.8; Jan: 20.7; Feb: 22.1; Mar: 26.6; Apr: 28.22; May: 30.6; Jun: 37.58; Jul: 40.64; Aug: 35.6; Sep: 36.3; Oct: 28.94; Nov: 22.3; Dec: 19.9
WA | RENTON MUNI | Jan: 42.3; Feb: 43.5; Mar: 46.5; Apr: 50.6; May: 56.5; Jun: 61.8; Jul: 67; Aug: 67.3; Sep: 62.2; Oct: 53.6; Nov: 46.1; Dec: 41.7; Jan: 37.2; Feb: 35.42; Mar: 41; Apr: 41.72; May: 45.1; Jun: 50.18; Jul: 53.24; Aug: 53.78; Sep: 52; Oct: 44.78; Nov: 41.4; Dec: 38.1
NY | REPUBLIC | Jan: 32; Feb: 34.3; Mar: 40.8; Apr: 50.5; May: 59.8; Jun: 69.3; Jul: 75.2; Aug: 74; Sep: 67.2; Oct: 56.3; Nov: 46.2; Dec: 37.4; Jan: 23.7; Feb: 17.78; Mar: 31.6; Apr: 37.22; May: 45.7; Jun: 57.92; Jul: 63.68; Aug: 66.92; Sep: 58.1; Oct: 44.24; Nov: 40.5; Dec: 25
WI | RHINELANDER ONEIDA | Jan: 13.5; Feb: 16.9; Mar: 27.7; Apr: 41.4; May: 53.5; Jun: 62.4; Jul: 67.2; Aug: 64.8; Sep: 56.8; Oct: 44.4; Nov: 32; Dec: 18.1; Jan: 10.2; Feb: 2.48; Mar: 21.7; Apr: 34.34; May: 42.6; Jun: 57.56; Jul: 59; Aug: 57.2; Sep: 49.8; Oct: 36.14; Nov: 27.3; Dec: 2.7
WI | RICE LAKE MUNICIPAL | Jan: 14.4; Feb: 17.8; Mar: 30.1; Apr: 44.6; May: 55.2; Jun: 64.8; Jul: 69.8; Aug: 67; Sep: 59.2; Oct: 46.6; Nov: 33.8; Dec: 19.5; Jan: 8.1; Feb: 6.26; Mar: 21.2; Apr: 37.04; May: 37.8; Jun: 57.56; Jul: 63.32; Aug: 62.78; Sep: 54.9; Oct: 32.36; Nov: 21; Dec: 8.4
VA | RICHMOND INTERNATIONAL AP | Jan: 39.2; Feb: 41.5; Mar: 48.9; Apr: 58.8; May: 66.7; Jun: 75.2; Jul: 79.4; Aug: 77.5; Sep: 70.9; Oct: 60.2; Nov: 50.2; Dec: 42.2; Jan: 23.5; Feb: 26.06; Mar: 31.8; Apr: 44.78; May: 54.1; Jun: 60.44; Jul: 69.08; Aug: 66.02; Sep: 63.9; Oct: 49.82; Nov: 37.6; Dec: 32.7
CO | RIFLE/GARFIELD RGNL | Jan: 25.1; Feb: 31; Mar: 40.4; Apr: 47.2; May: 57; Jun: 66.7; Jul: 73.9; Aug: 70.7; Sep: 62.3; Oct: 49.4; Nov: 36.5; Dec: 24.8; Jan: 14.7; Feb: 24.44; Mar: 19.6; Apr: 23.18; May: 33.1; Jun: 33.8; Jul: 47.12; Aug: 46.04; Sep: 41.2; Oct: 36.5; Nov: 24.6; Dec: 11.3
CA | RIVERSIDE MUNI | Jan: 56.2; Feb: 55.7; Mar: 58.8; Apr: 61.5; May: 67.7; Jun: 71.9; Jul: 78; Aug: 78.7; Sep: 76.1; Oct: 68.1; Nov: 60.6; Dec: 54.8; Jan: 34.7; Feb: 37.58; Mar: 49.1; Apr: 42.98; May: 51.4; Jun: 54.5; Jul: 56.12; Aug: 57.38; Sep: 54.3; Oct: 51.62; Nov: 41.9; Dec: 28.9
WY | RIVERTON MUNICIPL AP | Jan: 21.3; Feb: 25.1; Mar: 35.9; Apr: 43.8; May: 53.7; Jun: 63.5; Jul: 73.4; Aug: 70.3; Sep: 59.6; Oct: 45.7; Nov: 32; Dec: 20.9; Jan: 14.2; Feb: 9.86; Mar: 18; Apr: 30.02; May: 33.3; Jun: 34.52; Jul: 38.66; Aug: 40.82; Sep: 41.9; Oct: 28.22; Nov: 21; Dec: 13.5
VA | ROANOKE REGIONAL AP | Jan: 37.9; Feb: 40.4; Mar: 47.9; Apr: 57.5; May: 65.2; Jun: 73.1; Jul: 76.8; Aug: 75.5; Sep: 68.5; Oct: 58.2; Nov: 48.1; Dec: 40.2; Jan: 19.9; Feb: 21.74; Mar: 33.4; Apr: 41.9; May: 48.7; Jun: 60.62; Jul: 64.22; Aug: 64.76; Sep: 59; Oct: 46.04; Nov: 40.8; Dec: 25.9
NY | ROCHESTER GREATER ROCHESTER I | Jan: 25.8; Feb: 26.7; Mar: 34.7; Apr: 46.5; May: 57.6; Jun: 67; Jul: 71; Aug: 69.6; Sep: 62.2; Oct: 51.3; Nov: 40.9; Dec: 31.3; Jan: 18.5; Feb: 16.16; Mar: 26.2; Apr: 36.32; May: 47.3; Jun: 56.12; Jul: 62.6; Aug: 61.52; Sep: 55.6; Oct: 43.34; Nov: 33.6; Dec: 23.9
MN | ROCHESTER INTERNATIONAL ARPT | Jan: 15.2; Feb: 19.5; Mar: 31.7; Apr: 45.6; May: 57.4; Jun: 67.3; Jul: 70.4; Aug: 68.3; Sep: 60.6; Oct: 48.3; Nov: 33.7; Dec: 20.4; Jan: 4.6; Feb: 12.56; Mar: 24.4; Apr: 34.88; May: 48; Jun: 56.84; Jul: 61.34; Aug: 59.54; Sep: 46.6; Oct: 34.88; Nov: 25; Dec: 12.9
IL | ROCKFORD GREATER ROCKFORD AP | Jan: 21.6; Feb: 25.7; Mar: 37; Apr: 49; May: 59.9; Jun: 69.7; Jul: 73.1; Aug: 71.5; Sep: 63.6; Oct: 51.7; Nov: 38.6; Dec: 26.4; Jan: 10; Feb: 14.36; Mar: 26.1; Apr: 37.22; May: 46; Jun: 57.74; Jul: 60.8; Aug: 62.42; Sep: 53.8; Oct: 41.54; Nov: 27.3; Dec: 17.6
ME | ROCKLAND/KNOX(AWOS) | Jan: 22.4; Feb: 25; Mar: 32.4; Apr: 41.9; May: 51; Jun: 59.8; Jul: 65.6; Aug: 64.8; Sep: 57.9; Oct: 47.9; Nov: 39.2; Dec: 29.7; Jan: 19.8; Feb: 13.82; Mar: 24.6; Apr: 23.72; May: 39; Jun: 46.76; Jul: 50.54; Aug: 52.88; Sep: 54.1; Oct: 42.98; Nov: 29.3; Dec: 22.1
TX | ROCKPORT/ARANSAS CO | Jan: 57.4; Feb: 60.3; Mar: 65.9; Apr: 72.6; May: 78.7; Jun: 83.8; Jul: 84.4; Aug: 85.4; Sep: 81.9; Oct: 75.2; Nov: 66.1; Dec: 58.4; Jan: 52.3; Feb: 55.04; Mar: 60.8; Apr: 63.86; May: 72.1; Jun: 75.2; Jul: 76.1; Aug: 75.74; Sep: 72.9; Oct: 67.64; Nov: 63.5; Dec: 55.6
NC | ROCKY MOUNT WILSON | Jan: 41.1; Feb: 43.5; Mar: 51; Apr: 60.8; May: 68.2; Jun: 76.5; Jul: 79.2; Aug: 78; Sep: 71.8; Oct: 61.2; Nov: 51.1; Dec: 43.7; Jan: 28.2; Feb: 34.16; Mar: 40.6; Apr: 47.12; May: 56.7; Jun: 66.56; Jul: 65.66; Aug: 63.86; Sep: 59.9; Oct: 51.44; Nov: 43.9; Dec: 30.2
AR | ROGERS (AWOS) | Jan: 36.6; Feb: 40.3; Mar: 47.8; Apr: 57; May: 65.3; Jun: 74.1; Jul: 78.3; Aug: 77.5; Sep: 69.7; Oct: 59.1; Nov: 48.3; Dec: 38.8; Jan: 22.3; Feb: 24.26; Mar: 25.2; Apr: 36.5; May: 53.1; Jun: 65.48; Jul: 66.56; Aug: 64.58; Sep: 60.1; Oct: 43.34; Nov: 37.6; Dec: 31.6
GA | ROME R B RUSSELL AP | Jan: 42.2; Feb: 45.7; Mar: 53.1; Apr: 61.2; May: 69.2; Jun: 76.7; Jul: 79.8; Aug: 79.5; Sep: 73; Oct: 61.8; Nov: 51.1; Dec: 44.5; Jan: 31.5; Feb: 36.32; Mar: 31.3; Apr: 49.1; May: 56.7; Jun: 65.84; Jul: 67.64; Aug: 64.94; Sep: 64.8; Oct: 59.54; Nov: 33.6; Dec: 28.9
MN | ROSEAU MUNI (AWOS) | Jan: 5.5; Feb: 10.2; Mar: 23.7; Apr: 40.4; May: 52.6; Jun: 62.8; Jul: 67.3; Aug: 65.5; Sep: 57.3; Oct: 43.8; Nov: 27.8; Dec: 11.9; Jan: 6.6; Feb: 1.04; Mar: 14.4; Apr: 31.28; May: 39.9; Jun: 55.04; Jul: 60.98; Aug: 57.74; Sep: 48.9; Oct: 42.62; Nov: 26.6; Dec: 13.3
OR | ROSEBURG REGIONAL AP | Jan: 43.3; Feb: 45.1; Mar: 48.4; Apr: 52.1; May: 58.3; Jun: 64; Jul: 71.3; Aug: 71.1; Sep: 66.1; Oct: 55.8; Nov: 47.5; Dec: 42.2; Jan: 37.6; Feb: 42.08; Mar: 42.6; Apr: 40.64; May: 46.8; Jun: 48.38; Jul: 53.96; Aug: 53.42; Sep: 51.6; Oct: 46.04; Nov: 43.3; Dec: 37.6
NM | ROSWELL INDUSTRIAL AIR PARK | Jan: 41.7; Feb: 46.4; Mar: 54; Apr: 62.2; May: 71.3; Jun: 79.8; Jul: 81.1; Aug: 79.8; Sep: 72.9; Oct: 62.2; Nov: 49.8; Dec: 41.3; Jan: 21.6; Feb: 25.16; Mar: 25.5; Apr: 26.24; May: 37.8; Jun: 44.96; Jul: 57.56; Aug: 55.04; Sep: 52.9; Oct: 32.9; Nov: 30; Dec: 28.2
KS | RUSSELL MUNICIPAL AP | Jan: 30.2; Feb: 34; Mar: 43.8; Apr: 53.4; May: 64; Jun: 74.7; Jul: 79.9; Aug: 77.8; Sep: 68.9; Oct: 56.2; Nov: 42.5; Dec: 31.7; Jan: 17.1; Feb: 17.96; Mar: 27; Apr: 41.36; May: 57; Jun: 56.66; Jul: 60.8; Aug: 61.16; Sep: 54.1; Oct: 41.72; Nov: 32.2; Dec: 27.9
VT | RUTLAND STATE | Jan: 20.6; Feb: 23; Mar: 31.8; Apr: 44.1; May: 55.3; Jun: 64.1; Jul: 68.2; Aug: 66.6; Sep: 59.3; Oct: 47.9; Nov: 38; Dec: 27.1; Jan: 8.1; Feb: 10.04; Mar: 17.2; Apr: 33.62; May: 44.8; Jun: 53.42; Jul: 60.26; Aug: 56.84; Sep: 52.9; Oct: 40.28; Nov: 24.6; Dec: 15.1
CA | SACRAMENTO EXECUTIVE ARPT | Jan: 47.2; Feb: 51.1; Mar: 55.2; Apr: 59.1; May: 65.8; Jun: 71.4; Jul: 75.5; Aug: 74.9; Sep: 72.2; Oct: 64.3; Nov: 53.8; Dec: 47; Jan: 41.5; Feb: 41.18; Mar: 42.6; Apr: 47.3; May: 47.8; Jun: 51.08; Jul: 53.42; Aug: 54.86; Sep: 51.1; Oct: 46.4; Nov: 43.3; Dec: 39
CA | SACRAMENTO METROPOLITAN AP | Jan: 47; Feb: 50.8; Mar: 55.2; Apr: 59.5; May: 66.7; Jun: 72.8; Jul: 76.8; Aug: 75.8; Sep: 72.6; Oct: 64.3; Nov: 53.7; Dec: 46.8; Jan: 41; Feb: 42.08; Mar: 46.2; Apr: 44.78; May: 46.8; Jun: 53.42; Jul: 55.04; Aug: 55.04; Sep: 51.6; Oct: 47.3; Nov: 42.4; Dec: 41
AZ | SAFFORD (AMOS) | Jan: 47.3; Feb: 50.9; Mar: 57; Apr: 64.5; May: 73.5; Jun: 83.1; Jul: 85.3; Aug: 83.4; Sep: 78.8; Oct: 67.3; Nov: 55; Dec: 46.6; Jan: 19.8; Feb: 21.2; Mar: 36.1; Apr: 28.94; May: 30.6; Jun: 33.8; Jul: 46.4; Aug: 56.3; Sep: 43.3; Oct: 41.36; Nov: 27; Dec: 27
MI | SAGINAW TRI CITY INTL AP | Jan: 23; Feb: 24.6; Mar: 33.8; Apr: 46; May: 57.7; Jun: 67.9; Jul: 71.1; Aug: 69.1; Sep: 61.6; Oct: 50.5; Nov: 38.7; Dec: 28.4; Jan: 9.7; Feb: 11.12; Mar: 30.4; Apr: 32.9; May: 41.9; Jun: 53.78; Jul: 57.56; Aug: 66.02; Sep: 51.4; Oct: 42.8; Nov: 33.1; Dec: 22.1
UT | SAINT GEORGE (AWOS) | Jan: 42.6; Feb: 46.9; Mar: 55.3; Apr: 61.9; May: 72.9; Jun: 82.2; Jul: 88.5; Aug: 86.3; Sep: 78.4; Oct: 64.5; Nov: 50.2; Dec: 40.8; Jan: 26.1; Feb: 35.24; Mar: 23.4; Apr: 25.7; May: 21.7; Jun: 30.02; Jul: 42.08; Aug: 47.12; Sep: 37.6; Oct: 35.06; Nov: 32.7; Dec: 23.2
AK | SAINT MARY`S (AWOS) | Jan: 6.3; Feb: 10.7; Mar: 11; Apr: 24.7; May: 39.5; Jun: 50.1; Jul: 53.2; Aug: 51.3; Sep: 44.1; Oct: 28.9; Nov: 17.6; Dec: 9.1; Jan: 7.3; Feb: 13.46; Mar: 17.8; Apr: 24.98; May: 27; Jun: 38.84; Jul: 44.96; Aug: 43.88; Sep: 33.4; Oct: 28.94; Nov: 19.9; Dec: 11.8
OR | SALEM MCNARY FIELD | Jan: 41.6; Feb: 43.5; Mar: 47.1; Apr: 50.7; May: 56.7; Jun: 61.6; Jul: 68.5; Aug: 68.3; Sep: 63.8; Oct: 53.8; Nov: 46; Dec: 40.8; Jan: 36.9; Feb: 35.24; Mar: 41; Apr: 42.8; May: 46; Jun: 49.82; Jul: 52.34; Aug: 52.52; Sep: 49.8; Oct: 44.06; Nov: 43; Dec: 35.6
KS | SALINA MUNICIPAL AP | Jan: 31.5; Feb: 35.7; Mar: 45.5; Apr: 55.2; May: 65.9; Jun: 76.5; Jul: 81.5; Aug: 79.7; Sep: 70.4; Oct: 57.9; Nov: 44.2; Dec: 33.1; Jan: 18.1; Feb: 21.92; Mar: 34.2; Apr: 38.84; May: 52.2; Jun: 63.14; Jul: 64.58; Aug: 66.38; Sep: 55.2; Oct: 42.08; Nov: 34.2; Dec: 29.5
CA | SALINAS MUNICIPAL AP | Jan: 51.7; Feb: 52.8; Mar: 54.8; Apr: 56.4; May: 59.1; Jun: 61.1; Jul: 62.7; Aug: 63.6; Sep: 63.7; Oct: 61.3; Nov: 56.2; Dec: 51.1; Jan: 40.1; Feb: 46.58; Mar: 43.5; Apr: 44.06; May: 48.9; Jun: 52.52; Jul: 52.52; Aug: 55.4; Sep: 54.3; Oct: 48.2; Nov: 42.8; Dec: 41.4
MD | SALISBURY WICOMICO CO AP | Jan: 36.8; Feb: 38.3; Mar: 45.2; Apr: 55; May: 63.3; Jun: 72.5; Jul: 77.4; Aug: 75.3; Sep: 68.8; Oct: 58; Nov: 48.2; Dec: 40.4; Jan: 25.2; Feb: 29.12; Mar: 37.6; Apr: 46.76; May: 54.3; Jun: 62.24; Jul: 66.92; Aug: 66.74; Sep: 61.7; Oct: 50.18; Nov: 39.6; Dec: 37.2
ID | SALMON/LEMHI (AWOS) | Jan: 20.1; Feb: 25.2; Mar: 37.2; Apr: 44; May: 52.7; Jun: 58.9; Jul: 67.8; Aug: 65.5; Sep: 56.3; Oct: 44; Nov: 31.1; Dec: 20.6; Jan: 16; Feb: 19.58; Mar: 22.3; Apr: 29.66; May: 35.1; Jun: 40.28; Jul: 45.5; Aug: 42.26; Sep: 37.2; Oct: 29.12; Nov: 23; Dec: 22.1
UT | SALT LAKE CITY INT ARPT [ISIS] | Jan: 30.2; Feb: 35.1; Mar: 44.4; Apr: 50.6; May: 60.2; Jun: 70.1; Jul: 79.8; Aug: 77.8; Sep: 67.5; Oct: 53.6; Nov: 40.5; Dec: 30.8; Jan: 22.6; Feb: 24.44; Mar: 29.7; Apr: 31.82; May: 39.7; Jun: 38.3; Jul: 46.94; Aug: 43.88; Sep: 41.2; Oct: 37.22; Nov: 28.4; Dec: 25.2
TX | SAN ANGELO MATHIS FIELD | Jan: 47.4; Feb: 51.2; Mar: 58.7; Apr: 67; May: 75.2; Jun: 81.7; Jul: 83.7; Aug: 83.1; Sep: 76.1; Oct: 66.5; Nov: 55.4; Dec: 48; Jan: 27.7; Feb: 33.98; Mar: 34.5; Apr: 47.3; May: 57; Jun: 61.7; Jul: 63.86; Aug: 63.68; Sep: 59.4; Oct: 47.84; Nov: 44.2; Dec: 31.3
TX | SAN ANTONIO INTL AP | Jan: 52.9; Feb: 56.9; Mar: 62.8; Apr: 70; May: 77.1; Jun: 83; Jul: 84.7; Aug: 85.6; Sep: 80; Oct: 71.5; Nov: 61.1; Dec: 53.9; Jan: 39.4; Feb: 40.1; Mar: 41.5; Apr: 56.66; May: 65.5; Jun: 70.52; Jul: 70.34; Aug: 69.44; Sep: 65.7; Oct: 57.74; Nov: 49.3; Dec: 40.6
TX | SAN ANTONIO KELLY FIELD AFB | Jan: 53.1; Feb: 57.5; Mar: 62.8; Apr: 70.4; May: 77.8; Jun: 83.3; Jul: 85; Aug: 85.6; Sep: 80.1; Oct: 71.5; Nov: 60.8; Dec: 54.3; Jan: 37; Feb: 39.2; Mar: 40.8; Apr: 49.28; May: 66.9; Jun: 67.28; Jul: 71.42; Aug: 69.26; Sep: 62.1; Oct: 53.06; Nov: 48.2; Dec: 40.5
TX | SAN ANTONIO/STINSON | Jan: 53.6; Feb: 57.6; Mar: 64.2; Apr: 71.5; May: 78; Jun: 83.7; Jul: 84.8; Aug: 86.2; Sep: 80.8; Oct: 72.3; Nov: 62.3; Dec: 54.2; Jan: 41.5; Feb: 33.26; Mar: 45.7; Apr: 62.96; May: 64.8; Jun: 69.98; Jul: 66.56; Aug: 69.44; Sep: 67.3; Oct: 56.84; Nov: 50; Dec: 36.7
CA | SAN DIEGO LINDBERGH FIELD | Jan: 57.5; Feb: 57.9; Mar: 59.6; Apr: 61.7; May: 64.2; Jun: 66.3; Jul: 69.7; Aug: 71.3; Sep: 70.6; Oct: 66.9; Nov: 61.8; Dec: 57.1; Jan: 46.4; Feb: 50; Mar: 49.5; Apr: 50.72; May: 54; Jun: 57.92; Jul: 61.7; Aug: 63.14; Sep: 62.2; Oct: 55.22; Nov: 45.9; Dec: 39.6
CA | SAN DIEGO MIRAMAR NAS | Jan: 56.5; Feb: 56.6; Mar: 57.6; Apr: 60.2; May: 63.4; Jun: 66.7; Jul: 71; Aug: 72.5; Sep: 71.2; Oct: 66.2; Nov: 60.7; Dec: 55.7; Jan: 44.4; Feb: 43.16; Mar: 45.3; Apr: 48.2; May: 53.6; Jun: 58.64; Jul: 62.42; Aug: 61.88; Sep: 60.4; Oct: 48.02; Nov: 46.8; Dec: 37.2
CA | SAN DIEGO NORTH ISLAND NAS | Jan: 57.9; Feb: 58.2; Mar: 59.8; Apr: 62; May: 64.5; Jun: 66.7; Jul: 69.9; Aug: 71.4; Sep: 70.9; Oct: 67.3; Nov: 62.4; Dec: 57.6; Jan: 47.1; Feb: 50; Mar: 47.8; Apr: 51.08; May: 54.5; Jun: 58.46; Jul: 63.5; Aug: 64.22; Sep: 63; Oct: 57.74; Nov: 51.6; Dec: 51.4
CA | SAN DIEGO/MONTGOMER | Jan: 56.5; Feb: 56.1; Mar: 58.2; Apr: 60.1; May: 63.7; Jun: 66.5; Jul: 71; Aug: 72.6; Sep: 71.5; Oct: 66.5; Nov: 60.9; Dec: 55.8; Jan: 43.2; Feb: 45.14; Mar: 48; Apr: 47.12; May: 52.7; Jun: 56.66; Jul: 59.9; Aug: 59.72; Sep: 55.9; Oct: 55.4; Nov: 44.2; Dec: 40.6
CA | SAN FRANCISCO INTL AP | Jan: 50.7; Feb: 52.7; Mar: 54.8; Apr: 56.7; May: 59.3; Jun: 61.7; Jul: 63.3; Aug: 64.1; Sep: 64.5; Oct: 62.1; Nov: 56.1; Dec: 51; Jan: 43.5; Feb: 43.88; Mar: 46.6; Apr: 46.76; May: 48.9; Jun: 50; Jul: 51.26; Aug: 52.7; Sep: 54.5; Oct: 48.92; Nov: 46.9; Dec: 43
CA | SAN JOSE INTL AP | Jan: 51.1; Feb: 53.4; Mar: 56.5; Apr: 58.7; May: 63.1; Jun: 66.9; Jul: 69.6; Aug: 69.8; Sep: 68.9; Oct: 64.2; Nov: 56.6; Dec: 50.9; Jan: 41.4; Feb: 41.9; Mar: 46.2; Apr: 44.78; May: 48.2; Jun: 51.08; Jul: 54.5; Aug: 55.22; Sep: 52.9; Oct: 49.28; Nov: 41.5; Dec: 41
CA | SAN LUIS CO RGNL | Jan: 53.4; Feb: 53.9; Mar: 55.8; Apr: 57.3; May: 60.4; Jun: 62.9; Jul: 65.9; Aug: 66.5; Sep: 66; Oct: 63.4; Nov: 58; Dec: 52.7; Jan: 40.3; Feb: 41.72; Mar: 48.7; Apr: 46.22; May: 47.8; Jun: 50.54; Jul: 52.88; Aug: 53.96; Sep: 49.8; Oct: 50.18; Nov: 43; Dec: 39.6
AK | SAND POINT | Jan: 31.4; Feb: 32.7; Mar: 31.6; Apr: 35.7; May: 41.6; Jun: 47.3; Jul: 51.6; Aug: 53.3; Sep: 49.7; Oct: 42.4; Nov: 37.2; Dec: 33.7; Jan: 28.6; Feb: 24.62; Mar: 28.2; Apr: 27.68; May: 30.4; Jun: 39.2; Jul: 42.98; Aug: 47.12; Sep: 38.1; Oct: 32.18; Nov: 23.9; Dec: 23.2
CA | SANDBERG | Jan: 44.1; Feb: 43.8; Mar: 48; Apr: 50.8; May: 58.6; Jun: 66.9; Jul: 74.9; Aug: 75.1; Sep: 70.8; Oct: 60.4; Nov: 50.4; Dec: 43.2; Jan: 22.3; Feb: 17.96; Mar: 36.1; Apr: 32; May: 34.3; Jun: 37.76; Jul: 39.02; Aug: 40.28; Sep: 36.3; Oct: 34.52; Nov: 23.2; Dec: 28.2
ME | SANFORD MUNI (AWOS) | Jan: 21.3; Feb: 23.1; Mar: 32.5; Apr: 44; May: 53.6; Jun: 63.8; Jul: 69; Aug: 66.6; Sep: 58.9; Oct: 47.8; Nov: 38; Dec: 28; Jan: 18.1; Feb: 11.12; Mar: 23.7; Apr: 24.26; May: 36.7; Jun: 45.86; Jul: 57.02; Aug: 49.28; Sep: 45.9; Oct: 32.9; Nov: 30.4; Dec: 19
CA | SANTA ANA-JOHN WAYNE AP | Jan: 58; Feb: 58; Mar: 60; Apr: 62; May: 65; Jun: 68; Jul: 72; Aug: 73; Sep: 72; Oct: 69; Nov: 63; Dec: 57; Jan: 46.4; Feb: 49.28; Mar: 51.6; Apr: 50; May: 56.5; Jun: 56.66; Jul: 60.62; Aug: 62.06; Sep: 60.8; Oct: 57.38; Nov: 50.7; Dec: 43.2
CA | SANTA BARBARA MUNICIPAL AP | Jan: 53; Feb: 54; Mar: 55.9; Apr: 58; May: 60.8; Jun: 62.8; Jul: 65.7; Aug: 66.2; Sep: 65.4; Oct: 62.1; Nov: 57.3; Dec: 52.5; Jan: 46; Feb: 42.98; Mar: 49.3; Apr: 46.76; May: 50.2; Jun: 55.94; Jul: 58.64; Aug: 59.18; Sep: 57.9; Oct: 51.44; Nov: 44.4; Dec: 40.3
NM | SANTA FE COUNTY MUNICIPAL AP | Jan: 32.7; Feb: 35.9; Mar: 43.3; Apr: 50.5; May: 60.1; Jun: 70; Jul: 73.3; Aug: 71.1; Sep: 64.7; Oct: 52.8; Nov: 40.7; Dec: 31.3; Jan: 14.4; Feb: 22.46; Mar: 23.4; Apr: 23.36; May: 34.7; Jun: 33.26; Jul: 51.44; Aug: 50.54; Sep: 43.3; Oct: 30.74; Nov: 22.1; Dec: 15.1
CA | SANTA MARIA PUBLIC ARPT | Jan: 52.4; Feb: 53.1; Mar: 54.8; Apr: 56; May: 58.5; Jun: 60.6; Jul: 63.2; Aug: 63.6; Sep: 63.5; Oct: 61.4; Nov: 56.7; Dec: 51.8; Jan: 40.6; Feb: 41.72; Mar: 46.9; Apr: 46.22; May: 48.6; Jun: 51.8; Jul: 53.6; Aug: 54.14; Sep: 54.3; Oct: 49.64; Nov: 45.9; Dec: 37.4
CA | SANTA MONICA MUNI | Jan: 57.5; Feb: 56.5; Mar: 58.5; Apr: 59.7; May: 63.2; Jun: 65.6; Jul: 68.5; Aug: 68.7; Sep: 68.3; Oct: 65; Nov: 61.1; Dec: 56.4; Jan: 44.6; Feb: 43.88; Mar: 50.9; Apr: 48.02; May: 53.6; Jun: 55.58; Jul: 61.34; Aug: 59.72; Sep: 61.9; Oct: 56.12; Nov: 44.1; Dec: 43
CA | SANTA ROSA (AWOS) | Jan: 47.2; Feb: 49.8; Mar: 53; Apr: 55.5; May: 60.9; Jun: 65.5; Jul: 67.2; Aug: 67.4; Sep: 65.9; Oct: 60.7; Nov: 52.9; Dec: 47.4; Jan: 42.4; Feb: 45.14; Mar: 44.6; Apr: 45.68; May: 48.7; Jun: 52.34; Jul: 52.34; Aug: 54.32; Sep: 51.6; Oct: 47.12; Nov: 42.6; Dec: 43.9
FL | SARASOTA BRADENTON | Jan: 61.9; Feb: 63.9; Mar: 67.2; Apr: 71.6; May: 77.2; Jun: 81; Jul: 82.5; Aug: 82.7; Sep: 81.4; Oct: 76.3; Nov: 69; Dec: 64.2; Jan: 47.5; Feb: 53.24; Mar: 59.7; Apr: 60.44; May: 67.1; Jun: 71.42; Jul: 75.02; Aug: 73.94; Sep: 72.7; Oct: 72.14; Nov: 59.7; Dec: 58.6
SK | SASKATOON | Jan: 4; Feb: 8.8; Mar: 21.3; Apr: 39.2; May: 51.1; Jun: 59.7; Jul: 64.5; Aug: 63.3; Sep: 53.8; Oct: 39; Nov: 21.8; Dec: 7.9; Jan: 0.9; Feb: 2.48; Mar: 14.4; Apr: 27.32; May: 34; Jun: 47.66; Jul: 55.04; Aug: 51.08; Sep: 43; Oct: 29.3; Nov: 18.5; Dec: 3.6
ON | SAULT STE MARIE | Jan: 15.2; Feb: 16.4; Mar: 24.8; Apr: 38.1; May: 50.2; Jun: 59.7; Jul: 64.1; Aug: 63.8; Sep: 56.7; Oct: 45.3; Nov: 34.2; Dec: 22.9; Jan: 10.8; Feb: 11.3; Mar: 17.6; Apr: 28.04; May: 39; Jun: 50.9; Jul: 55.76; Aug: 56.12; Sep: 51.3; Oct: 38.84; Nov: 29.8; Dec: 18.1
MI | SAULT STE MARIE SANDERSON FIE | Jan: 15.7; Feb: 17.6; Mar: 26.4; Apr: 39.1; May: 51.3; Jun: 60.5; Jul: 64.9; Aug: 64.6; Sep: 57.1; Oct: 45.6; Nov: 34.1; Dec: 23; Jan: 4.6; Feb: 8.6; Mar: 18.7; Apr: 26.42; May: 41.7; Jun: 51.08; Jul: 55.22; Aug: 56.12; Sep: 49.1; Oct: 36.5; Nov: 29.7; Dec: 14.5
GA | SAVANNAH INTL AP | Jan: 50.7; Feb: 53.6; Mar: 59.5; Apr: 66.2; May: 73.5; Jun: 79.6; Jul: 82.4; Aug: 81.5; Sep: 77.1; Oct: 68.1; Nov: 58.7; Dec: 52.6; Jan: 38.8; Feb: 41.18; Mar: 50.4; Apr: 50.9; May: 60.1; Jun: 70.7; Jul: 72.68; Aug: 71.6; Sep: 69.1; Oct: 55.4; Nov: 51.6; Dec: 39.6
AK | SAVOONGA | Jan: 3.8; Feb: 3.5; Mar: 7.2; Apr: 16.2; May: 29.6; Jun: 40; Jul: 47; Aug: 46.6; Sep: 41; Oct: 32.9; Nov: 25.4; Dec: 12.1; Jan: 3.9; Feb: 9.68; Mar: 3.2; Apr: 13.1; May: 28.6; Jun: 32.36; Jul: 32.36; Aug: 33.98; Sep: 34; Oct: 26.96; Nov: 21.7; Dec: 13.3
NE | SCOTTSBLUFF W B HEILIG FIELD | Jan: 27.9; Feb: 30.5; Mar: 39; Apr: 46.6; May: 57.2; Jun: 67.6; Jul: 74.3; Aug: 72.2; Sep: 62.5; Oct: 48.7; Nov: 36.3; Dec: 27.2; Jan: 8.8; Feb: 15.98; Mar: 19.9; Apr: 28.4; May: 42.6; Jun: 49.28; Jul: 53.42; Aug: 53.78; Sep: 42.6; Oct: 29.48; Nov: 22.5; Dec: 16.9
AZ | SCOTTSDALE MUNI | Jan: 55; Feb: 56.7; Mar: 63.9; Apr: 70.5; May: 79.7; Jun: 89.3; Jul: 93.5; Aug: 91.8; Sep: 86.6; Oct: 74.7; Nov: 63.4; Dec: 53.4; Jan: 29.1; Feb: 33.62; Mar: 31.1; Apr: 35.06; May: 37.4; Jun: 37.94; Jul: 57.2; Aug: 61.7; Sep: 50.4; Oct: 42.98; Nov: 37; Dec: 30
WA | SEATTLE BOEING FIELD [ISIS] | Jan: 42.7; Feb: 44.1; Mar: 47.3; Apr: 51.5; May: 57.4; Jun: 62.1; Jul: 67.4; Aug: 67.5; Sep: 62.9; Oct: 53.9; Nov: 46.4; Dec: 41.8; Jan: 36; Feb: 35.42; Mar: 40.3; Apr: 42.44; May: 45.9; Jun: 49.46; Jul: 52.16; Aug: 54.32; Sep: 48.9; Oct: 47.3; Nov: 43; Dec: 38.8
WA | SEATTLE SEATTLE-TACOMA INTL A | Jan: 41.9; Feb: 43.3; Mar: 46.2; Apr: 50.1; May: 55.9; Jun: 60.6; Jul: 66; Aug: 66.1; Sep: 61.7; Oct: 52.8; Nov: 45.6; Dec: 41; Jan: 34.2; Feb: 35.24; Mar: 37.2; Apr: 41.54; May: 45.5; Jun: 48.02; Jul: 50.72; Aug: 53.42; Sep: 51.3; Oct: 44.96; Nov: 41.5; Dec: 36.5
AK | SELAWIK | Jan: -5.1; Feb: -2.1; Mar: 1.3; Apr: 15; May: 34.7; Jun: 51.4; Jul: 57.2; Aug: 53.7; Sep: 43.3; Oct: 24; Nov: 6.4; Dec: -0.9; Jan: -14.6; Feb: -6.34; Mar: 8.6; Apr: 16.52; May: 29.5; Jun: 38.12; Jul: 44.6; Aug: 41; Sep: 29.1; Oct: 25.7; Nov: 4.6; Dec: 5
AK | SEWARD | Jan: 25.8; Feb: 27.4; Mar: 30.9; Apr: 38.1; May: 45.8; Jun: 51.9; Jul: 55.6; Aug: 55.2; Sep: 49.6; Oct: 39.8; Nov: 31.1; Dec: 27.1; Jan: 27; Feb: 23; Mar: 22.6; Apr: 31.64; May: 33.6; Jun: 43.52; Jul: 49.1; Aug: 46.4; Sep: 38.3; Oct: 27.32; Nov: 20.1; Dec: 26.6
OR | SEXTON SUMMIT | Jan: 37.8; Feb: 37.9; Mar: 39.4; Apr: 42.6; May: 49.8; Jun: 55.4; Jul: 64.5; Aug: 64.3; Sep: 60.8; Oct: 50.1; Nov: 41; Dec: 36.8; Jan: 30; Feb: 30.02; Mar: 29.1; Apr: 35.06; May: 36.5; Jun: 43.88; Jul: 48.38; Aug: 48.2; Sep: 37.9; Oct: 37.22; Nov: 30; Dec: 27.3
VA | SHANNON ARPT | Jan: 37.3; Feb: 39.4; Mar: 47; Apr: 57.3; May: 66.1; Jun: 74.5; Jul: 78.5; Aug: 77.5; Sep: 70; Oct: 58.8; Nov: 48.4; Dec: 40.4; Jan: 27.7; Feb: 24.8; Mar: 27; Apr: 36.14; May: 50.9; Jun: 63.68; Jul: 63.5; Aug: 67.1; Sep: 57.6; Oct: 46.76; Nov: 32; Dec: 32.4
NS | SHEARWATER | Jan: 23.4; Feb: 24.3; Mar: 31.3; Apr: 39.7; May: 48.4; Jun: 57.9; Jul: 64.3; Aug: 65.7; Sep: 59.7; Oct: 49.6; Nov: 40.3; Dec: 30.7; Jan: 16.3; Feb: 15.8; Mar: 22.1; Apr: 30.38; May: 39.4; Jun: 50; Jul: 57.74; Aug: 57.92; Sep: 52; Oct: 42.62; Nov: 33.8; Dec: 23.5
IA | SHELDON | Jan: 18.5; Feb: 22.5; Mar: 34.2; Apr: 48.1; May: 59.8; Jun: 69.8; Jul: 73.4; Aug: 70.2; Sep: 61.6; Oct: 49.2; Nov: 35.3; Dec: 23.2; Jan: 13.5; Feb: 29.48; Mar: 35.4; Apr: 41.9; May: 47.8; Jun: 60.08; Jul: 68.9; Aug: 65.66; Sep: 52.5; Oct: 43.7; Nov: 18.1; Dec: 17.4
AK | SHEMYA AFB | Jan: 31.1; Feb: 31.9; Mar: 32.1; Apr: 35.4; May: 39; Jun: 43.3; Jul: 47.5; Aug: 50.3; Sep: 48.6; Oct: 43.1; Nov: 37.8; Dec: 33; Jan: 23.9; Feb: 25.7; Mar: 24.4; Apr: 28.04; May: 32.9; Jun: 37.58; Jul: 43.7; Aug: 46.58; Sep: 43; Oct: 34.34; Nov: 27.7; Dec: 24.3
IA | SHENANDOAH MUNI | Jan: 25.9; Feb: 29.6; Mar: 41.1; Apr: 53; May: 64.5; Jun: 73.1; Jul: 77.6; Aug: 74.7; Sep: 66.2; Oct: 55.1; Nov: 40.9; Dec: 29.4; Jan: 18.7; Feb: 18.86; Mar: 28.6; Apr: 42.26; May: 55; Jun: 64.58; Jul: 64.4; Aug: 70.52; Sep: 56.7; Oct: 40.64; Nov: 28.9; Dec: 19.4
QC | SHERBROOKE AP | Jan: 13.4; Feb: 15.5; Mar: 26.1; Apr: 40.1; May: 52.5; Jun: 61.5; Jul: 65.6; Aug: 63.9; Sep: 55.9; Oct: 44.6; Nov: 33.5; Dec: 21; Jan: 5.9; Feb: 6.8; Mar: 15.4; Apr: 28.4; May: 40.5; Jun: 53.06; Jul: 57.74; Aug: 57.02; Sep: 49.8; Oct: 37.4; Nov: 28.6; Dec: 15.4
WY | SHERIDAN COUNTY ARPT | Jan: 24.3; Feb: 26.9; Mar: 35.8; Apr: 43.6; May: 52.6; Jun: 61.5; Jul: 70.8; Aug: 69.5; Sep: 59.4; Oct: 46; Nov: 33.6; Dec: 24.1; Jan: 11.5; Feb: 15.44; Mar: 22.3; Apr: 29.84; May: 40.8; Jun: 46.58; Jul: 50.36; Aug: 47.84; Sep: 39.6; Oct: 30.56; Nov: 21.6; Dec: 15.6
AK | SHISHMAREF (AWOS) | Jan: -0.2; Feb: 0.5; Mar: -0.7; Apr: 11.8; May: 28.9; Jun: 39.1; Jul: 49.3; Aug: 48.5; Sep: 41.8; Oct: 29.5; Nov: 16.3; Dec: 3.8; Jan: -0.9; Feb: -8.5; Mar: 1.9; Apr: 14.54; May: 27.1; Jun: 33.8; Jul: 42.8; Aug: 41; Sep: 32; Oct: 26.78; Nov: 15.6; Dec: 7.7
AZ | SHOW LOW MUNI AP | Jan: 33; Feb: 38; Mar: 45; Apr: 50; May: 57; Jun: 69; Jul: 72; Aug: 69; Sep: 64; Oct: 54; Nov: 44; Dec: 34; Jan: 18.3; Feb: 21.2; Mar: 18.9; Apr: 23.9; May: 31.8; Jun: 32.54; Jul: 39.2; Aug: 50.36; Sep: 41.2; Oct: 32.54; Nov: 22.1; Dec: 19.8
LA | SHREVEPORT DOWNTOWN | Jan: 48; Feb: 50.6; Mar: 57.9; Apr: 66; May: 74.2; Jun: 81.2; Jul: 83.7; Aug: 84.5; Sep: 77.6; Oct: 66.7; Nov: 56.2; Dec: 48.2; Jan: 32.5; Feb: 33.44; Mar: 39; Apr: 48.92; May: 58.3; Jun: 69.26; Jul: 73.22; Aug: 71.96; Sep: 65.8; Oct: 57.56; Nov: 44.4; Dec: 37.2
LA | SHREVEPORT REGIONAL ARPT | Jan: 48.1; Feb: 51.7; Mar: 58.6; Apr: 65.9; May: 73.8; Jun: 80.7; Jul: 83.4; Aug: 83.7; Sep: 77.8; Oct: 67.1; Nov: 56.4; Dec: 49.1; Jan: 35.8; Feb: 37.4; Mar: 48.9; Apr: 55.58; May: 62.4; Jun: 68.54; Jul: 70.7; Aug: 71.42; Sep: 66.2; Oct: 53.06; Nov: 44.8; Dec: 35.6
NE | SIDNEY MUNICIPAL AP | Jan: 28.4; Feb: 30; Mar: 38.6; Apr: 45.6; May: 56; Jun: 67; Jul: 74; Aug: 72; Sep: 62.8; Oct: 48.8; Nov: 36.7; Dec: 27.9; Jan: 12; Feb: 18.32; Mar: 28; Apr: 33.98; May: 43.3; Jun: 50.36; Jul: 45.86; Aug: 49.82; Sep: 44.2; Oct: 23.9; Nov: 23.2; Dec: 17.1
MT | SIDNEY-RICHLAND | Jan: 15; Feb: 19.2; Mar: 30.6; Apr: 44; May: 54.3; Jun: 63.3; Jul: 70.7; Aug: 69.1; Sep: 58.9; Oct: 45.1; Nov: 29.8; Dec: 19.6; Jan: -5.3; Feb: 13.64; Mar: 10; Apr: 27.5; May: 37.9; Jun: 47.12; Jul: 58.1; Aug: 48.2; Sep: 42.8; Oct: 25.52; Nov: 25.2; Dec: 3.4
NM | SIERRA BLANCA RGNL | Jan: 39; Feb: 40.5; Mar: 46.2; Apr: 52.8; May: 62; Jun: 69.7; Jul: 70.1; Aug: 68.3; Sep: 63.5; Oct: 54.8; Nov: 45.5; Dec: 37.9; Jan: 23.2; Feb: 19.76; Mar: 23.5; Apr: 23.54; May: 25.5; Jun: 33.62; Jul: 45.5; Aug: 47.48; Sep: 44.8; Oct: 37.22; Nov: 19.6; Dec: 18.9
AR | SILOAM SPRING(AWOS) | Jan: 36.8; Feb: 40.5; Mar: 48.8; Apr: 58.1; May: 66.3; Jun: 73.8; Jul: 79.1; Aug: 78.3; Sep: 69.6; Oct: 59.2; Nov: 48.4; Dec: 39; Jan: 27; Feb: 33.8; Mar: 35.4; Apr: 44.78; May: 57.2; Jun: 63.86; Jul: 67.46; Aug: 61.7; Sep: 58.3; Oct: 45.68; Nov: 40.5; Dec: 26.1
MN | SILVER BAY | Jan: 10.5; Feb: 14.3; Mar: 24.5; Apr: 36.8; May: 48.1; Jun: 57.7; Jul: 63.8; Aug: 62.1; Sep: 53.7; Oct: 42; Nov: 28.4; Dec: 16.1; Jan: -0.8; Feb: -2.02; Mar: 22.3; Apr: 26.78; May: 28; Jun: 49.82; Jul: 53.24; Aug: 50.9; Sep: 50.5; Oct: 29.48; Nov: 16.7; Dec: 7.3
IA | SIOUX CITY SIOUX GATEWAY AP | Jan: 20.4; Feb: 25.5; Mar: 37; Apr: 49.6; May: 61.2; Jun: 70.8; Jul: 74.5; Aug: 72.4; Sep: 64; Oct: 51.3; Nov: 36.4; Dec: 24.1; Jan: 7.2; Feb: 20.48; Mar: 26.1; Apr: 38.3; May: 49.3; Jun: 56.66; Jul: 62.42; Aug: 62.42; Sep: 53.1; Oct: 37.58; Nov: 25.2; Dec: 12
SD | SIOUX FALLS FOSS FIELD | Jan: 17.1; Feb: 22; Mar: 33.5; Apr: 46.4; May: 58.2; Jun: 68.4; Jul: 73.2; Aug: 71.1; Sep: 62.4; Oct: 48.9; Nov: 33.6; Dec: 21; Jan: 4.5; Feb: 10.76; Mar: 25.3; Apr: 33.26; May: 47.7; Jun: 57.74; Jul: 62.6; Aug: 59; Sep: 49.8; Oct: 35.6; Nov: 24.8; Dec: 12.7
AK | SITKA JAPONSKI AP | Jan: 36; Feb: 36.6; Mar: 37.3; Apr: 42.5; May: 47.8; Jun: 52.8; Jul: 56.1; Aug: 57.1; Sep: 53.1; Oct: 46.1; Nov: 39.7; Dec: 37; Jan: 24.8; Feb: 19.04; Mar: 25.5; Apr: 27.14; May: 37.4; Jun: 46.22; Jul: 50.18; Aug: 51.08; Sep: 46.4; Oct: 36.86; Nov: 26.6; Dec: 20.7
AK | SKAGWAY AIRPORT | Jan: 26.5; Feb: 30.2; Mar: 32.2; Apr: 40.9; May: 49.4; Jun: 55.3; Jul: 57.2; Aug: 56.4; Sep: 50.7; Oct: 43; Nov: 33.1; Dec: 28.7; Jan: 21.9; Feb: 19.22; Mar: 24.1; Apr: 27.68; May: 36; Jun: 45.68; Jul: 47.66; Aug: 48.38; Sep: 40.3; Oct: 31.1; Nov: 24.6; Dec: 12.9
AK | SLEETMUTE | Jan: -2.6; Feb: 8.7; Mar: 14.2; Apr: 31.2; May: 45; Jun: 54.2; Jul: 56.4; Aug: 53.5; Sep: 45.6; Oct: 28.3; Nov: 12.6; Dec: 0.6; Jan: -9.4; Feb: 17.6; Mar: 7.9; Apr: 36.32; May: 30.4; Jun: 38.12; Jul: 41.72; Aug: 39.38; Sep: 32.7; Oct: 28.04; Nov: 13.5; Dec: 5.7
BC | SMITHERS AP | Jan: 18.8; Feb: 24.4; Mar: 31.3; Apr: 40.5; May: 48.9; Jun: 55.3; Jul: 59.2; Aug: 58.2; Sep: 50.4; Oct: 39.6; Nov: 28.3; Dec: 20.2; Jan: 15.6; Feb: 17.42; Mar: 20.8; Apr: 26.24; May: 34.2; Jun: 43.16; Jul: 48.74; Aug: 47.48; Sep: 42.3; Oct: 33.62; Nov: 25.2; Dec: 15.6
WA | SNOHOMISH CO | Jan: 41; Feb: 42.1; Mar: 44.7; Apr: 48.5; May: 53.7; Jun: 58.3; Jul: 62.9; Aug: 63.7; Sep: 59.7; Oct: 51.7; Nov: 44.7; Dec: 40.2; Jan: 39.9; Feb: 34.7; Mar: 38.5; Apr: 40.28; May: 45.9; Jun: 49.64; Jul: 52.7; Aug: 53.06; Sep: 51.4; Oct: 45.5; Nov: 41; Dec: 37
AK | SOLDOTNA | Jan: 12.2; Feb: 19.5; Mar: 23.2; Apr: 35.5; May: 44.6; Jun: 51.7; Jul: 55.9; Aug: 54.6; Sep: 46.9; Oct: 34.4; Nov: 21.2; Dec: 15.4; Jan: 17.8; Feb: 26.42; Mar: 16.3; Apr: 27.68; May: 32.9; Jun: 39.56; Jul: 44.78; Aug: 39.38; Sep: 34.9; Oct: 26.78; Nov: 14.5; Dec: 20.5
KY | SOMERSET(AWOS) | Jan: 37.9; Feb: 40.6; Mar: 48.1; Apr: 58; May: 66.3; Jun: 74.2; Jul: 77.4; Aug: 76.7; Sep: 69.9; Oct: 58.4; Nov: 47.5; Dec: 39.8; Jan: 25.7; Feb: 30.4; Mar: 39.7; Apr: 47.5; May: 58.5; Jun: 63.9; Jul: 65.1; Aug: 65.3; Sep: 57.4; Oct: 41.7; Nov: 37.2; Dec: 29.5
IN | SOUTH BEND MICHIANA RGNL AP | Jan: 25.3; Feb: 28.2; Mar: 37.9; Apr: 49.3; May: 59.9; Jun: 69.5; Jul: 73; Aug: 71.4; Sep: 64; Oct: 52.7; Nov: 40.8; Dec: 30.2; Jan: 20.3; Feb: 20.48; Mar: 30; Apr: 35.6; May: 49.6; Jun: 55.94; Jul: 64.94; Aug: 63.86; Sep: 54.5; Oct: 42.08; Nov: 34.7; Dec: 23.5
CA | SOUTH LAKE TAHOE-LAKE TAHOE AP | Jan: 31; Feb: 31; Mar: 36; Apr: 40; May: 48; Jun: 56; Jul: 63; Aug: 61; Sep: 55; Oct: 46; Nov: 37; Dec: 31; Jan: 22.3; Feb: 18.14; Mar: 25.3; Apr: 25.7; May: 30; Jun: 30.74; Jul: 36.86; Aug: 36.86; Sep: 31.6; Oct: 25.7; Nov: 20.7; Dec: 20.3
MN | SOUTH ST PAUL MUNI | Jan: 16.8; Feb: 21.3; Mar: 32.8; Apr: 47.2; May: 59.1; Jun: 68.5; Jul: 74; Aug: 71.4; Sep: 63.3; Oct: 49.7; Nov: 35.3; Dec: 22; Jan: 7; Feb: 17.96; Mar: 22.3; Apr: 35.78; May: 41.9; Jun: 60.98; Jul: 64.4; Aug: 61.7; Sep: 55.8; Oct: 41.9; Nov: 25.5; Dec: 4.3
IL | SOUTHERN ILLINOIS | Jan: 33.9; Feb: 37.5; Mar: 46.8; Apr: 57.8; May: 66.9; Jun: 75.3; Jul: 77.9; Aug: 76.9; Sep: 68.6; Oct: 57.6; Nov: 46.8; Dec: 36.5; Jan: 19; Feb: 28.94; Mar: 38.5; Apr: 41.18; May: 63.5; Jun: 65.48; Jul: 68.9; Aug: 67.46; Sep: 61.5; Oct: 50; Nov: 41.9; Dec: 27
NC | SOUTHERN PINES AWOS | Jan: 42; Feb: 44.2; Mar: 52; Apr: 60.6; May: 68.8; Jun: 76.1; Jul: 79.7; Aug: 77.9; Sep: 71.6; Oct: 60.8; Nov: 51; Dec: 44.1; Jan: 31.3; Feb: 28.04; Mar: 28.2; Apr: 35.78; May: 45.7; Jun: 63.5; Jul: 66.92; Aug: 57.92; Sep: 48.2; Oct: 48.02; Nov: 35.1; Dec: 34.3
FL | SOUTHWEST FLORIDA I | Jan: 64.1; Feb: 66.2; Mar: 68.8; Apr: 73.1; May: 77.8; Jun: 81.3; Jul: 82.5; Aug: 82.9; Sep: 81.7; Oct: 77.3; Nov: 70.5; Dec: 66.3; Jan: 56.8; Feb: 60.98; Mar: 59.4; Apr: 64.76; May: 63.9; Jun: 73.94; Jul: 73.94; Aug: 74.84; Sep: 74.1; Oct: 65.3; Nov: 58.3; Dec: 56.1
IA | SPENCER | Jan: 17; Feb: 21.4; Mar: 33.3; Apr: 47; May: 58.8; Jun: 68.8; Jul: 72.7; Aug: 70; Sep: 62.2; Oct: 49.1; Nov: 34.4; Dec: 21.1; Jan: 10.2; Feb: 18.32; Mar: 24.4; Apr: 39.56; May: 45; Jun: 54.68; Jul: 63.5; Aug: 60.26; Sep: 50.4; Oct: 35.42; Nov: 28.8; Dec: 3.2
WA | SPOKANE INTERNATIONAL AP [CHENEY - UO] | Jan: 29.3; Feb: 32.6; Mar: 39.7; Apr: 46.3; May: 54.8; Jun: 61.1; Jul: 70.4; Aug: 69.4; Sep: 61.1; Oct: 47.5; Nov: 35.7; Dec: 28.3; Jan: 23.5; Feb: 23.18; Mar: 28.4; Apr: 32; May: 37.6; Jun: 40.28; Jul: 44.78; Aug: 43.34; Sep: 39; Oct: 36.32; Nov: 30.2; Dec: 25.9
AB | SPRINGBANK | Jan: 15.1; Feb: 20.8; Mar: 25.9; Apr: 37.1; May: 45.7; Jun: 52.5; Jul: 57.3; Aug: 57.3; Sep: 49.6; Oct: 38.1; Nov: 24.8; Dec: 16.6; Jan: 9; Feb: 10.4; Mar: 15.4; Apr: 22.82; May: 30.7; Jun: 41.54; Jul: 46.4; Aug: 43.88; Sep: 36.1; Oct: 25.88; Nov: 17.1; Dec: 9.9
AR | SPRINGDALE MUNI | Jan: 36.1; Feb: 38.3; Mar: 48.9; Apr: 57.5; May: 65.5; Jun: 74.3; Jul: 78; Aug: 78.1; Sep: 69.4; Oct: 58.1; Nov: 48.1; Dec: 38.3; Jan: 24.8; Feb: 27.5; Mar: 36.7; Apr: 46.4; May: 54.9; Jun: 63.32; Jul: 65.48; Aug: 67.1; Sep: 57.2; Oct: 46.4; Nov: 37.4; Dec: 27.7
IL | SPRINGFIELD CAPITAL AP | Jan: 27.6; Feb: 32.2; Mar: 42.8; Apr: 54; May: 64.1; Jun: 72.7; Jul: 75.7; Aug: 74.5; Sep: 66.7; Oct: 55.4; Nov: 43.3; Dec: 32.1; Jan: 14; Feb: 18.32; Mar: 36.1; Apr: 43.88; May: 51.8; Jun: 60.44; Jul: 65.66; Aug: 65.48; Sep: 55.9; Oct: 40.46; Nov: 32.9; Dec: 23.9
MO | SPRINGFIELD REGIONAL ARPT | Jan: 33.8; Feb: 38.3; Mar: 46.7; Apr: 56.3; May: 65.1; Jun: 73.9; Jul: 78.2; Aug: 77.7; Sep: 68.9; Oct: 57.8; Nov: 46.3; Dec: 36.3; Jan: 24.8; Feb: 21.92; Mar: 33.8; Apr: 44.6; May: 53.4; Jun: 63.86; Jul: 64.22; Aug: 64.94; Sep: 56.1; Oct: 48.02; Nov: 31.3; Dec: 27.7
VT | SPRINGFIELD/HARTNES | Jan: 20.8; Feb: 23.9; Mar: 31.8; Apr: 44.6; May: 55.8; Jun: 64.7; Jul: 69.5; Aug: 67.8; Sep: 60.3; Oct: 48; Nov: 37.5; Dec: 27.3; Jan: 13.1; Feb: 13.46; Mar: 27.7; Apr: 32.18; May: 45.3; Jun: 54.86; Jul: 57.02; Aug: 57.74; Sep: 53.8; Oct: 43.16; Nov: 29.7; Dec: 25.9
QC | ST ANICET | Jan: 15.8; Feb: 18.1; Mar: 28.7; Apr: 43.2; May: 55.7; Jun: 65.5; Jul: 69.1; Aug: 66.7; Sep: 59.5; Oct: 47.7; Nov: 36.4; Dec: 23.6; Jan: 7.5; Feb: 9.5; Mar: 19.6; Apr: 31.64; May: 42.8; Jun: 55.4; Jul: 60.44; Aug: 59.9; Sep: 52.7; Oct: 40.46; Nov: 31.1; Dec: 15.6
MN | ST CLOUD REGIONAL ARPT | Jan: 12.1; Feb: 17; Mar: 29.3; Apr: 43.9; May: 56.2; Jun: 66; Jul: 70.3; Aug: 68.1; Sep: 59.4; Oct: 46.3; Nov: 31.1; Dec: 17.7; Jan: 0.1; Feb: 7.88; Mar: 20.3; Apr: 27.32; May: 43.9; Jun: 55.58; Jul: 60.8; Aug: 57.38; Sep: 48.7; Oct: 36.32; Nov: 24.1; Dec: 5
MO | ST JOSEPH ROSECRANS MEMORIAL | Jan: 27.7; Feb: 32; Mar: 43.3; Apr: 54.7; May: 65.1; Jun: 73.8; Jul: 77.7; Aug: 76; Sep: 67.3; Oct: 55.6; Nov: 42.8; Dec: 30.5; Jan: 19.9; Feb: 22.82; Mar: 21.9; Apr: 36.32; May: 49.1; Jun: 64.22; Jul: 69.98; Aug: 69.8; Sep: 55.8; Oct: 42.26; Nov: 30.2; Dec: 28.4
MO | ST LOUIS LAMBERT INT ARPT | Jan: 32.6; Feb: 37; Mar: 46.9; Apr: 57.7; May: 67.2; Jun: 76.2; Jul: 80.1; Aug: 78.9; Sep: 70.4; Oct: 59; Nov: 46.8; Dec: 36.2; Jan: 18; Feb: 22.82; Mar: 35.8; Apr: 41; May: 53.4; Jun: 59.9; Jul: 64.22; Aug: 65.3; Sep: 55.9; Oct: 45.14; Nov: 35.6; Dec: 24.1
MO | ST LOUIS SPIRIT OF ST LOUIS A | Jan: 31.9; Feb: 36.2; Mar: 46; Apr: 56.3; May: 65.6; Jun: 74.3; Jul: 78.3; Aug: 76.8; Sep: 68.1; Oct: 57; Nov: 45.4; Dec: 35.2; Jan: 23.7; Feb: 21.92; Mar: 31.8; Apr: 47.12; May: 54.7; Jun: 62.96; Jul: 65.3; Aug: 67.82; Sep: 52.2; Oct: 47.3; Nov: 40.5; Dec: 31.8
FL | ST LUCIE CO INTL | Jan: 61.5; Feb: 64.6; Mar: 67.5; Apr: 71.4; May: 76.3; Jun: 79.9; Jul: 81.1; Aug: 81.6; Sep: 80.1; Oct: 75.8; Nov: 69.2; Dec: 65.3; Jan: 47.1; Feb: 57.38; Mar: 55.4; Apr: 56.3; May: 65.8; Jun: 73.22; Jul: 73.76; Aug: 74.3; Sep: 71.1; Oct: 63.5; Nov: 59; Dec: 56.1
MN | ST PAUL DOWNTOWN AP | Jan: 15.9; Feb: 20.7; Mar: 32.7; Apr: 47.2; May: 59; Jun: 68.7; Jul: 73.6; Aug: 71.3; Sep: 62.7; Oct: 49.7; Nov: 34.8; Dec: 21.5; Jan: -2.7; Feb: 14.9; Mar: 28.2; Apr: 30.2; May: 43.9; Jun: 57.92; Jul: 59.9; Aug: 62.06; Sep: 56.3; Oct: 36.14; Nov: 30; Dec: 11.5
AK | ST PAUL ISLAND ARPT | Jan: 24.4; Feb: 24; Mar: 24.4; Apr: 29.1; May: 35.8; Jun: 42.2; Jul: 47.1; Aug: 48.9; Sep: 45.5; Oct: 38.9; Nov: 33.6; Dec: 28.7; Jan: 24.3; Feb: 22.46; Mar: 22.3; Apr: 26.96; May: 32.2; Jun: 38.66; Jul: 44.42; Aug: 46.4; Sep: 42.1; Oct: 34.7; Nov: 25.7; Dec: 26.2
FL | ST PETERSBURG ALBERT WHITTED | Jan: 61.9; Feb: 64.5; Mar: 68.8; Apr: 74; May: 79.3; Jun: 82.9; Jul: 83.9; Aug: 84.4; Sep: 82.5; Oct: 77.6; Nov: 69.8; Dec: 64.9; Jan: 54; Feb: 55.76; Mar: 53.6; Apr: 58.1; May: 68.2; Jun: 73.04; Jul: 76.1; Aug: 74.84; Sep: 73.4; Oct: 71.24; Nov: 56.3; Dec: 62.1
FL | ST PETERSBURG CLEAR | Jan: 62.2; Feb: 63.8; Mar: 68.4; Apr: 73.3; May: 78.1; Jun: 81.7; Jul: 82.9; Aug: 83.8; Sep: 81.9; Oct: 76.9; Nov: 68.7; Dec: 65.6; Jan: 43.9; Feb: 52.34; Mar: 53.1; Apr: 58.82; May: 69.4; Jun: 72.86; Jul: 75.2; Aug: 74.66; Sep: 73.6; Oct: 65.48; Nov: 61; Dec: 54.7
MI | ST.CLAIR COUNTY INT | Jan: 24.7; Feb: 25.6; Mar: 34.3; Apr: 45.5; May: 56.4; Jun: 65.6; Jul: 69.6; Aug: 67.8; Sep: 61; Oct: 50.4; Nov: 39.7; Dec: 29.6; Jan: 14.7; Feb: 21.2; Mar: 30.9; Apr: 34.88; May: 49.6; Jun: 60.62; Jul: 60.8; Aug: 62.06; Sep: 54.3; Oct: 39.38; Nov: 34.9; Dec: 23.5
WA | STAMPEDE PASS | Jan: 27.4; Feb: 29.4; Mar: 33.4; Apr: 37.7; May: 44.2; Jun: 49.6; Jul: 57.1; Aug: 57.6; Sep: 53.2; Oct: 42; Nov: 32.6; Dec: 26.4; Jan: 28.2; Feb: 22.82; Mar: 26.2; Apr: 29.84; May: 35.6; Jun: 41.54; Jul: 45.68; Aug: 46.94; Sep: 41.5; Oct: 31.1; Nov: 27.1; Dec: 24.6
PA | STATE COLLEGE [PENN STATE - SURFRAD] | Jan: 27.6; Feb: 29.6; Mar: 38.1; Apr: 50.3; May: 59.3; Jun: 67.7; Jul: 71.2; Aug: 70.8; Sep: 63.4; Oct: 52; Nov: 42; Dec: 31; Jan: 20.1; Feb: 16.16; Mar: 24.6; Apr: 29.84; May: 41; Jun: 57.02; Jul: 60.08; Aug: 58.1; Sep: 49.5; Oct: 37.04; Nov: 33.3; Dec: 22.5
VA | STAUNTON/SHENANDOAH | Jan: 35.6; Feb: 37.6; Mar: 45.4; Apr: 55.5; May: 64.2; Jun: 72.7; Jul: 76; Aug: 74.7; Sep: 67.4; Oct: 56.2; Nov: 45.8; Dec: 38.1; Jan: 28.6; Feb: 24.44; Mar: 26.8; Apr: 32.36; May: 42.3; Jun: 54.86; Jul: 64.76; Aug: 69.98; Sep: 61.3; Oct: 42.44; Nov: 28; Dec: 30.6
QC | STE ANNE DE BELLEVUE | Jan: 15.4; Feb: 18.2; Mar: 28.5; Apr: 43.2; May: 56.3; Jun: 65.7; Jul: 69.7; Aug: 67.7; Sep: 60; Oct: 48.1; Nov: 35.9; Dec: 22.8; Jan: 6.4; Feb: 9.14; Mar: 18.3; Apr: 30.38; May: 42.6; Jun: 55.22; Jul: 59.54; Aug: 58.82; Sep: 52.3; Oct: 40.1; Nov: 30.4; Dec: 14.5
QC | STE FOY | Jan: 12.2; Feb: 16.5; Mar: 25.9; Apr: 40; May: 53.8; Jun: 62.5; Jul: 67.7; Aug: 65.9; Sep: 58; Oct: 45.5; Nov: 34; Dec: 20.2; Jan: 4.6; Feb: 7.16; Mar: 16.5; Apr: 27.14; May: 38.5; Jun: 50.72; Jul: 57.56; Aug: 56.48; Sep: 49.8; Oct: 37.76; Nov: 28; Dec: 14.2
IL | STERLING ROCKFALLS | Jan: 21.2; Feb: 25.4; Mar: 37; Apr: 49.6; May: 60.8; Jun: 70.1; Jul: 72.8; Aug: 70.9; Sep: 63.2; Oct: 52; Nov: 39; Dec: 26.8; Jan: 6.4; Feb: 23.36; Mar: 28; Apr: 39.2; May: 42.3; Jun: 55.76; Jul: 64.04; Aug: 58.82; Sep: 54.5; Oct: 39.56; Nov: 28.9; Dec: 23.7
NY | STEWART FIELD | Jan: 27.1; Feb: 30.1; Mar: 37.9; Apr: 49.3; May: 59; Jun: 68.6; Jul: 72.8; Aug: 71.7; Sep: 63.5; Oct: 52.2; Nov: 42.1; Dec: 32.6; Jan: 10.2; Feb: 18.32; Mar: 30.2; Apr: 30.2; May: 43.2; Jun: 57.56; Jul: 62.24; Aug: 57.02; Sep: 53.6; Oct: 42.08; Nov: 33.4; Dec: 27
OK | STILLWATER RGNL | Jan: 38.4; Feb: 41.9; Mar: 50.9; Apr: 60.3; May: 69; Jun: 77.6; Jul: 82.9; Aug: 82.4; Sep: 73.6; Oct: 61.6; Nov: 50; Dec: 39.6; Jan: 28; Feb: 27.68; Mar: 40.3; Apr: 51.62; May: 59.9; Jun: 64.58; Jul: 69.44; Aug: 66.2; Sep: 54; Oct: 47.48; Nov: 42.3; Dec: 28.9
CA | STOCKTON METROPOLITAN ARPT | Jan: 47; Feb: 50.9; Mar: 55.7; Apr: 59.9; May: 66.7; Jun: 72.7; Jul: 77.1; Aug: 76.4; Sep: 73; Oct: 64.5; Nov: 53.9; Dec: 46.7; Jan: 41.7; Feb: 42.62; Mar: 48.2; Apr: 47.3; May: 45.5; Jun: 52.88; Jul: 52.16; Aug: 52.7; Sep: 54.1; Oct: 47.48; Nov: 43.7; Dec: 41.2
IA | STORM LAKE | Jan: 20.3; Feb: 23.7; Mar: 35.8; Apr: 49.4; May: 61.1; Jun: 70.7; Jul: 74.4; Aug: 71.6; Sep: 64; Oct: 51.7; Nov: 37.2; Dec: 23.7; Jan: 17.2; Feb: 11.12; Mar: 22.1; Apr: 39.02; May: 39.6; Jun: 55.58; Jul: 61.88; Aug: 67.46; Sep: 51.8; Oct: 38.66; Nov: 24.4; Dec: 17.2
WI | STURGEON BAY | Jan: 19.2; Feb: 21.4; Mar: 30.2; Apr: 41.9; May: 53.2; Jun: 63.4; Jul: 68.5; Aug: 67.4; Sep: 60.1; Oct: 48.9; Nov: 36.6; Dec: 25.6; Jan: 12.7; Feb: 17.42; Mar: 20.3; Apr: 31.46; May: 37; Jun: 52.88; Jul: 54.5; Aug: 59; Sep: 53.6; Oct: 39.74; Nov: 28.9; Dec: 20.8
AR | STUTTGART (AWOS) | Jan: 41.7; Feb: 45.5; Mar: 53.3; Apr: 62.9; May: 71.8; Jun: 79.8; Jul: 82.2; Aug: 81.1; Sep: 73.6; Oct: 63.1; Nov: 52.1; Dec: 44.2; Jan: 36; Feb: 37.94; Mar: 38.3; Apr: 49.28; May: 61.7; Jun: 68; Jul: 72.68; Aug: 69.44; Sep: 65.7; Oct: 54.14; Nov: 43; Dec: 31.6
ON | SUDBURY AP | Jan: 9.7; Feb: 12.9; Mar: 23.9; Apr: 38.4; May: 52.3; Jun: 62.3; Jul: 66; Aug: 64.3; Sep: 55.7; Oct: 43.4; Nov: 30.5; Dec: 17.8; Jan: 4.5; Feb: 5.72; Mar: 13.6; Apr: 25.52; May: 38.1; Jun: 50.72; Jul: 55.04; Aug: 54.5; Sep: 49.3; Oct: 37.04; Nov: 27.1; Dec: 12.7
BC | SUMMERLAND | Jan: 29.6; Feb: 32.8; Mar: 40.4; Apr: 48; May: 56.6; Jun: 63.1; Jul: 70.9; Aug: 69.7; Sep: 60.8; Oct: 48.1; Nov: 36.6; Dec: 30.2; Jan: 19.6; Feb: 23; Mar: 27.1; Apr: 30.38; May: 37.6; Jun: 43.34; Jul: 45.86; Aug: 45.5; Sep: 41; Oct: 35.42; Nov: 28.2; Dec: 19.4
SC | SUMTER SHAW AFB | Jan: 45.8; Feb: 49; Mar: 55.6; Apr: 63.7; May: 71.6; Jun: 78.2; Jul: 81.3; Aug: 79.8; Sep: 74.5; Oct: 64.6; Nov: 54.6; Dec: 48.2; Jan: 30.4; Feb: 34.16; Mar: 35.4; Apr: 43.7; May: 51.3; Jun: 66.56; Jul: 72.5; Aug: 68.9; Sep: 62.8; Oct: 46.22; Nov: 39.4; Dec: 33.3
NS | SYDNEY AP | Jan: 23; Feb: 21.9; Mar: 28.1; Apr: 36.7; May: 46.1; Jun: 56; Jul: 64.7; Aug: 65; Sep: 58.1; Oct: 48.1; Nov: 39.4; Dec: 30.5; Jan: 17.4; Feb: 15.44; Mar: 20.8; Apr: 28.76; May: 37; Jun: 47.66; Jul: 56.66; Aug: 57.38; Sep: 51.1; Oct: 42.26; Nov: 35.2; Dec: 25.3
NY | SYRACUSE HANCOCK INT ARPT | Jan: 24.8; Feb: 25.9; Mar: 34.3; Apr: 46.9; May: 58.2; Jun: 67.4; Jul: 71.8; Aug: 70.4; Sep: 62.7; Oct: 51.5; Nov: 40.9; Dec: 30.6; Jan: 18.1; Feb: 17.06; Mar: 25.9; Apr: 37.4; May: 48.4; Jun: 55.22; Jul: 60.98; Aug: 59.54; Sep: 51.8; Oct: 41.9; Nov: 32.2; Dec: 20.5
WA | TACOMA MCCHORD AFB | Jan: 40; Feb: 41.5; Mar: 44.9; Apr: 48.8; May: 54.8; Jun: 59.7; Jul: 65; Aug: 65.1; Sep: 60; Oct: 51; Nov: 43.9; Dec: 39.2; Jan: 34; Feb: 30.92; Mar: 33.8; Apr: 34.7; May: 42.4; Jun: 46.04; Jul: 52.34; Aug: 52.88; Sep: 47.7; Oct: 41; Nov: 33.8; Dec: 36
WA | TACOMA NARROWS | Jan: 41.9; Feb: 43; Mar: 45.8; Apr: 49.7; May: 55.3; Jun: 60; Jul: 65; Aug: 64.9; Sep: 61.1; Oct: 52.9; Nov: 45.4; Dec: 41.4; Jan: 38.1; Feb: 37.76; Mar: 37.8; Apr: 41; May: 43; Jun: 48.2; Jul: 51.98; Aug: 53.6; Sep: 52.3; Oct: 45.86; Nov: 42.1; Dec: 39.2
AK | TALKEETNA STATE ARPT | Jan: 13.8; Feb: 18.3; Mar: 23.9; Apr: 36; May: 47.5; Jun: 56.9; Jul: 59.6; Aug: 56.4; Sep: 47.4; Oct: 33.7; Nov: 19.4; Dec: 15.3; Jan: 11.8; Feb: 6.26; Mar: 14.9; Apr: 24.62; May: 34.2; Jun: 41; Jul: 49.28; Aug: 48.74; Sep: 42.1; Oct: 28.94; Nov: 10.4; Dec: 7.3
FL | TALLAHASSEE REGIONAL AP [ISIS] | Jan: 52.4; Feb: 55.3; Mar: 61; Apr: 67; May: 74.9; Jun: 80.5; Jul: 82.2; Aug: 82.1; Sep: 78.7; Oct: 69.6; Nov: 59.9; Dec: 54.1; Jan: 40.6; Feb: 42.08; Mar: 50.4; Apr: 53.96; May: 63.9; Jun: 71.6; Jul: 73.76; Aug: 71.06; Sep: 67.5; Oct: 56.48; Nov: 53.4; Dec: 42.4
FL | TAMPA INTERNATIONAL AP | Jan: 61.4; Feb: 63.6; Mar: 67.4; Apr: 72.6; May: 78.6; Jun: 82; Jul: 82.9; Aug: 83.1; Sep: 81.6; Oct: 76.1; Nov: 68.5; Dec: 63.7; Jan: 50.2; Feb: 53.6; Mar: 59.7; Apr: 60.26; May: 67.1; Jun: 71.42; Jul: 73.76; Aug: 73.58; Sep: 72.7; Oct: 65.66; Nov: 57.9; Dec: 50.2
AK | TANANA RALPH M CALHOUN MEM AP | Jan: -9.1; Feb: 0.2; Mar: 5.3; Apr: 26.9; May: 46; Jun: 58.3; Jul: 59.4; Aug: 53.7; Sep: 43; Oct: 25.4; Nov: 2.6; Dec: -5; Jan: -9.6; Feb: 3.38; Mar: 7.2; Apr: 13.64; May: 24.8; Jun: 41; Jul: 48.56; Aug: 40.28; Sep: 28.9; Oct: 26.42; Nov: 3; Dec: -0.8
NM | TAOS MUNI APT(AWOS) | Jan: 26; Feb: 30.8; Mar: 38.3; Apr: 44.6; May: 54; Jun: 63.5; Jul: 68.1; Aug: 66; Sep: 58.8; Oct: 47.1; Nov: 35; Dec: 25.4; Jan: 13.1; Feb: 24.8; Mar: 11.8; Apr: 22.64; May: 15.6; Jun: 28.76; Jul: 41.36; Aug: 41.9; Sep: 36; Oct: 17.96; Nov: 17.6; Dec: 11.8
NE | TEKAMAH (ASOS) | Jan: 21.6; Feb: 26.4; Mar: 38.4; Apr: 51.2; May: 62.5; Jun: 71.7; Jul: 76.1; Aug: 73; Sep: 64.8; Oct: 52.2; Nov: 38.6; Dec: 25.3; Jan: 14.9; Feb: 25.52; Mar: 31.6; Apr: 36.32; May: 52.2; Jun: 61.52; Jul: 65.66; Aug: 65.48; Sep: 56.7; Oct: 38.3; Nov: 32.4; Dec: 8.6
IN | TERRE HAUTE HULMAN REGIONAL A | Jan: 29.3; Feb: 33.2; Mar: 43.1; Apr: 54.2; May: 63.9; Jun: 72.8; Jul: 75.5; Aug: 73.8; Sep: 66.4; Oct: 55.3; Nov: 43.6; Dec: 33.3; Jan: 17.1; Feb: 24.62; Mar: 33.8; Apr: 46.76; May: 47.7; Jun: 63.14; Jul: 65.48; Aug: 71.42; Sep: 60.3; Oct: 44.24; Nov: 39.4; Dec: 28
NJ | TETERBORO AIRPORT | Jan: 32.3; Feb: 34.2; Mar: 41.7; Apr: 52.4; May: 62; Jun: 71.5; Jul: 76.6; Aug: 74.8; Sep: 67.6; Oct: 56.3; Nov: 46.3; Dec: 37.2; Jan: 19.8; Feb: 22.1; Mar: 30.6; Apr: 32.18; May: 51.1; Jun: 54.5; Jul: 60.8; Aug: 58.64; Sep: 50.9; Oct: 45.14; Nov: 37.2; Dec: 27.9
AR | TEXARKANA WEBB FIELD | Jan: 45.6; Feb: 49.2; Mar: 56.5; Apr: 64.4; May: 72.1; Jun: 79.7; Jul: 83.1; Aug: 83; Sep: 75.8; Oct: 65.4; Nov: 54.6; Dec: 46.9; Jan: 36.3; Feb: 41.18; Mar: 43.3; Apr: 57.92; May: 60.8; Jun: 66.74; Jul: 71.24; Aug: 69.08; Sep: 69.3; Oct: 59.36; Nov: 41.2; Dec: 37.4
WA | THE DALLES MUNICIPAL ARPT | Jan: 37.1; Feb: 40.4; Mar: 46.7; Apr: 52.4; May: 60.5; Jun: 66.7; Jul: 75; Aug: 74.1; Sep: 66.7; Oct: 54.7; Nov: 42.4; Dec: 36; Jan: 31.5; Feb: 31.28; Mar: 35.8; Apr: 39.92; May: 43.2; Jun: 47.84; Jul: 52.88; Aug: 51.44; Sep: 45.7; Oct: 40.28; Nov: 35.8; Dec: 34.3
MN | THIEF RIVER(AWOS) | Jan: 6.4; Feb: 10.9; Mar: 23.9; Apr: 40.5; May: 53.3; Jun: 63.2; Jul: 67.2; Aug: 65.8; Sep: 56.8; Oct: 43.7; Nov: 27.2; Dec: 12.4; Jan: 1.9; Feb: 15.08; Mar: 6.8; Apr: 33.98; May: 35.1; Jun: 52.34; Jul: 60.26; Aug: 56.48; Sep: 48.4; Oct: 26.6; Nov: 29.3; Dec: 6.3
ON | THUNDER BAY AP | Jan: 7.6; Feb: 12.2; Mar: 23.2; Apr: 36.8; May: 48.4; Jun: 58.4; Jul: 63.8; Aug: 62.9; Sep: 53.9; Oct: 41.6; Nov: 28.3; Dec: 14.7; Jan: 1.9; Feb: 3.2; Mar: 13.6; Apr: 25.88; May: 36.3; Jun: 49.28; Jul: 55.22; Aug: 54.86; Sep: 48.7; Oct: 34.7; Nov: 23.5; Dec: 8.2
ON | TIMMINS AP | Jan: 2.8; Feb: 7.2; Mar: 19.4; Apr: 34.7; May: 49.5; Jun: 59.8; Jul: 63.4; Aug: 61.2; Sep: 52.6; Oct: 40.4; Nov: 26.5; Dec: 11.9; Jan: -2; Feb: -0.58; Mar: 8.8; Apr: 21.56; May: 34.7; Jun: 46.94; Jul: 52.7; Aug: 52.34; Sep: 46.6; Oct: 33.62; Nov: 23.2; Dec: 7.2
AK | TOGIAK VILLAGE AWOS | Jan: 16.8; Feb: 19.8; Mar: 19.1; Apr: 31.4; May: 41.6; Jun: 49.7; Jul: 53.4; Aug: 52.6; Sep: 46.4; Oct: 34.7; Nov: 23.5; Dec: 18.2; Jan: 20.5; Feb: 30.2; Mar: 20.3; Apr: 21.02; May: 28.4; Jun: 39.2; Jul: 47.48; Aug: 44.96; Sep: 33.8; Oct: 30.2; Nov: 23.9; Dec: 17.8
OH | TOLEDO EXPRESS AIRPORT | Jan: 26.1; Feb: 28.4; Mar: 37.8; Apr: 49.6; May: 60.2; Jun: 70; Jul: 73.4; Aug: 71.6; Sep: 64.2; Oct: 52.8; Nov: 41.3; Dec: 30.9; Jan: 19; Feb: 17.6; Mar: 28.9; Apr: 37.4; May: 47.8; Jun: 57.2; Jul: 59.72; Aug: 60.08; Sep: 55.2; Oct: 39.2; Nov: 29.7; Dec: 18.5
NV | TONOPAH AIRPORT | Jan: 33.4; Feb: 36.8; Mar: 43.6; Apr: 49.4; May: 58.8; Jun: 68.3; Jul: 75.2; Aug: 73; Sep: 65.4; Oct: 53.3; Nov: 40.9; Dec: 32; Jan: 20.1; Feb: 19.58; Mar: 21.7; Apr: 20.84; May: 25.3; Jun: 28.4; Jul: 31.82; Aug: 35.6; Sep: 30.4; Oct: 28.22; Nov: 21.9; Dec: 19.9
KS | TOPEKA FORBES FIELD | Jan: 30.1; Feb: 34.2; Mar: 45.2; Apr: 55.1; May: 64.9; Jun: 74; Jul: 79; Aug: 77.5; Sep: 68.5; Oct: 56.4; Nov: 44; Dec: 32.9; Jan: 23.9; Feb: 19.4; Mar: 38.7; Apr: 45.14; May: 53.2; Jun: 66.38; Jul: 70.34; Aug: 64.58; Sep: 62.4; Oct: 42.08; Nov: 35.8; Dec: 21.4
KS | TOPEKA MUNICIPAL AP | Jan: 30.3; Feb: 35.1; Mar: 45.2; Apr: 55.3; May: 65.5; Jun: 75; Jul: 79.6; Aug: 78.1; Sep: 68.7; Oct: 57.2; Nov: 44.2; Dec: 33.4; Jan: 18.1; Feb: 24.26; Mar: 32; Apr: 44.96; May: 55.9; Jun: 61.7; Jul: 65.84; Aug: 64.94; Sep: 59.2; Oct: 46.58; Nov: 32.5; Dec: 19.4
ON | TORONTO | Jan: 25.2; Feb: 26.3; Mar: 35.1; Apr: 46.6; May: 57.9; Jun: 67.7; Jul: 72.8; Aug: 71.6; Sep: 64.4; Oct: 51.9; Nov: 41.5; Dec: 31.3; Jan: 16.3; Feb: 16.52; Mar: 22.5; Apr: 31.64; May: 42.4; Jun: 54.32; Jul: 58.46; Aug: 58.46; Sep: 53.4; Oct: 41.9; Nov: 33.1; Dec: 21.6
ON | TORONTO AP | Jan: 21.7; Feb: 22.7; Mar: 31.7; Apr: 44.1; May: 55.7; Jun: 66; Jul: 70.2; Aug: 68.7; Sep: 60.7; Oct: 48.9; Nov: 38; Dec: 27.8; Jan: 14.7; Feb: 15.08; Mar: 21.6; Apr: 31.28; May: 42.3; Jun: 53.6; Jul: 57.38; Aug: 57.56; Sep: 52; Oct: 41; Nov: 32.4; Dec: 20.7
ON | TORONTO ISLAND AP | Jan: 25.7; Feb: 27.1; Mar: 33.8; Apr: 43.9; May: 54.4; Jun: 64.6; Jul: 69.4; Aug: 69.8; Sep: 63; Oct: 50.9; Nov: 40.6; Dec: 31.5; Jan: 18; Feb: 17.96; Mar: 23.4; Apr: 32.72; May: 43.3; Jun: 55.04; Jul: 59.9; Aug: 60.98; Sep: 55.6; Oct: 43.16; Nov: 34.3; Dec: 23.2
MI | TRAVERSE CITY CHERRY CAPITAL | Jan: 23; Feb: 23.6; Mar: 32; Apr: 43.5; May: 54.7; Jun: 65.3; Jul: 69.5; Aug: 68.4; Sep: 60.7; Oct: 49.4; Nov: 38.2; Dec: 28.4; Jan: 14.5; Feb: 15.62; Mar: 20.8; Apr: 28.58; May: 41.9; Jun: 51.62; Jul: 59.72; Aug: 55.76; Sep: 50.5; Oct: 37.4; Nov: 30; Dec: 17.8
CA | TRAVIS FIELD AFB | Jan: 47.2; Feb: 50.9; Mar: 55.2; Apr: 58.7; May: 64.3; Jun: 69.6; Jul: 72.6; Aug: 73; Sep: 71.5; Oct: 64.7; Nov: 54.4; Dec: 47.2; Jan: 35.8; Feb: 39.56; Mar: 41.9; Apr: 42.8; May: 45.9; Jun: 50.72; Jul: 52.88; Aug: 51.44; Sep: 50; Oct: 45.5; Nov: 36.7; Dec: 37.6
ON | TRENTON AP | Jan: 20.1; Feb: 21.8; Mar: 30.7; Apr: 43.7; May: 54.9; Jun: 65; Jul: 69.1; Aug: 67.8; Sep: 59.9; Oct: 48.5; Nov: 37.6; Dec: 26.8; Jan: 13.3; Feb: 13.64; Mar: 21; Apr: 32.54; May: 44.4; Jun: 55.94; Jul: 60.08; Aug: 60.26; Sep: 54.1; Oct: 41.72; Nov: 32.2; Dec: 19.9
NJ | TRENTON MERCER COUNTY AP | Jan: 32.1; Feb: 34.2; Mar: 42.7; Apr: 52.7; May: 62.4; Jun: 71.3; Jul: 76.2; Aug: 74.4; Sep: 67.2; Oct: 55.7; Nov: 46.3; Dec: 36.8; Jan: 18.7; Feb: 19.94; Mar: 31.8; Apr: 43.52; May: 47.8; Jun: 58.28; Jul: 62.06; Aug: 65.84; Sep: 58.3; Oct: 43.88; Nov: 38.7; Dec: 25.2
CO | TRINIDAD LAS ANIMAS COUNTY AP | Jan: 33.2; Feb: 35.6; Mar: 43.1; Apr: 50; May: 59.7; Jun: 69.6; Jul: 73.9; Aug: 71.9; Sep: 64.9; Oct: 53.1; Nov: 41; Dec: 32.3; Jan: 14.4; Feb: 22.1; Mar: 25.2; Apr: 26.78; May: 32.4; Jun: 42.98; Jul: 49.64; Aug: 46.94; Sep: 39.7; Oct: 27.86; Nov: 24.6; Dec: 15.4
QC | TROIS RIVIERES | Jan: 13.6; Feb: 16.3; Mar: 26.6; Apr: 40.3; May: 54.1; Jun: 64.4; Jul: 69; Aug: 67.5; Sep: 59.5; Oct: 47.4; Nov: 35.2; Dec: 22.3; Jan: 5.4; Feb: 8.6; Mar: 17.8; Apr: 29.12; May: 41.9; Jun: 54.14; Jul: 60.08; Aug: 58.82; Sep: 52.2; Oct: 39.92; Nov: 30.2; Dec: 13.6
AL | TROY AIR FIELD | Jan: 47; Feb: 52; Mar: 58; Apr: 65; May: 72; Jun: 79; Jul: 81; Aug: 80; Sep: 76; Oct: 66; Nov: 56; Dec: 50; Jan: 39; Feb: 44.96; Mar: 46; Apr: 48.74; May: 64; Jun: 68.54; Jul: 70.88; Aug: 70.34; Sep: 67.5; Oct: 64.04; Nov: 43.7; Dec: 35.4
CA | TRUCKEE-TAHOE | Jan: 27.9; Feb: 30.7; Mar: 34.8; Apr: 39.6; May: 48; Jun: 54.9; Jul: 62.8; Aug: 60.9; Sep: 54.3; Oct: 44.8; Nov: 36.6; Dec: 29; Jan: 25.2; Feb: 25.52; Mar: 25.7; Apr: 24.44; May: 32; Jun: 36.5; Jul: 41; Aug: 32.36; Sep: 32.2; Oct: 29.84; Nov: 22.3; Dec: 22.3
NM | TRUTH OR CONSEQUENCES MUNI AP | Jan: 42.6; Feb: 46.9; Mar: 53.6; Apr: 61; May: 70.1; Jun: 79; Jul: 79.9; Aug: 77.7; Sep: 72; Oct: 62.1; Nov: 49.9; Dec: 41.6; Jan: 19; Feb: 22.1; Mar: 16.3; Apr: 24.08; May: 22.3; Jun: 37.58; Jul: 53.6; Aug: 54.5; Sep: 43.9; Oct: 37.4; Nov: 24.4; Dec: 21.9
AZ | TUCSON INTERNATIONAL AP | Jan: 53.3; Feb: 55.6; Mar: 61.3; Apr: 67.6; May: 76.7; Jun: 85.8; Jul: 87.5; Aug: 86; Sep: 82.4; Oct: 72.1; Nov: 61; Dec: 52.5; Jan: 22.3; Feb: 35.42; Mar: 29.1; Apr: 30.2; May: 28.8; Jun: 39.56; Jul: 57.02; Aug: 57.56; Sep: 52.3; Oct: 40.64; Nov: 31.6; Dec: 30.2
NM | TUCUMCARI AP | Jan: 39; Feb: 42; Mar: 51; Apr: 59; May: 67; Jun: 78; Jul: 81; Aug: 79; Sep: 72; Oct: 60; Nov: 48; Dec: 39; Jan: 19.8; Feb: 26.6; Mar: 25; Apr: 31.46; May: 44.4; Jun: 52.34; Jul: 57.56; Aug: 59.36; Sep: 52.9; Oct: 41; Nov: 28.8; Dec: 23.4
OK | TULSA INTERNATIONAL AIRPORT | Jan: 38.8; Feb: 43.1; Mar: 51.7; Apr: 60.8; May: 69.5; Jun: 78.3; Jul: 83.2; Aug: 82.6; Sep: 73.4; Oct: 62.2; Nov: 50.6; Dec: 40.6; Jan: 22.8; Feb: 27.14; Mar: 36.9; Apr: 47.48; May: 55.6; Jun: 67.64; Jul: 69.8; Aug: 68.54; Sep: 60.4; Oct: 48.92; Nov: 34.5; Dec: 24.3
MS | TUPELO C D LEMONS ARPT | Jan: 42.6; Feb: 46.4; Mar: 54; Apr: 62.4; May: 70.6; Jun: 78; Jul: 81; Aug: 80.5; Sep: 74; Oct: 63; Nov: 52.1; Dec: 44.8; Jan: 32.4; Feb: 38.84; Mar: 45.1; Apr: 52.7; May: 55.9; Jun: 67.1; Jul: 73.04; Aug: 65.84; Sep: 63.5; Oct: 48.02; Nov: 43.2; Dec: 34.5
AL | TUSCALOOSA MUNICIPAL AP | Jan: 45.4; Feb: 49.3; Mar: 56.4; Apr: 64.1; May: 71.9; Jun: 78.9; Jul: 81.6; Aug: 81.3; Sep: 75.5; Oct: 64.5; Nov: 54.1; Dec: 47.8; Jan: 39.6; Feb: 39.02; Mar: 37.6; Apr: 56.66; May: 65.5; Jun: 65.48; Jul: 70.7; Aug: 67.46; Sep: 68; Oct: 50.36; Nov: 52.3; Dec: 28.8
CA | TWENTYNINE PALMS | Jan: 51; Feb: 54; Mar: 61; Apr: 67; May: 75; Jun: 85; Jul: 90; Aug: 89; Sep: 82; Oct: 70; Nov: 58; Dec: 50; Jan: 29.5; Feb: 23.18; Mar: 32.2; Apr: 35.6; May: 38.1; Jun: 48.02; Jul: 49.64; Aug: 48.02; Sep: 48.2; Oct: 34.34; Nov: 30; Dec: 20.5
MN | TWO HARBORS MUNI AP | Jan: 12; Feb: 15; Mar: 27; Apr: 39; May: 50; Jun: 60; Jul: 66; Aug: 64; Sep: 56; Oct: 44; Nov: 30; Dec: 18; Jan: 7.2; Feb: -0.94; Mar: 25.7; Apr: 29.48; May: 43.2; Jun: 54.68; Jul: 57.74; Aug: 56.3; Sep: 49.3; Oct: 29.66; Nov: 26.6; Dec: 14.7
TX | TYLER/POUNDS FLD | Jan: 48; Feb: 51.2; Mar: 58.8; Apr: 66.5; May: 73.9; Jun: 80.9; Jul: 83.8; Aug: 84.7; Sep: 78; Oct: 67.5; Nov: 57.5; Dec: 48.7; Jan: 37; Feb: 40.28; Mar: 43.2; Apr: 54.14; May: 58.5; Jun: 69.8; Jul: 72.32; Aug: 66.2; Sep: 60.8; Oct: 60.26; Nov: 40.3; Dec: 36.3
FL | TYNDALL AFB | Jan: 53.1; Feb: 56.2; Mar: 61; Apr: 67.2; May: 74.5; Jun: 79.9; Jul: 81.9; Aug: 81.8; Sep: 79; Oct: 70.9; Nov: 61.4; Dec: 55.6; Jan: 39.4; Feb: 46.22; Mar: 46.9; Apr: 55.22; May: 63.3; Jun: 69.62; Jul: 73.58; Aug: 72.86; Sep: 70.2; Oct: 56.3; Nov: 48.7; Dec: 43.2
CA | UKIAH MUNICIPAL AP | Jan: 47; Feb: 48.9; Mar: 52.6; Apr: 55.2; May: 61.9; Jun: 68.2; Jul: 74.3; Aug: 73.3; Sep: 69.6; Oct: 61.1; Nov: 51.6; Dec: 46.1; Jan: 40.6; Feb: 42.44; Mar: 38.8; Apr: 41.9; May: 43.3; Jun: 46.4; Jul: 52.34; Aug: 52.34; Sep: 47.5; Oct: 42.62; Nov: 40.3; Dec: 40.3
AK | UNALAKLEET FIELD | Jan: 5.8; Feb: 10.5; Mar: 11.4; Apr: 25; May: 38.3; Jun: 49.4; Jul: 55.3; Aug: 52.5; Sep: 44.4; Oct: 28.2; Nov: 13.5; Dec: 9.8; Jan: 0.3; Feb: 6.98; Mar: 11.3; Apr: 18.86; May: 29.3; Jun: 37.22; Jul: 44.42; Aug: 40.64; Sep: 31.6; Oct: 28.22; Nov: 12.9; Dec: 6.6
IL | UNIV OF ILLINOIS WI [BONDVILLE - SURFRAD] | Jan: 26; Feb: 30.3; Mar: 40.9; Apr: 52.6; May: 63.2; Jun: 71.8; Jul: 74.2; Aug: 72.3; Sep: 66.1; Oct: 54.2; Nov: 41.6; Dec: 30.3; Jan: 16.3; Feb: 23; Mar: 32.4; Apr: 47.12; May: 51.1; Jun: 63.68; Jul: 65.48; Aug: 66.56; Sep: 55.2; Oct: 42.44; Nov: 38.3; Dec: 20.3
NY | UTICA ONEIDA COUNTY AP | Jan: 22.6; Feb: 24.5; Mar: 32.3; Apr: 45.2; May: 56.4; Jun: 66; Jul: 69.8; Aug: 68.8; Sep: 60.8; Oct: 49.4; Nov: 39.2; Dec: 28.6; Jan: 19.9; Feb: 20.48; Mar: 22.8; Apr: 29.12; May: 51.1; Jun: 56.48; Jul: 59.72; Aug: 59.36; Sep: 55; Oct: 44.6; Nov: 32.9; Dec: 18.7
AK | VALDEZ PIONEER FIEL | Jan: 23.8; Feb: 26.4; Mar: 30.7; Apr: 39.1; May: 47.2; Jun: 54.2; Jul: 55.8; Aug: 54.2; Sep: 47.4; Oct: 38.7; Nov: 29.4; Dec: 25.8; Jan: 28.2; Feb: 26.06; Mar: 25.3; Apr: 23.9; May: 33.4; Jun: 39.92; Jul: 48.02; Aug: 44.24; Sep: 32.2; Oct: 28.04; Nov: 27.5; Dec: 24.1
AK | VALDEZ WSO | Jan: 22.3; Feb: 25.3; Mar: 28; Apr: 36.5; May: 45.7; Jun: 52; Jul: 54.1; Aug: 52.6; Sep: 47.3; Oct: 38.7; Nov: 27.6; Dec: 24.2; Jan: 15.3; Feb: 19.76; Mar: 21.2; Apr: 31.82; May: 39.9; Jun: 45.32; Jul: 48.74; Aug: 48.2; Sep: 43.7; Oct: 31.82; Nov: 11.7; Dec: 18.7
GA | VALDOSTA WB AIRPORT | Jan: 52.5; Feb: 55.7; Mar: 61.2; Apr: 67; May: 74.7; Jun: 80.3; Jul: 82.3; Aug: 81.9; Sep: 78; Oct: 69.2; Nov: 59.8; Dec: 54.4; Jan: 50.5; Feb: 39.74; Mar: 50.5; Apr: 62.06; May: 64; Jun: 71.78; Jul: 73.94; Aug: 74.66; Sep: 67.5; Oct: 61.88; Nov: 50.5; Dec: 41.5
NE | VALENTINE MILLER FIELD | Jan: 24.1; Feb: 27.3; Mar: 36.6; Apr: 46.4; May: 57.4; Jun: 67.6; Jul: 74.5; Aug: 72.9; Sep: 63.1; Oct: 48.7; Nov: 35.1; Dec: 25.2; Jan: 16.5; Feb: 22.46; Mar: 23.5; Apr: 31.46; May: 40.8; Jun: 52.7; Jul: 56.84; Aug: 54.68; Sep: 45; Oct: 37.76; Nov: 25.3; Dec: 17.2
FL | VALPARAISO EGLIN AFB | Jan: 51.5; Feb: 55.1; Mar: 60.1; Apr: 66.5; May: 74.4; Jun: 80.1; Jul: 81.8; Aug: 81.6; Sep: 78.5; Oct: 69.6; Nov: 59.8; Dec: 53.8; Jan: 37.6; Feb: 44.42; Mar: 45.1; Apr: 53.24; May: 66.6; Jun: 71.06; Jul: 73.4; Aug: 70.88; Sep: 68.4; Oct: 52.16; Nov: 47.3; Dec: 37.2
FL | VALPARAISO HURLBURT | Jan: 52.2; Feb: 54.8; Mar: 59.7; Apr: 66; May: 73.6; Jun: 79.8; Jul: 81.7; Aug: 81.4; Sep: 78; Oct: 69.3; Nov: 59.4; Dec: 54.9; Jan: 39.7; Feb: 45.32; Mar: 45.3; Apr: 59.18; May: 67.3; Jun: 70.7; Jul: 75.56; Aug: 71.96; Sep: 68.9; Oct: 54.32; Nov: 46.9; Dec: 43.5
CA | VAN NUYS AIRPORT | Jan: 56.9; Feb: 55.9; Mar: 59.6; Apr: 61.7; May: 67.2; Jun: 70.8; Jul: 76.8; Aug: 77.7; Sep: 75.2; Oct: 67.9; Nov: 61.1; Dec: 55.5; Jan: 32.2; Feb: 45.32; Mar: 50.7; Apr: 48.02; May: 52.2; Jun: 55.04; Jul: 57.56; Aug: 58.1; Sep: 53.6; Oct: 50.54; Nov: 42.3; Dec: 35.8
OK | VANCE AFB | Jan: 36.1; Feb: 42.2; Mar: 49.6; Apr: 57.6; May: 68.1; Jun: 78.4; Jul: 82.7; Aug: 81.6; Sep: 72.6; Oct: 60.7; Nov: 47.5; Dec: 37.2; Jan: 31.1; Feb: 28.4; Mar: 26.8; Apr: 35.24; May: 56.8; Jun: 65.12; Jul: 63.68; Aug: 61.16; Sep: 48.6; Oct: 40.82; Nov: 34.2; Dec: 26.2
BC | VANCOUVER | Jan: 39.4; Feb: 40.8; Mar: 44.2; Apr: 48.9; May: 55.1; Jun: 60; Jul: 64.5; Aug: 64.6; Sep: 59.2; Oct: 50.7; Nov: 43.6; Dec: 38.8; Jan: 35.4; Feb: 35.06; Mar: 36.9; Apr: 40.28; May: 45.9; Jun: 50.36; Jul: 54.86; Aug: 55.22; Sep: 51.8; Oct: 45.5; Nov: 39.2; Dec: 34.5
QC | VARENNES | Jan: 14.8; Feb: 17.7; Mar: 28; Apr: 42.7; May: 56.1; Jun: 65.5; Jul: 69; Aug: 66.9; Sep: 59.3; Oct: 47.5; Nov: 35.6; Dec: 22.7; Jan: 5.7; Feb: 8.42; Mar: 18.9; Apr: 30.56; May: 41.5; Jun: 53.96; Jul: 59.54; Aug: 58.28; Sep: 51.6; Oct: 39.56; Nov: 30.6; Dec: 14
UT | VERNAL | Jan: 18.1; Feb: 26.5; Mar: 39.3; Apr: 47.2; May: 57; Jun: 66.3; Jul: 74.4; Aug: 70.7; Sep: 61.5; Oct: 48.5; Nov: 34.8; Dec: 20.6; Jan: 19.4; Feb: 21.38; Mar: 25.9; Apr: 28.76; May: 34; Jun: 36.86; Jul: 42.08; Aug: 39.56; Sep: 48.7; Oct: 24.26; Nov: 24.8; Dec: 14.7
BC | VERNON | Jan: 26.8; Feb: 30.7; Mar: 39.4; Apr: 47.4; May: 56.5; Jun: 62.6; Jul: 69.1; Aug: 68.1; Sep: 59.2; Oct: 46; Nov: 34.7; Dec: 27.2; Jan: 20.1; Feb: 23.9; Mar: 28.9; Apr: 33.44; May: 41.9; Jun: 48.2; Jul: 50.72; Aug: 49.82; Sep: 46.4; Oct: 39.02; Nov: 31.3; Dec: 20.3
FL | VERO BEACH MUNICIPAL ARPT | Jan: 62.8; Feb: 64.8; Mar: 67.8; Apr: 71.7; May: 76.6; Jun: 80.3; Jul: 81.5; Aug: 81.8; Sep: 80.6; Oct: 76.4; Nov: 69.9; Dec: 65.3; Jan: 58.5; Feb: 54.68; Mar: 58.5; Apr: 66.38; May: 68.4; Jun: 70.88; Jul: 73.4; Aug: 73.22; Sep: 72.3; Oct: 68.72; Nov: 62.1; Dec: 58.1
MO | VICHY ROLLA NATL ARPT | Jan: 32.1; Feb: 35.7; Mar: 45.5; Apr: 56.1; May: 64.6; Jun: 72.7; Jul: 77.4; Aug: 77; Sep: 68; Oct: 56.7; Nov: 45.8; Dec: 34.6; Jan: 18.7; Feb: 33.98; Mar: 36; Apr: 48.2; May: 54; Jun: 62.06; Jul: 69.98; Aug: 62.78; Sep: 54.9; Oct: 44.42; Nov: 39; Dec: 23.9
BC | VICTORIA | Jan: 41.2; Feb: 42.4; Mar: 44.3; Apr: 48.5; May: 54.3; Jun: 59.8; Jul: 65; Aug: 64.6; Sep: 60.1; Oct: 51.1; Nov: 44.4; Dec: 40.4; Jan: 35.1; Feb: 36.14; Mar: 39.9; Apr: 41.9; May: 46.4; Jun: 50.36; Jul: 53.6; Aug: 54.5; Sep: 52.2; Oct: 47.12; Nov: 42.3; Dec: 34.9
BC | VICTORIA AP | Jan: 40.2; Feb: 41.2; Mar: 44.1; Apr: 48.2; May: 53.9; Jun: 58.8; Jul: 62.7; Aug: 62.4; Sep: 57.9; Oct: 50.2; Nov: 43.7; Dec: 39.8; Jan: 36; Feb: 34.88; Mar: 36.5; Apr: 39.2; May: 44.1; Jun: 47.84; Jul: 51.44; Aug: 52.16; Sep: 49.1; Oct: 44.24; Nov: 39.6; Dec: 35.2
TX | VICTORIA REGIONAL AP | Jan: 54.9; Feb: 58.4; Mar: 63.9; Apr: 70.4; May: 77.2; Jun: 82.5; Jul: 84.1; Aug: 84.7; Sep: 80.3; Oct: 72.4; Nov: 62.7; Dec: 56.1; Jan: 47.1; Feb: 46.58; Mar: 51.1; Apr: 59.54; May: 67.5; Jun: 71.96; Jul: 74.48; Aug: 73.04; Sep: 70; Oct: 61.34; Nov: 54; Dec: 45
BC | VICTORIA UNIV | Jan: 42.3; Feb: 42.8; Mar: 45.3; Apr: 49.1; May: 54.5; Jun: 59.1; Jul: 63.3; Aug: 63.2; Sep: 58.9; Oct: 51.3; Nov: 45.5; Dec: 42.2; Jan: 35.6; Feb: 36.68; Mar: 39.9; Apr: 42.08; May: 46.8; Jun: 50.9; Jul: 54.5; Aug: 55.04; Sep: 52.2; Oct: 47.48; Nov: 42.6; Dec: 35.4
VA | VIRGINIA TECH ARPT | Jan: 33.8; Feb: 36.5; Mar: 44.4; Apr: 54; May: 62.2; Jun: 69.8; Jul: 72.9; Aug: 72.2; Sep: 65.3; Oct: 54.9; Nov: 44.4; Dec: 36.6; Jan: 20.1; Feb: 24.08; Mar: 20.7; Apr: 35.6; May: 49.6; Jun: 57.2; Jul: 62.42; Aug: 60.26; Sep: 57; Oct: 44.96; Nov: 37; Dec: 24.4
CA | VISALIA MUNI (AWOS) | Jan: 46.6; Feb: 50.4; Mar: 56.2; Apr: 60.3; May: 68.4; Jun: 74.8; Jul: 79.7; Aug: 78; Sep: 73.4; Oct: 63.8; Nov: 53.1; Dec: 46; Jan: 38.5; Feb: 30.74; Mar: 43; Apr: 41.54; May: 44.6; Jun: 48.56; Jul: 58.1; Aug: 54.5; Sep: 52.2; Oct: 45.32; Nov: 37.6; Dec: 34.9
BC | W VANCOUVER | Jan: 39.2; Feb: 40.9; Mar: 43.6; Apr: 48.2; May: 54.5; Jun: 59.2; Jul: 64.1; Aug: 64.8; Sep: 59.9; Oct: 50.7; Nov: 42.9; Dec: 38.4; Jan: 31.5; Feb: 32.9; Mar: 36.9; Apr: 39.02; May: 45; Jun: 50.18; Jul: 53.96; Aug: 54.32; Sep: 51.1; Oct: 44.42; Nov: 38.7; Dec: 30.6
IL | W. CHICAGO/DU PAGE | Jan: 23.2; Feb: 27; Mar: 37.5; Apr: 48.9; May: 59.2; Jun: 68.8; Jul: 72.9; Aug: 71.1; Sep: 63.8; Oct: 51.9; Nov: 39.5; Dec: 27.9; Jan: 22.6; Feb: 26.06; Mar: 29.5; Apr: 39.38; May: 45.7; Jun: 60.98; Jul: 59.36; Aug: 62.96; Sep: 53.1; Oct: 42.26; Nov: 32.5; Dec: 17.1
TX | WACO REGIONAL AP | Jan: 48.3; Feb: 52.1; Mar: 58.9; Apr: 66.8; May: 74.7; Jun: 82.2; Jul: 85.5; Aug: 85.7; Sep: 78.7; Oct: 68.6; Nov: 57.6; Dec: 49.4; Jan: 36.7; Feb: 41; Mar: 48.2; Apr: 55.94; May: 61.5; Jun: 68; Jul: 67.28; Aug: 68.18; Sep: 67.1; Oct: 53.78; Nov: 47.1; Dec: 34
WA | WALLA WALLA CITY COUNTY AP | Jan: 36.6; Feb: 39.7; Mar: 46.8; Apr: 52.4; May: 59.8; Jun: 66.5; Jul: 76.3; Aug: 75.2; Sep: 66.9; Oct: 53.8; Nov: 42.4; Dec: 35.1; Jan: 30.6; Feb: 30.56; Mar: 30.9; Apr: 38.12; May: 41; Jun: 46.94; Jul: 44.96; Aug: 48.74; Sep: 45.9; Oct: 39.02; Nov: 36; Dec: 30.4
AR | WALNUT RIDGE (AWOS) | Jan: 37.6; Feb: 41.2; Mar: 50.1; Apr: 59.9; May: 69.2; Jun: 77.8; Jul: 80.3; Aug: 78.8; Sep: 70.9; Oct: 60.7; Nov: 48.9; Dec: 39.8; Jan: 28.8; Feb: 34.52; Mar: 32.2; Apr: 42.8; May: 54.3; Jun: 63.14; Jul: 70.34; Aug: 66.2; Sep: 64.2; Oct: 53.6; Nov: 36.3; Dec: 27.7
GA | WARNER ROBINS AFB | Jan: 47.5; Feb: 51.2; Mar: 58; Apr: 64.6; May: 72.8; Jun: 79.1; Jul: 82; Aug: 80.9; Sep: 75.5; Oct: 65; Nov: 55.6; Dec: 50; Jan: 31.8; Feb: 37.22; Mar: 36.1; Apr: 44.42; May: 66.9; Jun: 67.82; Jul: 73.04; Aug: 69.8; Sep: 64.8; Oct: 46.94; Nov: 42.4; Dec: 30.7
IA | WASHINGTON | Jan: 25; Feb: 28; Mar: 40; Apr: 52.5; May: 63.3; Jun: 72.3; Jul: 75.5; Aug: 73.7; Sep: 64.8; Oct: 53.8; Nov: 40.5; Dec: 28; Jan: 21.2; Feb: 17.78; Mar: 30.2; Apr: 41.36; May: 51.4; Jun: 58.64; Jul: 68.18; Aug: 65.66; Sep: 59.5; Oct: 43.88; Nov: 27.5; Dec: 21.6
PA | WASHINGTON (AWOS) | Jan: 28.5; Feb: 30.4; Mar: 38.6; Apr: 49.9; May: 58.4; Jun: 67.1; Jul: 70.7; Aug: 69; Sep: 62.1; Oct: 51.9; Nov: 41.4; Dec: 32.8; Jan: 30.6; Feb: 22.64; Mar: 19.8; Apr: 36.68; May: 46.8; Jun: 57.92; Jul: 60.26; Aug: 60.44; Sep: 55.6; Oct: 38.66; Nov: 32; Dec: 24.8
VA | WASHINGTON DC DULLES INT AR [STERLING - ISIS] | Jan: 34.4; Feb: 36.5; Mar: 44.5; Apr: 55; May: 63.6; Jun: 72.4; Jul: 76.8; Aug: 75.5; Sep: 68; Oct: 56.3; Nov: 46.1; Dec: 37.6; Jan: 20.7; Feb: 24.08; Mar: 30.4; Apr: 39.92; May: 53.6; Jun: 61.16; Jul: 66.56; Aug: 63.86; Sep: 59.7; Oct: 41.18; Nov: 36.7; Dec: 23.4
VA | WASHINGTON DC REAGAN AP | Jan: 37.2; Feb: 39.4; Mar: 47.1; Apr: 57.4; May: 66.3; Jun: 75.4; Jul: 80; Aug: 78.4; Sep: 71.3; Oct: 59.9; Nov: 49.4; Dec: 40.9; Jan: 23.4; Feb: 20.3; Mar: 27.7; Apr: 42.62; May: 53.2; Jun: 63.32; Jul: 65.48; Aug: 63.68; Sep: 60.6; Oct: 49.64; Nov: 39.7; Dec: 32.7
IA | WATERLOO MUNICIPAL AP | Jan: 18.5; Feb: 23.3; Mar: 35.6; Apr: 48.4; May: 60.1; Jun: 70; Jul: 73; Aug: 70.9; Sep: 62.9; Oct: 50.5; Nov: 36.4; Dec: 23.4; Jan: 9.1; Feb: 13.82; Mar: 25; Apr: 33.44; May: 45.7; Jun: 56.12; Jul: 64.22; Aug: 61.34; Sep: 50.7; Oct: 38.12; Nov: 29.7; Dec: 16.3
WI | WATERTOWN | Jan: 20.2; Feb: 23.8; Mar: 34.5; Apr: 46.9; May: 57.8; Jun: 67.7; Jul: 71.8; Aug: 70; Sep: 62.2; Oct: 50.4; Nov: 37.5; Dec: 25; Jan: 18.7; Feb: 15.98; Mar: 22.1; Apr: 41; May: 48.2; Jun: 60.08; Jul: 65.66; Aug: 63.32; Sep: 59.2; Oct: 43.7; Nov: 34; Dec: 27.5
NY | WATERTOWN AP | Jan: 20.7; Feb: 21.5; Mar: 31; Apr: 44; May: 55.2; Jun: 64.4; Jul: 69; Aug: 67.7; Sep: 60; Oct: 49.3; Nov: 38.6; Dec: 27.6; Jan: 17.2; Feb: 16.7; Mar: 20.3; Apr: 35.24; May: 42.8; Jun: 54.14; Jul: 62.24; Aug: 59.54; Sep: 54.1; Oct: 44.06; Nov: 29.1; Dec: 22.5
SD | WATERTOWN MUNICIPAL AP | Jan: 13.1; Feb: 16.7; Mar: 28.5; Apr: 43.3; May: 55.6; Jun: 65.7; Jul: 71.5; Aug: 69.1; Sep: 60; Oct: 46.3; Nov: 30.9; Dec: 17.8; Jan: 12.7; Feb: 4.28; Mar: 24.3; Apr: 35.06; May: 46.4; Jun: 52.7; Jul: 60.98; Aug: 57.38; Sep: 50.5; Oct: 33.44; Nov: 27.5; Dec: 4.1
ME | WATERVILLE (AWOS) | Jan: 18.7; Feb: 21.9; Mar: 31.8; Apr: 43.4; May: 54.4; Jun: 62.9; Jul: 68.2; Aug: 67; Sep: 59.3; Oct: 47.6; Nov: 37.2; Dec: 26.3; Jan: 16.3; Feb: 11.48; Mar: 17.2; Apr: 21.74; May: 36.5; Jun: 42.08; Jul: 59.54; Aug: 57.38; Sep: 42.4; Oct: 31.1; Nov: 28.2; Dec: 19.9
WI | WAUSAU MUNICIPAL ARPT | Jan: 15.5; Feb: 19.6; Mar: 30.5; Apr: 44.1; May: 56.1; Jun: 65.7; Jul: 69.7; Aug: 68; Sep: 59.3; Oct: 47; Nov: 33.3; Dec: 20.8; Jan: 9.7; Feb: 5.9; Mar: 11.8; Apr: 35.42; May: 36.3; Jun: 57.74; Jul: 57.02; Aug: 61.34; Sep: 52; Oct: 38.3; Nov: 26.4; Dec: 17.4
IA | WEBSTER CITY | Jan: 20.9; Feb: 24.7; Mar: 36; Apr: 49.5; May: 61.2; Jun: 71.1; Jul: 74.7; Aug: 71.8; Sep: 63.3; Oct: 51.6; Nov: 37.6; Dec: 23.9; Jan: 14.5; Feb: 20.48; Mar: 32; Apr: 42.08; May: 41.7; Jun: 60.26; Jul: 65.66; Aug: 64.76; Sep: 54.9; Oct: 42.8; Nov: 25.2; Dec: 21.2
WA | WENATCHEE/PANGBORN | Jan: 29.3; Feb: 35; Mar: 43.5; Apr: 51.3; May: 59.7; Jun: 66.2; Jul: 75; Aug: 73.8; Sep: 65.5; Oct: 51.2; Nov: 38; Dec: 29.2; Jan: 27.1; Feb: 29.12; Mar: 27.7; Apr: 31.46; May: 39.2; Jun: 41.36; Jul: 47.3; Aug: 50.72; Sep: 44.8; Oct: 35.6; Nov: 31.6; Dec: 26.2
UT | WENDOVER USAF AUXILIARY FIELD | Jan: 27.5; Feb: 33.4; Mar: 43.2; Apr: 50.5; May: 60.6; Jun: 70.4; Jul: 79.9; Aug: 77.1; Sep: 66.5; Oct: 51.5; Nov: 37.4; Dec: 27.9; Jan: 18.3; Feb: 21.56; Mar: 23.4; Apr: 25.16; May: 32.5; Jun: 30.56; Jul: 37.22; Aug: 38.48; Sep: 31.5; Oct: 31.28; Nov: 17.6; Dec: 18.3
MA | WESTFIELD BARNES MUNI AP | Jan: 24.5; Feb: 27.6; Mar: 36.2; Apr: 48.6; May: 58.7; Jun: 67.4; Jul: 72.6; Aug: 70.7; Sep: 63.2; Oct: 51.2; Nov: 41.2; Dec: 31; Jan: 5.9; Feb: 14.72; Mar: 28.4; Apr: 35.96; May: 42.8; Jun: 58.1; Jul: 58.82; Aug: 60.44; Sep: 57.7; Oct: 44.6; Nov: 31.1; Dec: 22.3
NY | WESTHAMPTON GABRESKI AP | Jan: 29.6; Feb: 31.3; Mar: 37.6; Apr: 46.9; May: 56.1; Jun: 66; Jul: 72; Aug: 70.9; Sep: 64; Oct: 53.1; Nov: 44.1; Dec: 35.2; Jan: 22.3; Feb: 25.34; Mar: 32.7; Apr: 33.98; May: 49.5; Jun: 57.38; Jul: 60.8; Aug: 64.04; Sep: 59.9; Oct: 48.38; Nov: 34.9; Dec: 26.6
MN | WHEATON NDB (AWOS) | Jan: 11.1; Feb: 15.2; Mar: 27.9; Apr: 43.6; May: 56.5; Jun: 66.3; Jul: 70.6; Aug: 68.1; Sep: 59.8; Oct: 46.7; Nov: 30.8; Dec: 17.1; Jan: 6.3; Feb: 4.64; Mar: 19; Apr: 35.6; May: 42.6; Jun: 51.62; Jul: 60.44; Aug: 59.18; Sep: 54; Oct: 34.52; Nov: 16.5; Dec: 16.2
WV | WHEELING OHIO COUNTY AP | Jan: 29.3; Feb: 31.5; Mar: 40.6; Apr: 52.7; May: 61.4; Jun: 68.7; Jul: 72.5; Aug: 71.6; Sep: 64.9; Oct: 53.8; Nov: 44; Dec: 33.9; Jan: 30.4; Feb: 19.04; Mar: 25.3; Apr: 42.44; May: 45.9; Jun: 57.56; Jul: 63.32; Aug: 60.98; Sep: 52.9; Oct: 44.96; Nov: 31.6; Dec: 21.4
WA | WHIDBEY ISLAND NAS | Jan: 41.7; Feb: 42.5; Mar: 45.4; Apr: 48.8; May: 52.8; Jun: 56.6; Jul: 59.2; Aug: 59.6; Sep: 56.4; Oct: 50.7; Nov: 45.2; Dec: 40.9; Jan: 37.9; Feb: 37.04; Mar: 36.7; Apr: 43.88; May: 46.4; Jun: 49.82; Jul: 52.7; Aug: 51.98; Sep: 51.4; Oct: 44.96; Nov: 43; Dec: 37.8
BC | WHISTLER | Jan: 28.6; Feb: 31.1; Mar: 35; Apr: 41; May: 50; Jun: 55.3; Jul: 62.7; Aug: 62.1; Sep: 55.4; Oct: 43.9; Nov: 33.3; Dec: 27.3; Jan: 20.8; Feb: 23.54; Mar: 28.2; Apr: 32; May: 38.7; Jun: 44.96; Jul: 48.56; Aug: 48.2; Sep: 44.1; Oct: 37.22; Nov: 30; Dec: 20.7
NY | WHITE PLAINS WESTCHESTER CO A | Jan: 30.1; Feb: 31.9; Mar: 39.2; Apr: 49.8; May: 59.4; Jun: 68.7; Jul: 73.8; Aug: 72.3; Sep: 64.9; Oct: 54.2; Nov: 44.4; Dec: 35.3; Jan: 13.3; Feb: 16.34; Mar: 30.6; Apr: 37.76; May: 44.2; Jun: 58.28; Jul: 61.34; Aug: 61.16; Sep: 58.6; Oct: 44.78; Nov: 33.4; Dec: 16.7
YT | WHITEHORSE | Jan: 2.6; Feb: 10.8; Mar: 18.8; Apr: 34.1; May: 45.4; Jun: 54.5; Jul: 57.6; Aug: 54.8; Sep: 45.1; Oct: 32.5; Nov: 14.9; Dec: 7.3; Jan: 33.1; Feb: 34.7; Mar: 39; Apr: 42.08; May: 48; Jun: 52.52; Jul: 56.12; Aug: 56.66; Sep: 53.2; Oct: 46.76; Nov: 40.8; Dec: 32.4
MO | WHITEMAN AFB | Jan: 30.4; Feb: 35.8; Mar: 44.9; Apr: 55.2; May: 65.1; Jun: 74.4; Jul: 78.8; Aug: 77.2; Sep: 68.6; Oct: 57.4; Nov: 44.8; Dec: 34; Jan: 29.5; Feb: 22.82; Mar: 33.3; Apr: 35.06; May: 50.5; Jun: 65.12; Jul: 64.76; Aug: 63.68; Sep: 53.8; Oct: 41; Nov: 30.2; Dec: 27.7
FL | WHITING FIELD NAAS | Jan: 51.6; Feb: 55.2; Mar: 60.7; Apr: 66.5; May: 74.4; Jun: 80.6; Jul: 81.9; Aug: 81.8; Sep: 78.2; Oct: 68.5; Nov: 58.3; Dec: 54.2; Jan: 45.9; Feb: 45.32; Mar: 44.4; Apr: 55.22; May: 64.4; Jun: 69.98; Jul: 73.58; Aug: 71.6; Sep: 67.3; Oct: 56.12; Nov: 53.8; Dec: 41.2
AK | WHITTIER | Jan: 28.4; Feb: 29.1; Mar: 32.1; Apr: 39.1; May: 46.4; Jun: 54.1; Jul: 56.7; Aug: 55.8; Sep: 48.7; Oct: 39.8; Nov: 32.1; Dec: 29.7; Jan: 23.7; Feb: 26.06; Mar: 25.2; Apr: 23.18; May: 35.8; Jun: 45.68; Jul: 49.64; Aug: 47.84; Sep: 37.6; Oct: 30.56; Nov: 21; Dec: 25.5
TX | WICHITA FALLS MUNICIPAL ARPT | Jan: 43.2; Feb: 47; Mar: 55.1; Apr: 63.5; May: 72.5; Jun: 80.8; Jul: 85.1; Aug: 84.6; Sep: 76.4; Oct: 65.2; Nov: 53.3; Dec: 43.9; Jan: 28.2; Feb: 33.26; Mar: 40.8; Apr: 49.82; May: 58.5; Jun: 62.78; Jul: 65.84; Aug: 65.12; Sep: 61.2; Oct: 47.12; Nov: 40.8; Dec: 30.7
KS | WICHITA MID-CONTINENT AP | Jan: 33.2; Feb: 37.7; Mar: 46.9; Apr: 56.4; May: 66.6; Jun: 76.4; Jul: 81.3; Aug: 80.1; Sep: 71.3; Oct: 59; Nov: 45.8; Dec: 35; Jan: 23; Feb: 26.78; Mar: 32; Apr: 41.72; May: 51.8; Jun: 61.88; Jul: 63.68; Aug: 65.12; Sep: 55.6; Oct: 46.94; Nov: 36; Dec: 22.3
KS | WICHITA/COL. JABARA | Jan: 33; Feb: 37.1; Mar: 46.3; Apr: 56.6; May: 66.4; Jun: 75.1; Jul: 80.6; Aug: 79.5; Sep: 70.3; Oct: 58.7; Nov: 46.1; Dec: 34.6; Jan: 28.6; Feb: 28.76; Mar: 39.2; Apr: 45.68; May: 48.2; Jun: 63.5; Jul: 65.3; Aug: 66.92; Sep: 59.4; Oct: 47.3; Nov: 32; Dec: 16.5
PA | WILKES-BARRE SCRANTON INTL AP | Jan: 27.2; Feb: 29.3; Mar: 37.6; Apr: 49.4; May: 59.5; Jun: 67.9; Jul: 72.2; Aug: 70.4; Sep: 63; Oct: 51.9; Nov: 41.9; Dec: 32.2; Jan: 16.2; Feb: 17.42; Mar: 23.2; Apr: 34.34; May: 46.6; Jun: 58.1; Jul: 58.28; Aug: 59.9; Sep: 51.4; Oct: 41.54; Nov: 29.8; Dec: 21.7
WA | WILLIAM R FAIRCHILD | Jan: 39.5; Feb: 40.3; Mar: 42.7; Apr: 46.6; May: 51.3; Jun: 55.9; Jul: 60; Aug: 60.3; Sep: 57.3; Oct: 49.2; Nov: 43.1; Dec: 39.2; Jan: 35.6; Feb: 36.86; Mar: 37; Apr: 38.12; May: 43.3; Jun: 49.46; Jul: 50.9; Aug: 51.26; Sep: 48.4; Oct: 44.24; Nov: 40.1; Dec: 35.6
PA | WILLIAMSPORT REGIONAL AP | Jan: 27.9; Feb: 30.1; Mar: 39; Apr: 50.5; May: 60.4; Jun: 69.4; Jul: 73.4; Aug: 71.7; Sep: 64; Oct: 52.7; Nov: 42.1; Dec: 32.5; Jan: 17.4; Feb: 18.32; Mar: 29.1; Apr: 37.4; May: 49.8; Jun: 58.28; Jul: 61.34; Aug: 61.88; Sep: 56.8; Oct: 43.52; Nov: 33.1; Dec: 21.9
ND | WILLISTON SLOULIN INTL AP | Jan: 11.7; Feb: 17.2; Mar: 28.8; Apr: 42.9; May: 53.6; Jun: 63; Jul: 70.1; Aug: 69.2; Sep: 58.4; Oct: 43.7; Nov: 27.7; Dec: 15.6; Jan: 5.9; Feb: 13.82; Mar: 22.6; Apr: 28.4; May: 41.7; Jun: 51.44; Jul: 50.36; Aug: 53.24; Sep: 42.3; Oct: 35.96; Nov: 18.9; Dec: 11.7
MN | WILLMAR | Jan: 12.4; Feb: 18.1; Mar: 29.2; Apr: 45; May: 56.8; Jun: 67.1; Jul: 70.6; Aug: 68.4; Sep: 60.7; Oct: 47.6; Nov: 31.4; Dec: 18.7; Jan: 5.5; Feb: 18.14; Mar: 30.9; Apr: 40.28; May: 46.4; Jun: 56.3; Jul: 63.5; Aug: 63.14; Sep: 45; Oct: 32.9; Nov: 24.4; Dec: 15.3
PA | WILLOW GROVE NAS | Jan: 33; Feb: 34.7; Mar: 42.4; Apr: 52.9; May: 62.1; Jun: 71.7; Jul: 75.9; Aug: 73.8; Sep: 66.1; Oct: 55.6; Nov: 45.1; Dec: 37.1; Jan: 24.8; Feb: 24.98; Mar: 28; Apr: 36.86; May: 48.6; Jun: 59.54; Jul: 60.98; Aug: 65.66; Sep: 57; Oct: 44.24; Nov: 39.6; Dec: 27.9
NC | WILMINGTON INTERNATIONAL ARPT | Jan: 46.9; Feb: 48.9; Mar: 55.1; Apr: 63.4; May: 70.6; Jun: 77.6; Jul: 81; Aug: 79.4; Sep: 74.5; Oct: 65.2; Nov: 55.8; Dec: 49.3; Jan: 34.7; Feb: 36.32; Mar: 41.9; Apr: 51.62; May: 60.8; Jun: 69.44; Jul: 72.32; Aug: 70.34; Sep: 66; Oct: 55.04; Nov: 48.4; Dec: 40.8
DE | WILMINGTON NEW CASTLE CNTY AP | Jan: 33.6; Feb: 35.4; Mar: 43.2; Apr: 53.7; May: 63; Jun: 72.3; Jul: 77; Aug: 75.2; Sep: 68.1; Oct: 56.7; Nov: 46.6; Dec: 37.9; Jan: 18.5; Feb: 25.7; Mar: 31.3; Apr: 41.36; May: 52.7; Jun: 60.26; Jul: 65.84; Aug: 64.04; Sep: 56.7; Oct: 43.34; Nov: 31.6; Dec: 21.4
VA | WINCHESTER RGNL | Jan: 34.8; Feb: 36.7; Mar: 44.7; Apr: 54.9; May: 63.6; Jun: 72.3; Jul: 76.5; Aug: 75; Sep: 67.6; Oct: 56.2; Nov: 46.1; Dec: 37.4; Jan: 27.5; Feb: 22.28; Mar: 24.4; Apr: 32.54; May: 42.6; Jun: 62.42; Jul: 60.62; Aug: 65.3; Sep: 53.2; Oct: 42.98; Nov: 28.6; Dec: 28.4
ON | WINDSOR | Jan: 25.9; Feb: 27.7; Mar: 36.4; Apr: 48.1; May: 59.4; Jun: 69.5; Jul: 73.4; Aug: 71.7; Sep: 64.4; Oct: 53; Nov: 41.5; Dec: 31; Jan: 19; Feb: 19.22; Mar: 26.1; Apr: 35.42; May: 46.2; Jun: 56.66; Jul: 60.26; Aug: 61.52; Sep: 55.2; Oct: 42.98; Nov: 34.2; Dec: 23
TX | WINK WINKLER COUNTY AP | Jan: 45.9; Feb: 50.6; Mar: 58.1; Apr: 66.9; May: 75.8; Jun: 84.3; Jul: 84.4; Aug: 83.6; Sep: 76.6; Oct: 66.5; Nov: 54; Dec: 45.9; Jan: 29.1; Feb: 25.7; Mar: 39.2; Apr: 30.38; May: 43.2; Jun: 55.04; Jul: 61.52; Aug: 57.2; Sep: 56.7; Oct: 49.64; Nov: 39.7; Dec: 19.6
NV | WINNEMUCCA MUNICIPAL ARPT | Jan: 30.6; Feb: 35.3; Mar: 41.6; Apr: 46.4; May: 55.1; Jun: 64.1; Jul: 73.5; Aug: 70.3; Sep: 61.6; Oct: 48.6; Nov: 37.4; Dec: 29.2; Jan: 18.3; Feb: 22.82; Mar: 21.4; Apr: 23.72; May: 34.5; Jun: 31.64; Jul: 39.2; Aug: 37.22; Sep: 28.6; Oct: 26.6; Nov: 23.4; Dec: 19
MB | WINNIPEG | Jan: 2.5; Feb: 7.4; Mar: 21.1; Apr: 39.1; May: 51.7; Jun: 62.5; Jul: 66.8; Aug: 65.8; Sep: 55.9; Oct: 41.5; Nov: 24; Dec: 8.6; Jan: -2.6; Feb: -0.58; Mar: 14; Apr: 27.86; May: 37.8; Jun: 51.62; Jul: 57.74; Aug: 55.04; Sep: 47.8; Oct: 33.44; Nov: 21.4; Dec: 3.7
MN | WINONA MUNI (AWOS) | Jan: 18; Feb: 22.5; Mar: 34.2; Apr: 47.6; May: 58.8; Jun: 68.7; Jul: 73; Aug: 70.8; Sep: 62.7; Oct: 50.5; Nov: 36.9; Dec: 23.8; Jan: 10.6; Feb: 10.4; Mar: 28.6; Apr: 38.66; May: 44.2; Jun: 56.48; Jul: 62.24; Aug: 61.7; Sep: 54.1; Oct: 38.12; Nov: 28.6; Dec: 3.9
AZ | WINSLOW MUNICIPAL AP | Jan: 35.6; Feb: 40.1; Mar: 47.4; Apr: 54; May: 63.3; Jun: 72.7; Jul: 78.2; Aug: 75.9; Sep: 69; Oct: 56.3; Nov: 43.7; Dec: 34.4; Jan: 20.7; Feb: 21.38; Mar: 21.4; Apr: 23.18; May: 30.6; Jun: 30.56; Jul: 49.28; Aug: 53.78; Sep: 46.8; Oct: 21.2; Nov: 25; Dec: 16.2
NC | WINSTON-SALEM REYNOLDS AP | Jan: 40.3; Feb: 43.4; Mar: 50.7; Apr: 59.8; May: 67.4; Jun: 75.1; Jul: 78; Aug: 76.9; Sep: 70; Oct: 59.7; Nov: 50.4; Dec: 43.1; Jan: 23.2; Feb: 33.98; Mar: 41.2; Apr: 46.76; May: 53.2; Jun: 64.4; Jul: 69.08; Aug: 63.86; Sep: 59.2; Oct: 50.72; Nov: 42.3; Dec: 26.1
ME | WISCASSET | Jan: 21.3; Feb: 24.8; Mar: 32.7; Apr: 43.3; May: 53.3; Jun: 62.2; Jul: 68.1; Aug: 66.9; Sep: 59.5; Oct: 48.3; Nov: 38.6; Dec: 28.5; Jan: 21.4; Feb: 14; Mar: 25.9; Apr: 33.08; May: 42.6; Jun: 53.24; Jul: 60.26; Aug: 58.46; Sep: 56.3; Oct: 44.06; Nov: 33.8; Dec: 28.2
VA | WISE/LONESOME PINE | Jan: 33.2; Feb: 36.4; Mar: 44.8; Apr: 54.6; May: 62; Jun: 69; Jul: 72.4; Aug: 72; Sep: 65.5; Oct: 55.5; Nov: 45.4; Dec: 37; Jan: 24.4; Feb: 27.68; Mar: 26.8; Apr: 31.28; May: 47.3; Jun: 58.82; Jul: 65.3; Aug: 60.62; Sep: 55.6; Oct: 43.34; Nov: 34.7; Dec: 20.1
WI | WITTMAN RGNL | Jan: 18.7; Feb: 22.2; Mar: 32.7; Apr: 45.8; May: 56.7; Jun: 66.8; Jul: 71.5; Aug: 69.4; Sep: 61.6; Oct: 49.4; Nov: 36.8; Dec: 24.1; Jan: 10.4; Feb: 8.78; Mar: 30.7; Apr: 37.4; May: 41.4; Jun: 55.76; Jul: 58.46; Aug: 61.52; Sep: 53.1; Oct: 36.86; Nov: 31.6; Dec: 6.6
MT | WOLF POINT INTL [FORT PECK - SURFRAD] | Jan: 13.8; Feb: 16.2; Mar: 29.7; Apr: 43.3; May: 53.3; Jun: 62.3; Jul: 71.5; Aug: 69.2; Sep: 58.1; Oct: 44.1; Nov: 28.5; Dec: 15.6; Jan: 13.5; Feb: 2.84; Mar: 15.3; Apr: 28.22; May: 41.2; Jun: 50.36; Jul: 53.42; Aug: 53.42; Sep: 39; Oct: 31.28; Nov: 22.6; Dec: 12.4
MA | WORCESTER REGIONAL ARPT | Jan: 24.9; Feb: 27; Mar: 34.8; Apr: 46.4; May: 56.4; Jun: 65.3; Jul: 70.4; Aug: 69; Sep: 61.6; Oct: 50.6; Nov: 40.5; Dec: 30.6; Jan: 9.3; Feb: 14.36; Mar: 19.9; Apr: 31.64; May: 43.9; Jun: 52.52; Jul: 59; Aug: 56.3; Sep: 51.4; Oct: 37.22; Nov: 25.5; Dec: 18.1
WY | WORLAND MUNICIPAL | Jan: 18.3; Feb: 22.1; Mar: 37.3; Apr: 46.1; May: 55.2; Jun: 65.4; Jul: 74.3; Aug: 71; Sep: 60.9; Oct: 46.3; Nov: 32.3; Dec: 18.2; Jan: 11.1; Feb: 17.06; Mar: 18.7; Apr: 28.4; May: 37.6; Jun: 42.8; Jul: 46.58; Aug: 43.88; Sep: 37.4; Oct: 33.44; Nov: 21.9; Dec: 12.7
MN | WORTHINGTON (AWOS) | Jan: 15.4; Feb: 20; Mar: 31.5; Apr: 45.5; May: 56.6; Jun: 66.9; Jul: 70.8; Aug: 68.3; Sep: 60.6; Oct: 48.6; Nov: 33.3; Dec: 20.4; Jan: 8.1; Feb: 18.68; Mar: 12.2; Apr: 35.96; May: 46.6; Jun: 53.96; Jul: 60.26; Aug: 60.44; Sep: 53.4; Oct: 33.44; Nov: 23.4; Dec: 9.5
AK | WRANGELL | Jan: 32.1; Feb: 34.3; Mar: 36.8; Apr: 42.9; May: 49.6; Jun: 54.6; Jul: 57; Aug: 56.9; Sep: 52.2; Oct: 45.2; Nov: 37.9; Dec: 33.9; Jan: 21.9; Feb: 24.62; Mar: 26.1; Apr: 30.56; May: 37.8; Jun: 46.58; Jul: 51.44; Aug: 50.36; Sep: 44.8; Oct: 37.76; Nov: 28.9; Dec: 25.5
WA | YAKIMA AIR TERMINAL | Jan: 31.6; Feb: 36.6; Mar: 43.3; Apr: 49.5; May: 57.8; Jun: 64.4; Jul: 72.1; Aug: 70.2; Sep: 62.2; Oct: 49.5; Nov: 37.9; Dec: 30; Jan: 26.2; Feb: 28.58; Mar: 30; Apr: 35.6; May: 39.7; Jun: 44.78; Jul: 47.48; Aug: 45.32; Sep: 40.6; Oct: 36.68; Nov: 25.9; Dec: 23.9
AK | YAKUTAT STATE ARPT | Jan: 27.7; Feb: 29.9; Mar: 31.3; Apr: 37.9; May: 44.9; Jun: 51.3; Jul: 54.6; Aug: 54.1; Sep: 49; Oct: 41.2; Nov: 32.6; Dec: 29.6; Jan: 23; Feb: 19.4; Mar: 25; Apr: 33.62; May: 40.1; Jun: 45.86; Jul: 50; Aug: 50.9; Sep: 44.8; Oct: 36.86; Nov: 28; Dec: 26.8
NT | YELLOWKNIFE AP | Jan: -13.9; Feb: -8.2; Mar: 2; Apr: 22.2; May: 40.8; Jun: 56.6; Jul: 62.8; Aug: 57.6; Sep: 45.8; Oct: 30; Nov: 8.8; Dec: -7.4; Jan: -19.7; Feb: -17.68; Mar: -9.6; Apr: 11.66; May: 24.6; Jun: 38.66; Jul: 47.84; Aug: 45.68; Sep: 37.8; Oct: 25.34; Nov: 6.4; Dec: -12.3
OH | YOUNGSTOWN REGIONAL AIRPORT | Jan: 27; Feb: 28.8; Mar: 37.3; Apr: 49.1; May: 58.7; Jun: 67.2; Jul: 70.9; Aug: 69.5; Sep: 62.3; Oct: 51.7; Nov: 41.4; Dec: 31.6; Jan: 16.9; Feb: 18.32; Mar: 28.8; Apr: 34.34; May: 47.1; Jun: 54.68; Jul: 63.68; Aug: 60.44; Sep: 54.1; Oct: 40.1; Nov: 33.6; Dec: 22.1
CA | YUBA CO | Jan: 46.7; Feb: 50.5; Mar: 55.2; Apr: 58.8; May: 67.5; Jun: 73.9; Jul: 78.7; Aug: 76.6; Sep: 72.8; Oct: 63.7; Nov: 53.2; Dec: 47.1; Jan: 42.8; Feb: 39.02; Mar: 46; Apr: 43.52; May: 46.8; Jun: 51.62; Jul: 55.22; Aug: 54.14; Sep: 50.7; Oct: 45.86; Nov: 43.2; Dec: 41.9
AZ | YUMA INTL ARPT | Jan: 59.2; Feb: 61.8; Mar: 67.6; Apr: 73.2; May: 81.2; Jun: 89.4; Jul: 94.8; Aug: 94.6; Sep: 89.8; Oct: 78.1; Nov: 66.3; Dec: 57.7; Jan: 33.4; Feb: 29.84; Mar: 34.5; Apr: 31.28; May: 35.6; Jun: 40.64; Jul: 61.34; Aug: 59.36; Sep: 53.1; Oct: 40.1; Nov: 35.6; Dec: 32.9
AZ | YUMA MCAS | Jan: 58.9; Feb: 62.1; Mar: 67.6; Apr: 73.6; May: 81.2; Jun: 89.3; Jul: 94.7; Aug: 94.3; Sep: 89.2; Oct: 78; Nov: 66; Dec: 57.5; Jan: 32.2; Feb: 29.84; Mar: 34.5; Apr: 37.58; May: 38.5; Jun: 40.46; Jul: 54.68; Aug: 66.74; Sep: 52.9; Oct: 46.22; Nov: 38.5; Dec: 40.3
OH | ZANESVILLE MUNICIPAL AP | Jan: 29.9; Feb: 32.5; Mar: 41.3; Apr: 52.5; May: 61.5; Jun: 69.8; Jul: 73.3; Aug: 72.1; Sep: 64.8; Oct: 53.5; Nov: 43.1; Dec: 34; Jan: 30.4; Feb: 26.6; Mar: 32; Apr: 43.88; May: 56.8; Jun: 57.74; Jul: 62.06; Aug: 60.8; Sep: 56.8; Oct: 46.76; Nov: 33.6; Dec: 27.1

## COP Calcs (hidden)
[16 empty] | Energy Saving Mode 1 |  |  | Energy Saving Mode 2 |  |  | Max Capacity Operation Mode |  |  |  | Weighted COP for Calculator |  |  | Description | Type | Day | 1am | 2am | 3am | 4am | 5am | 6am | 7am | 8am | 9am | 10am | 11am | 12am | 1pm | 2pm | 3pm | 4pm | 5pm | 6pm | 7pm | 8pm | 9pm | 10pm | 11pm | 12pm | Hours per day in Max Capacity
Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | Energy Saving 1 COP @ 130F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | Energy Saving 1 COP @ 150F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | Energy Saving 1 COP @ 170F | Outside Air Temp | 130F | 150F | 170F | 130F | 150F | 170F | 130F | 150F | 170F | Outside Air Temp | 130F | 150F | 170F | Service Hot Water | Fraction | WD | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05 | 4
55 | -10 | 69603 | 53245 | 1.2813 | 55 | -10 | 70212 | 53260 | 1.2922 | 55 | -10 | 69301 | 54421 | 1.2482 | -10 | 1.2813 | 1.2922 | 1.2482 | 1.2915 | 1.2871 | 1.2517 | 1.0194 | 1.2909 | 1.2498 | -10 | 1.2377 | 1.2877 | 1.2485 |  |  | Sat | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05 | 4
55 | 0 | 81572 | 60193 | 1.3283 | 55 | 0 | 81562 | 59904 | 1.3346 | 55 | 0 | 80068 | 61166 | 1.2831 | 0 | 1.3283 | 1.3346 | 1.2831 | 1.3327 | 1.3406 | 1.2838 | 1.0539 | 1.3329 | 1.2878 | 0 | 1.2826 | 1.3343 | 1.2839 |  |  | Sun | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.8 | 0.7 | 0.5 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.6 | 0.7 | 0.7 | 0.4 | 0.25 | 0.2 | 0.2 | 0.05 | 0.05 | 4
55 | 10 | 93935 | 64615 | 1.425 | 55 | 10 | 94394 | 64577 | 1.4328 | 55 | 10 | 92988 | 66236 | 1.3761 | 10 | 1.425 | 1.4328 | 1.3761 | 1.4393 | 1.4375 | 1.3784 | 1.1371 | 1.4406 | 1.3856 | 10 | 1.377 | 1.4341 | 1.3777
55 | 20 | 109127 | 65897 | 1.6232 | 55 | 20 | 109143 | 65673 | 1.629 | 55 | 20 | 107639 | 67808 | 1.556 | 20 | 1.6232 | 1.629 | 1.556 | 1.6301 | 1.6277 | 1.5652 | 1.2875 | 1.6307 | 1.559 | 20 | 1.5673 | 1.6282 | 1.5565
55 | 30 | 120976 | 66405 | 1.7857 | 55 | 30 | 120927 | 66111 | 1.7929 | 55 | 30 | 118713 | 68442 | 1.7002 | 30 | 1.7857 | 1.7929 | 1.7002 | 1.7888 | 1.7838 | 1.703 | 1.4013 | 1.771 | 1.6964 | 30 | 1.7216 | 1.7817 | 1.6995
55 | 40 | 136485 | 55479 | 2.4114 | 55 | 40 | 136485 | 55742 | 2.4 | 55 | 40 | 136262 | 62679 | 2.1309 | 40 | 2.4114 | 2.4 | 2.1309 | 2.152 | 2.143 | 1.937 | 1.6362 | 2.0637 | 1.9365 | 40 | 2.066 | 2.1298 | 1.9369
55 | 50 | 136485 | 40140 | 3.3329 | 55 | 50 | 136485 | 40043 | 3.341 | 55 | 50 | 136262 | 52992 | 2.5205 | 50 | 3.3329 | 3.341 | 2.5205 | 2.953 | 2.9287 | 2.3706 | 2.0677 | 2.6349 | 2.22 | 50 | 2.8054 | 2.8797 | 2.3455
55 | 60 | 136485 | 33501 | 3.9934 | 55 | 60 | 136485 | 35297 | 3.7902 | 55 | 60 | 136262 | 51556 | 2.5907 | 60 | 3.9934 | 3.7902 | 2.5907 | 3.7821 | 3.651 | 2.5935 | 2.2823 | 2.882 | 2.3522 | 60 | 3.5321 | 3.5228 | 2.5509
55 | 70 | 136485 | 33310 | 4.0163 | 55 | 70 | 136485 | 34056 | 3.9283 | 55 | 70 | 136262 | 45587 | 2.9299 | 70 | 4.0163 | 3.9283 | 2.9299 | 3.8777 | 3.8021 | 2.9454 | 2.4733 | 3.1303 | 2.6219 | 70 | 3.6437 | 3.6901 | 2.8785
55 | 80 | 136485 | 32961 | 4.0588 | 55 | 80 | 136485 | 33398 | 4.0057 | 55 | 80 | 136262 | 42447 | 3.1466 | 80 | 4.0588 | 4.0057 | 3.1466 | 3.9115 | 3.8591 | 3.1316 | 2.631 | 3.3648 | 2.7955 | 80 | 3.6981 | 3.7767 | 3.0756
55 | 90 | 136485 | 33102 | 4.0415 | 55 | 90 | 136485 | 32960 | 4.0589 | 55 | 90 | 136262 | 40768 | 3.2762 | 90 | 4.0415 | 4.0589 | 3.2762 | 3.8626 | 3.8774 | 3.3002 | 2.6971 | 3.4485 | 2.932 | 90 | 3.6684 | 3.8059 | 3.2188
55 | 100 | 136485 | 32663 | 4.0958 | 55 | 100 | 136485 | 32449 | 4.1228 | 55 | 100 | 136262 | 40768 | 3.2762 | 100 | 4.0958 | 4.1228 | 3.2762 | 3.9147 | 3.9349 | 3.3105 | 2.7905 | 3.5551 | 3.0266 | 100 | 3.7273 | 3.8716 | 3.2346
Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | Energy Saving 1 COP @ 130F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | Energy Saving 1 COP @ 150F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | Energy Saving 1 COP @ 170F
45 | -10 | 72440 | 52723 | 1.3468 | 45 | -10 | 72865 | 52602 | 1.3578 | 45 | -10 | 71992 | 54103 | 1.3043
45 | 0 | 84245 | 59367 | 1.391 | 45 | 0 | 84261 | 58955 | 1.4009 | 45 | 0 | 83144 | 60760 | 1.3413
45 | 10 | 98095 | 64094 | 1.5002 | 45 | 10 | 98032 | 63993 | 1.5016 | 45 | 10 | 96256 | 65645 | 1.4373
45 | 20 | 114372 | 64993 | 1.7249 | 45 | 20 | 113033 | 64796 | 1.7099 | 45 | 20 | 111099 | 67042 | 1.6243
45 | 30 | 124428 | 65123 | 1.8728 | 45 | 30 | 124575 | 64796 | 1.8845 | 45 | 30 | 123020 | 67377 | 1.7897
45 | 40 | 136485 | 53587 | 2.4965 | 45 | 40 | 136485 | 54063 | 2.4746 | 45 | 40 | 136262 | 59180 | 2.2569
45 | 50 | 136485 | 37120 | 3.604 | 45 | 50 | 136485 | 37488 | 3.5687 | 45 | 50 | 136262 | 51217 | 2.6078
45 | 60 | 136485 | 32760 | 4.0837 | 45 | 60 | 136485 | 33325 | 4.0145 | 45 | 60 | 136262 | 51556 | 2.5907
45 | 70 | 136485 | 32921 | 4.0637 | 45 | 70 | 136485 | 33106 | 4.041 | 45 | 70 | 136262 | 45587 | 2.9299
45 | 80 | 136485 | 32009 | 4.1795 | 45 | 80 | 136485 | 31792 | 4.2081 | 45 | 80 | 136262 | 41133 | 3.2471
45 | 90 | 136485 | 30766 | 4.3484 | 45 | 90 | 136485 | 30624 | 4.3685 | 45 | 90 | 136262 | 37774 | 3.5359
45 | 100 | 136485 | 29512 | 4.5332 | 45 | 100 | 136485 | 29163 | 4.5874 | 45 | 100 | 136262 | 34707 | 3.8483
Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 130F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 150F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 170F
55 | -10 | 70258 | 67555 | 1.0194 | 55 | -10 | 70395 | 53450 | 1.2909 | 55 | -10 | 69466 | 54482 | 1.2498
55 | 0 | 81485 | 75788 | 1.0539 | 55 | 0 | 81543 | 59964 | 1.3329 | 55 | 0 | 80525 | 61290 | 1.2878
55 | 10 | 94512 | 81472 | 1.1371 | 55 | 10 | 94737 | 64461 | 1.4406 | 55 | 10 | 93562 | 66188 | 1.3856
55 | 20 | 108980 | 82968 | 1.2875 | 55 | 20 | 109207 | 65645 | 1.6307 | 55 | 20 | 107559 | 67625 | 1.559
55 | 30 | 120584 | 84347 | 1.4013 | 55 | 30 | 120578 | 66735 | 1.771 | 55 | 30 | 118664 | 68565 | 1.6964
55 | 40 | 137358 | 82288 | 1.6362 | 55 | 40 | 137078 | 65107 | 2.0637 | 55 | 40 | 137779 | 69738 | 1.9365
55 | 50 | 166058 | 78721 | 2.0677 | 55 | 50 | 169653 | 63111 | 2.6349 | 55 | 50 | 159743 | 70531 | 2.22
55 | 60 | 181887 | 78115 | 2.2823 | 55 | 60 | 184584 | 62779 | 2.882 | 55 | 60 | 169111 | 70472 | 2.3522
55 | 70 | 181119 | 71780 | 2.4733 | 55 | 70 | 185137 | 57973 | 3.1303 | 55 | 70 | 180683 | 67548 | 2.6219
55 | 80 | 174778 | 65116 | 2.631 | 55 | 80 | 184504 | 53747 | 3.3648 | 55 | 80 | 184577 | 64720 | 2.7955
55 | 90 | 172813 | 62804 | 2.6971 | 55 | 90 | 184572 | 52463 | 3.4485 | 55 | 90 | 183954 | 61497 | 2.932
55 | 100 | 170736 | 59973 | 2.7905 | 55 | 100 | 183999 | 50731 | 3.5551 | 55 | 100 | 176277 | 57090 | 3.0266
Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 130F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 150F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 170F
45 | -10 | 72904 | 66841 | 1.0691 | 45 | -10 | 72860 | 52835 | 1.3517 | 45 | -10 | 72056 | 54392 | 1.2985
45 | 0 | 84623 | 74822 | 1.1086 | 45 | 0 | 84391 | 59121 | 1.3992 | 45 | 0 | 83587 | 60907 | 1.3452
45 | 10 | 98346 | 80809 | 1.1929 | 45 | 10 | 98007 | 63837 | 1.5049 | 45 | 10 | 96936 | 65629 | 1.4478
45 | 20 | 113028 | 81959 | 1.3518 | 45 | 20 | 113028 | 64770 | 1.7105 | 45 | 20 | 111565 | 66832 | 1.6363
45 | 30 | 124569 | 83065 | 1.47 | 45 | 30 | 124390 | 65597 | 1.8587 | 45 | 30 | 123052 | 67771 | 1.7797
45 | 40 | 141120 | 81313 | 1.7011 | 45 | 40 | 140728 | 64030 | 2.1543 | 45 | 40 | 142488 | 68798 | 2.0301
45 | 50 | 166654 | 76043 | 2.1482 | 45 | 50 | 174092 | 63111 | 2.7039 | 45 | 50 | 164977 | 70531 | 2.2928
45 | 60 | 183579 | 76082 | 2.3651 | 45 | 60 | 191347 | 62779 | 2.9876 | 45 | 60 | 174051 | 70472 | 2.4209
45 | 70 | 185075 | 70912 | 2.5582 | 45 | 70 | 191860 | 57973 | 3.2439 | 45 | 70 | 185855 | 66388 | 2.7441
45 | 80 | 181011 | 64391 | 2.7555 | 45 | 80 | 191236 | 53747 | 3.4876 | 45 | 80 | 189802 | 62515 | 2.976
45 | 90 | 179204 | 62121 | 2.8276 | 45 | 90 | 191138 | 52463 | 3.5711 | 45 | 90 | 189170 | 58788 | 3.1541
45 | 100 | 176743 | 59740 | 2.9 | 45 | 100 | 190642 | 50731 | 3.6835 | 45 | 100 | 181635 | 54738 | 3.2526
Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 130F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 150F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 170F
55 | -10 | 70674 | 53638 | 1.2915 | 55 | -10 | 70431 | 53638 | 1.2871 | 55 | -10 | 69550 | 54462 | 1.2517
55 | 0 | 81907 | 60241 | 1.3327 | 55 | 0 | 81909 | 59891 | 1.3406 | 55 | 0 | 80128 | 61181 | 1.2838
55 | 10 | 94785 | 64552 | 1.4393 | 55 | 10 | 94670 | 64552 | 1.4375 | 55 | 10 | 93046 | 66167 | 1.3784
55 | 20 | 109350 | 65755 | 1.6301 | 55 | 20 | 109192 | 65755 | 1.6277 | 55 | 20 | 107623 | 67400 | 1.5652
55 | 30 | 121126 | 66371 | 1.7888 | 55 | 30 | 120787 | 66371 | 1.7838 | 55 | 30 | 118579 | 68251 | 1.703
55 | 40 | 138254 | 57392 | 2.3612 | 55 | 40 | 137872 | 57392 | 2.3547 | 55 | 40 | 137540 | 69601 | 1.937
55 | 50 | 147850 | 45531 | 3.1829 | 55 | 50 | 147757 | 45531 | 3.1809 | 55 | 50 | 145188 | 60032 | 2.3706
55 | 60 | 147850 | 37461 | 3.8686 | 55 | 60 | 147757 | 38603 | 3.7518 | 55 | 60 | 145188 | 54873 | 2.5935
55 | 70 | 147850 | 37373 | 3.8777 | 55 | 70 | 147757 | 37970 | 3.8144 | 55 | 70 | 145188 | 47943 | 2.9684
55 | 80 | 147850 | 37050 | 3.9115 | 55 | 80 | 147757 | 37530 | 3.8591 | 55 | 80 | 145188 | 44517 | 3.1968
55 | 90 | 147850 | 37519 | 3.8626 | 55 | 90 | 147757 | 37353 | 3.8774 | 55 | 90 | 145188 | 43119 | 3.3005
55 | 100 | 147850 | 37020 | 3.9147 | 55 | 100 | 147757 | 36807 | 3.9349 | 55 | 100 | 145188 | 42989 | 3.3105
Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 130F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 150F | Inlet Water Temperature (F) | Outside Air Temp (F) | Capacity (Btu/h) | Input (Btu/h) | 170F
45 | -10 | 72904 | 53055 | 1.3469 | 45 | -10 | 73026 | 52836 | 1.3548 | 45 | -10 | 71918 | 54168 | 1.3014
45 | 0 | 84623 | 59350 | 1.3976 | 45 | 0 | 84707 | 59204 | 1.4024 | 45 | 0 | 83266 | 60883 | 1.3406
45 | 10 | 98346 | 64140 | 1.5029 | 45 | 10 | 97906 | 63994 | 1.4996 | 45 | 10 | 96337 | 65487 | 1.442
45 | 20 | 113028 | 64932 | 1.7062 | 45 | 20 | 113111 | 64762 | 1.712 | 45 | 20 | 111145 | 66835 | 1.63
45 | 30 | 124569 | 65059 | 1.8768 | 45 | 30 | 124182 | 64997 | 1.8727 | 45 | 30 | 122639 | 67388 | 1.7839
45 | 40 | 141120 | 64278 | 2.152 | 45 | 40 | 140734 | 64371 | 2.143 | 45 | 40 | 142369 | 68737 | 2.0302
45 | 50 | 165151 | 54819 | 2.953 | 45 | 50 | 164814 | 55162 | 2.9287 | 45 | 50 | 158170 | 63247 | 2.4513
45 | 60 | 165000 | 42763 | 3.7821 | 45 | 60 | 165000 | 44298 | 3.651 | 45 | 60 | 158170 | 58722 | 2.6402
45 | 70 | 165000 | 41561 | 3.8915 | 45 | 70 | 165000 | 42538 | 3.8021 | 45 | 70 | 158170 | 52638 | 2.9454
45 | 80 | 165000 | 40357 | 4.0075 | 45 | 80 | 165000 | 41077 | 3.9373 | 45 | 80 | 158170 | 49507 | 3.1316
45 | 90 | 165000 | 39854 | 4.0581 | 45 | 90 | 165000 | 40020 | 4.0413 | 45 | 90 | 158170 | 46979 | 3.3002
45 | 100 | 165000 | 38684 | 4.1809 | 45 | 100 | 165000 | 38559 | 4.1944 | 45 | 100 | 158170 | 44989 | 3.4461

## phius_monthly climate data (hidden)
Country | State | City_WUFIp Data Set | Country | Select | Select | Country | State | AB | AE | AK | AL | AR | AZ | BC | BD | CA | CO | CT | DE | FL | GA | HI | IA | ID | IL | IN | KS | KY | LA | MA | MB | MD | ME | MI | MN | MO | MS | MT | NB | NC | ND | NE | NL | NH | NJ | NM | NS | NT | NU | NV | NY | OH | OK | ON | OR | PA | PE | QC | RI | SA | SC | SD | SK | TN | TX | UT | VA | Cartagena | VT | WA | WI | WV | WY | YT | 1 | USA | Canada | Columbia
Canada | AB | CALGARY INT AP | Select | #N/A |  | Canada | AB | CALGARY INT AP | DUBAI INT AP | ADAK NAS | ANNISTON METROPOLITAN AP | BATESVILLE (AWOS) | CASA GRANDE (AWOS) | ABBOTSFORD AP | DHAKA | ALTURAS | AKRON WASHINGTON CO AP | BRIDGEPORT SIKORSKY MEMORIAL | DOVER AFB | CRESTVIEW BOB SIKES AP | ALBANY DOUGHERTY COUNTY AP | BARBERS POINT NAS | ALGONA | BOISE AIR TERMINAL [UO] | AURORA MUNICIPAL | DELAWARE CO JOHNSON | CHANUTE MARTIN JOHNSON AP | BOWLING GREEN WARREN CO AP | ALEXANDRIA ESLER REGIONAL AP | BARNSTABLE MUNI BOA | WINNIPEG | ANDREWS AFB | AUBURN-LEWISTON | ALPENA COUNTY REGIONAL AP | AITKIN NDB(AWOS) | CAPE GIRARDEAU MUNICIPAL AP | COLUMBUS AFB | BILLINGS LOGAN INT ARPT | FREDERICTON | ASHEVILLE REGIONAL ARPT | BISMARCK MUNICIPAL ARPT [ISIS] | AINSWORTH MUNICIPAL | ST JOHNS | BERLIN MUNICIPAL | ATLANTIC CITY INTL AP | ALBUQUERQUE INTL ARPT [ISIS] | GREENWOOD AP | YELLOWKNIFE AP | IQALUIT | ELKO MUNICIPAL ARPT | ADIRONDACK RGNL | AKRON AKRON-CANTON REG AP | ALTUS AFB | BEAUSOLEIL | ASTORIA REGIONAL AIRPORT | ALLENTOWN LEHIGH VALLEY INTL | CHARLOTTETOWN | JONQUIERE | BLOCK ISLAND STATE ARPT | RIYADH | ANDERSON COUNTY AP | ABERDEEN REGIONAL ARPT | MOOSE JAW AP | BRISTOL TRI CITY AIRPORT | ABILENE DYESS AFB | CEDAR CITY MUNICIPAL AP | ABINGDON | CARTAGENA, COLUMBIA | BURLINGTON INTERNATIONAL AP | BELLINGHAM INTL AP | APPLETON/OUTAGAMIE | BECKLEY RALEIGH CO MEM AP | CASPER NATRONA CO INTL AP | WHITEHORSE | 2 | AK | AB | Cartagena
Canada | AB | COP UPPER |  | #N/A |  | United Arab Emirates | AE | COP UPPER |  | AMBLER | AUBURN-OPELIKA APT | BENTONVILLE (AWOS) | DAVIS MONTHAN AFB | AGASSIZ CDA |  | ARCATA AIRPORT | ALAMOSA SAN LUIS VALLEY RGNL | DANBURY MUNICIPAL | WILMINGTON NEW CASTLE CNTY AP | DAYTONA BEACH INTL AP | ALMA BACON COUNTY AP | HILO INTERNATIONAL AP | ATLANTIC | BURLEY MUNICIPAL ARPT | BELLEVILLE SCOTT AFB | EVANSVILLE REGIONAL AP | CONCORDIA BLOSSER MUNI AP | CINCINNATI NORTHERN KY AP | BARKSDALE AFB | BEVERLY MUNI |  | BALTIMORE BLT-WASHNGTN INT | AUGUSTA AIRPORT | ANN ARBOR MUNICIPAL | ALBERT LEA (AWOS) | COLUMBIA REGIONAL AIRPORT | GOLDEN TRI(AWOS) | BOZEMAN GALLATIN FIELD | MONCTON AP | CAPE HATTERAS NWS BLDG | DEVILS LAKE(AWOS) | ALLIANCE MUNICIPAL |  | CONCORD MUNICIPAL ARPT | BELMAR ASC | CARLSBAD CAVERN CITY AIR TERM | HALIFAX |  |  | ELY YELLAND FIELD | ALBANY COUNTY AP | BURKE LAKEFRONT | CLINTON-SHERMAN | BURLINGTON PIERS | AURORA STATE | ALTOONA BLAIR CO ARPT |  | LA BAIE | PAWTUCKET (AWOS) |  | BEAUFORT MCAS | BROOKINGS (AWOS) | PRINCE ALBERT AP | CHATTANOOGA LOVELL FIELD AP | ABILENE REGIONAL AP [UT] | MOAB/CANYONLANDS [UO] | CHARLOTTESVILLE FAA |  | HO CHI MIHN | BREMERTON NATIONAL | EAU CLAIRE COUNTY AP | BLUEFIELD/MERCER CO [NREL] | CHEYENNE MUNICIPAL ARPT |  | 3 | AL | BC
Canada | AB | EDMONTON AP |  | #N/A |  | USA | AK | EDMONTON AP |  | ANAKTUVUK PASS | BIRMINGHAM MUNICIPAL AP | EL DORADO GOODWIN FIELD | DEER VALLEY/PHOENIX | BALLENAS ISLAND |  | BAKERSFIELD MEADOWS FIELD | ASPEN PITKIN CO SAR | GROTON NEW LONDON AP |  | FORT LAUDERDALE | ATHENS BEN EPPS AP | HONOLULU INTL ARPT | BOONE MUNI | CALDWELL (AWOS) | CAHOKIA/ST. LOUIS | FORT WAYNE INTL AP | DODGE CITY REGIONAL AP | FORT CAMPBELL AAF | BATON ROUGE RYAN ARPT | BOSTON LOGAN INT ARPT |  | HAGERSTOWN RGNL RIC | BANGOR INTERNATIONAL AP | BATTLE CREEK KELLOGG AP | ALEXANDRIA MUNICIPAL AP | FARMINGTON | GREENWOOD LEFLORE ARPT | BUTTE BERT MOONEY ARPT |  | CHARLOTTE DOUGLAS INTL ARPT | DICKINSON MUNICIPAL AP | BEATRICE MUNICIPAL |  | DILLANT HOPKINS | CALDWELL/ESSEX CO. | CLAYTON MUNICIPAL AIRPARK | SHEARWATER |  |  | FALLON NAAS | BINGHAMTON EDWIN A LINK FIELD | CINCINNATI MUNICIPAL AP LUNKI | FORT SILL POST FIELD AF | ERIEAU | BAKER MUNICIPAL AP | BRADFORD REGIONAL AP |  | LACADIE | PROVIDENCE T F GREEN STATE AR |  | CHARLESTON INTL ARPT | CHAN GURNEY MUNI | REGINA | CROSSVILLE MEMORIAL AP | ALICE INTL AP | OGDEN HILL AFB | DANVILLE FAA AP |  | MONTPELIER AP | EPHRATA AP FCWOS | GREEN BAY AUSTIN STRAUBEL INT | CHARLESTON YEAGER ARPT | CODY MUNI (AWOS) |  | 4 | AR | MB
Canada | AB | EDMONTON MUN AP |  | #N/A |  | USA | AL | EDMONTON MUN AP |  | ANCHORAGE INTL AP | CAIRNS FIELD FORT RUCKER | FAYETTEVILLE DRAKE FIELD | DOUGLAS BISBEE-DOUGLAS INTL A | COMOX AP |  | BEALE AFB | AURORA BUCKLEY FIELD ANGB | HARTFORD BRADLEY INTL AP |  | FORT LAUDERDALE HOLLYWOOD INT | ATLANTA HARTSFIELD INTL AP | KAHULUI AIRPORT | BURLINGTON MUNICIPAL AP | COEUR D`ALENE(AWOS) | CENTRAL ILLINOIS RG | GRISSOM ARB | EMPORIA MUNICIPAL AP | FORT KNOX GODMAN AAF | ENGLAND AFB | CHICOPEE FALLS WESTO |  | PATUXENT RIVER NAS | BAR HARBOR (AWOS) | BENTON HARBOR/ROSS | AUSTIN MUNI | JEFFERSON CITY MEM | GULFPORT BILOXI INT | CUT BANK MUNI AP |  | CHERRY POINT MCAS | FARGO HECTOR INTERNATIONAL AP | BELLEVUE OFFUTT AFB |  | LACONIA MUNI (AWOS) | CAPE MAY CO | CLOVIS CANNON AFB | SYDNEY AP |  |  | LAS VEGAS MCCARRAN INTL AP | BUFFALO NIAGARA INTL AP | CLEVELAND HOPKINS INTL AP | GAGE AIRPORT | LAGOON CITY | BURNS MUNICIPAL ARPT [UO] | BUTLER CO (AWOS) |  | LASSOMPTION |  |  | COLUMBIA METRO ARPT | ELLSWORTH AFB | SASKATOON | DYERSBURG MUNICIPAL AP | AMARILLO INTERNATIONAL AP [CANYON - UT] | OGDEN HINKLEY AIRPORT | DAVISON AAF |  | RUTLAND STATE | FAIRCHILD AFB | JANESVILLE/ROCK CO. | ELKINS ELKINS-RANDOLPH CO ARP | GILLETTE/GILLETTE-C |  | 5 | AZ | NB
Canada | AB | EDMONTON NAMAO |  | #N/A |  | USA | AR | EDMONTON NAMAO |  | ANCHORAGE MERRILL FIELD | DOTHAN MUNICIPAL AP | FLIPPIN (AWOS) | FLAGSTAFF PULLIAM ARPT | CRANBROOK AP |  | BISHOP AIRPORT | BARRANQUILLA | HARTFORD BRAINARD FD |  | FORT MYERS PAGE FIELD | AUGUSTA BUSH FIELD | KANEOHE BAY MCAS | CARROLL | IDAHO FALLS FANNING FIELD | CHICAGO MIDWAY AP | HUNTINGBURG | FORT RILEY MARSHALL AAF | HENDERSON CITY | FORT POLK AAF | LAWRENCE MUNI |  | SALISBURY WICOMICO CO AP | CARIBOU MUNICIPAL ARPT | CADILLAC WEXFORD CO AP | BAUDETTE INTERNATIONAL AP | JOPLIN MUNICIPAL AP | HATTIESBURG LAUREL | GLASGOW INTL ARPT |  | DARE CO RGNL | GRAND FORKS AF | BREWSTER FIELD ARPT |  | LEBANON MUNICIPAL | MCGUIRE AFB | CLOVIS MUNI (AWOS) |  |  |  | LOVELOCK DERBY FIELD | ELMIRA CORNING REGIONAL AP | COLUMBUS PORT COLUMBUS INTL A | HOBART MUNICIPAL AP | LONDON AP | CORVALLIS MUNI | DUBOIS FAA AP |  | LENNOXVILLE |  |  | FLORENCE REGIONAL AP | HURON REGIONAL ARPT |  | JACKSON MCKELLAR-SIPES REGL A | AUSTIN MUELLER MUNICIPAL AP [UT] | PROVO MUNI (AWOS) | FARMVILLE |  | SPRINGFIELD/HARTNES | FELTS FLD | LA CROSSE MUNICIPAL ARPT | HARRISON MARION RGN | JACKSON HOLE |  | 6 | CA | ON
Canada | AB | FORT MCMURRAY AP |  | #N/A |  | USA | AZ | FORT MCMURRAY AP |  | ANCHORAGE/ELMENDORF | HUNTSVILLE INTL/JONES FIELD | FORT SMITH REGIONAL AP | GRAND CANYON NATL P | DISCOVERY ISLAND |  | BLUE CANYON AP | BROOMFIELD/JEFFCO [BOULDER - SURFRAD] | NEW HAVEN TWEED AIRPORT |  | GAINESVILLE REGIONAL AP | BRUNSWICK GOLDEN IS | KONA INTL AT KEAHOL | CEDAR RAPIDS MUNICIPAL AP | JOSLIN FLD MAGIC VA [TWIN FALLS - UO] | CHICAGO OHARE INTL AP | INDIANAPOLIS INTL AP | GARDEN CITY MUNICIPAL AP | JACKSON JULIAN CARROLL AP | LAFAYETTE REGIONAL AP | MARTHAS VINEYARD |  |  | HOULTON INTL ARPT | CHIPPEWA CO INTL | BEMIDJI MUNICIPAL | KAISER MEM (AWOS) | JACKSON INTERNATIONAL AP | GLENDIVE(AWOS) |  | ELIZABETH CITY COAST GUARD AI [NREL] | GRAND FORKS INTERNATIONAL AP | BROKEN BOW MUNI |  | MANCHESTER AIRPORT | MILLVILLE MUNICIPAL AP | DEMING MUNI |  |  |  | MERCURY DESERT ROCK AP [SURFRAD] | FORT DRUM/WHEELER-S | DAYTON INTERNATIONAL AIRPORT | LAWTON MUNICIPAL | NORTH BAY AP | EUGENE MAHLON SWEET ARPT [UO] | ERIE INTERNATIONAL AP |  | MC TAVISH |  |  | GREENVILLE DOWNTOWN AP | MITCHELL (AWOS) |  | KNOXVILLE MCGHEE TYSON AP | BROWNSVILLE S PADRE ISL INTL | SAINT GEORGE (AWOS) | FRANKLIN NAAS |  |  | GRAY AAF | LONE ROCK FAA AP | HUNTINGTON TRI-STATE ARPT | LANDER HUNT FIELD |  | 7 | CO | PE
Canada | AB | GRAND PRAIRIE |  | #N/A |  | Canada | BC | GRAND PRAIRIE |  | ANIAK AIRPORT | MAXWELL AFB | HARRISON FAA AP | KINGMAN (AMOS) | ENTRANCE ISLAND |  | BLYTHE RIVERSIDE CO ARPT | CALI | OXFORD (AWOS) |  | HOMESTEAD AFB | BRUNSWICK MALCOLM MCKINNON AP | LIHUE AIRPORT | CHARITON | LEWISTON NEZ PERCE CNTY AP | CHICAGO/WAUKEGAN | LAFAYETTE PURDUE UNIV AP | GOODLAND RENNER FIELD | LEXINGTON BLUEGRASS AP | LAKE CHARLES REGIONAL ARPT | NANTUCKET MEMORIAL AP |  |  | MILLINOCKET MUNICIPAL AP | DETROIT CITY AIRPORT | BENSON MUNI | KANSAS CITY DOWNTOWN AP | KEESLER AFB | GREAT FALLS INTL ARPT |  | FAYETTEVILLE POPE AFB | JAMESTOWN MUNICIPAL ARPT | COLUMBUS MUNI |  | MOUNT WASHINGTON | NEWARK INTERNATIONAL ARPT | FARMINGTON FOUR CORNERS REGL |  |  |  | NELLIS AFB | GLENS FALLS AP | FINDLAY AIRPORT | MCALESTER MUNICIPAL AP | OTTAWA | KLAMATH FALLS INTL AP [UO] | FRANKLIN |  | MONT JOLI AB |  |  | GREER GREENV-SPARTANBRG AP | MOBRIDGE |  | MEMPHIS INTERNATIONAL AP | CAMP MABRY | SALT LAKE CITY INT ARPT [ISIS] | HILLSVILLE |  |  | HANFORD | MADISON DANE CO REGIONAL ARPT [ISIS] | LEWISBURG/GREENBRIE | LARAMIE GENERAL BREES FIELD |  | 8 | CT | QC
Canada | AB | LACOMBE |  | #N/A |  | India | BD | LACOMBE |  | ANNETTE ISLAND AP | MOBILE DOWNTOWN AP | JONESBORO MUNI | LUKE AFB | ESQUIMALT HARBOUR |  | BURBANK-GLENDALE-PASADENA AP | CARTAGENA |  |  | JACKSONVILLE INTL ARPT | COLUMBUS METROPOLITAN ARPT | MOLOKAI (AMOS) | CHARLES CITY | MOUNTAIN HOME AFB | DECATUR | MONROE CO | GREAT BEND (AWOS) | LONDON-CORBIN AP | MONROE REGIONAL AP | NEW BEDFORD RGNL |  |  | NORTHERN AROOSTOOK | DETROIT METROPOLITAN ARPT | BRAINERD/WIELAND | KANSAS CITY INT ARPT | MCCOMB PIKE COUNTY AP | HAVRE CITY-COUNTY AP |  | FAYETTEVILLE RGNL G | MINOT AFB | FALLS CITY/BRENNER |  | PEASE INTL TRADEPOR | TETERBORO AIRPORT | GALLUP SEN CLARKE FLD |  |  |  | RENO TAHOE INTERNATIONAL AP | ISLIP LONG ISL MACARTHUR AP | MANSFIELD LAHM MUNICIPAL ARPT | OKLAHOMA CITY TINKER AFB | PETERBOROUGH AP | LA GRANDE MUNI AP | HARRISBURG CAPITAL CITY ARPT |  | MONT-ORFORD |  |  | MYRTLE BEACH AFB | PIERRE MUNICIPAL AP |  | NASHVILLE INTERNATIONAL AP | CHILDRESS MUNICIPAL AP | VERNAL | HOT SPRINGS/INGALLS |  |  | HOQUIAM AP | MANITOWOC MUNI AWOS | MARTINSBURG EASTERN WV REG AP | RAWLINS MUNICIPAL AP |  | 9 | DE | SK
Canada | AB | LETHBRIDGE |  | #N/A |  | USA | CA | LETHBRIDGE |  | ANVIK | MOBILE REGIONAL AP | LITTLE ROCK ADAMS FIELD | PAGE MUNI (AMOS) | FORT NELSON |  | CAMARILLO (AWOS) | COLORADO SPRINGS MUNI AP |  |  | JACKSONVILLE NAS | DEKALB PEACHTREE |  | CLARINDA | POCATELLO REGIONAL AP | MARION REGIONAL | NEW DELHI SAFDARJUNG AP | HAYS MUNI (AWOS) | LOUISVILLE BOWMAN FIELD | NEW IBERIA NAAS | NORTH ADAMS |  |  | PORTLAND INTL JETPORT | DETROIT WILLOW RUN AP | CAMBRIDGE MUNI | KIRKSVILLE REGIONAL AP | MERIDIAN KEY FIELD | HELENA REGIONAL AIRPORT |  | FORT BRAGG SIMMONS AAF | MINOT FAA AP | FREMONT MUNI ARPT |  |  | TRENTON MERCER COUNTY AP | HOLLOMAN AFB |  |  |  | TONOPAH AIRPORT | JAMESTOWN (AWOS) | OHIO STATE UNIVERSI | OKLAHOMA CITY WILL ROGERS WOR | PORT WELLER | LAKEVIEW (AWOS) | JOHNSTOWN CAMBRIA COUNTY AP |  | MONTREAL |  |  | SUMTER SHAW AFB | RAPID CITY REGIONAL ARPT |  |  | COLLEGE STATION EASTERWOOD FL | WENDOVER USAF AUXILIARY FIELD | LANGLEY AFB |  |  | KELSO WB AP | MARSHFIELD MUNI | MORGANTOWN HART FIELD | RIVERTON MUNICIPL AP |  | 10 | FL | YT
Canada | AB | MEDICINE AP |  | #N/A |  | USA | CO | MEDICINE AP |  | BARROW W POST-W ROGERS ARPT [NSA - ARM] | MONTGOMERY DANNELLY FIELD | LITTLE ROCK AFB | PHOENIX SKY HARBOR INTL AP | FORT SAINT JOHN |  | CAMP PENDLETON MCAS | CORTEZ/MONTEZUMA |  |  | JACKSONVILLE/CRAIG | FORT BENNING LAWSON |  | CLINTON MUNI (AWOS) | SALMON/LEMHI (AWOS) | MOLINE QUAD CITY INTL AP | PATNA | HILL CITY MUNICIPAL AP | LOUISVILLE STANDIFORD FIELD | NEW ORLEANS ALVIN CALLENDER F | NORWOOD MEMORIAL |  |  | PRESQUE ISLE MUNICIP | ESCANABA (AWOS) | CLOQUET (AWOS) | POPLAR BLUFF(AMOS) | MERIDIAN NAAS | KALISPELL GLACIER PK INT AR |  | GOLDSBORO SEYMOUR JOHNSON AFB | WILLISTON SLOULIN INTL AP | GRAND ISLAND CENTRAL NE REGIO |  |  |  | LAS VEGAS MUNICIPAL ARPT |  |  |  | WINNEMUCCA MUNICIPAL ARPT | MASSENA AP | TOLEDO EXPRESS AIRPORT | OKLAHOMA CITY/WILEY | SAULT STE MARIE | MEDFORD ROGUE VALLEY INTL AP [ASHLAND - UO] | LANCASTER |  | MONTREAL-MIRABEL |  |  |  | SIOUX FALLS FOSS FIELD |  |  | CORPUS CHRISTI INTL ARPT [UT] |  | LEESBURG/GODFREY |  |  | MOSES LAKE GRANT COUNTY AP | MILWAUKEE MITCHELL INTL AP | PARKERSBURG WOOD COUNTY AP | SHERIDAN COUNTY ARPT |  | 11 | GA | -
Canada | AB | RED DEER AP |  | #N/A |  | Colombia | CO | RED DEER AP |  | BETHEL AIRPORT | MUSCLE SHOALS REGIONAL AP | PINE BLUFF FAA AP | PRESCOTT LOVE FIELD | KAMLOOPS AP |  | CARLSBAD/PALOMAR | CRAIG-MOFFAT |  |  | KEY WEST INTL ARPT | FULTON CO ARPT BROW |  | COUNCIL BLUFFS |  | MOUNT VERNON (AWOS) | SOUTH BEND MICHIANA RGNL AP | HUTCHINSON MUNICIPAL AP | PADUCAH BARKLEY REGIONAL AP | NEW ORLEANS INTL ARPT | OTIS ANGB |  |  | ROCKLAND/KNOX(AWOS) | FLINT BISHOP INTL ARPT | CRANE LAKE (AWOS) | SPRINGFIELD REGIONAL ARPT | NATCHEZ/HARDY(AWOS) | LEWISTOWN MUNICIPAL ARPT |  | GREENSBORO PIEDMONT TRIAD INT |  | HASTINGS MUNICIPAL |  |  |  | ROSWELL INDUSTRIAL AIR PARK |  |  |  |  | MONTICELLO(AWOS) | YOUNGSTOWN REGIONAL AIRPORT | PONCA CITY MUNICIPAL AP [SGP - ARM] | SUDBURY AP | NORTH BEND MUNI AIRPORT | MIDDLETOWN HARRISBURG INTL AP |  | NICOLET |  |  |  | WATERTOWN MUNICIPAL AP |  |  | CORPUS CHRISTI NAS |  | LYNCHBURG REGIONAL ARPT |  |  | OLYMPIA AIRPORT | MINOCQUA/WOODRUFF | WHEELING OHIO COUNTY AP | WORLAND MUNICIPAL |  | 12 | HI | -
Canada | AB | SPRINGBANK |  | #N/A |  | USA | CT | SPRINGBANK |  | BETTLES FIELD | TUSCALOOSA MUNICIPAL AP | ROGERS (AWOS) | SAFFORD (AMOS) | KELOWNA AP |  | CHINO AIRPORT | DENVER INTL AP |  |  | KEY WEST NAS | HUNTER AAF |  | CRESTON |  | PEORIA GREATER PEORIA AP | TERRE HAUTE HULMAN REGIONAL A | LIBERAL MUNI | SOMERSET(AWOS) | NEW ORLEANS LAKEFRONT AP | PLYMOUTH MUNICIPAL |  |  | SANFORD MUNI (AWOS) | GRAND RAPIDS KENT COUNTY INT | CROOKSTON MUNI FLD | ST JOSEPH ROSECRANS MEMORIAL | TUPELO C D LEMONS ARPT | LIVINGSTON MISSION FIELD |  | HICKORY REGIONAL AP |  | KEARNEY MUNI (AWOS) |  |  |  | SANTA FE COUNTY MUNICIPAL AP |  |  |  |  | NEW YORK CENTRAL PRK OBS BELV | ZANESVILLE MUNICIPAL AP | STILLWATER RGNL | THUNDER BAY AP | PENDLETON E OR REGIONAL AP | PHILADELPHIA INTERNATIONAL AP |  | POINT-AU-PERE | [6 empty] | COTULLA FAA AP |  | MANASSAS MUNI(AWOS) |  |  | PASCO | MOSINEE/CENTRAL WI |  |  |  | 13 | IA | -
United Arab Emirates | AE | DUBAI INT AP |  | #N/A |  | USA | DE |  |  | BIG DELTA ALLEN AAF |  | SILOAM SPRING(AWOS) | SCOTTSDALE MUNI | MALAHAT |  | CHULA VISTA BROWN FIELD NAAS | DENVER/CENTENNIAL [GOLDEN - NREL] |  |  | MACDILL AFB | MACON MIDDLE GA REGIONAL AP |  | DECORAH |  | QUINCY MUNI BALDWIN FLD |  | MANHATTAN RGNL |  | PATTERSON MEMORIAL | PROVINCETOWN (AWOS) |  |  | WATERVILLE (AWOS) | HANCOCK HOUGHTON CO AP | DETROIT LAKES(AWOS) | ST LOUIS LAMBERT INT ARPT |  | MILES CITY MUNICIPAL ARPT |  | JACKSONVILLE (AWOS) |  | LINCOLN MUNICIPAL ARPT |  |  |  | SIERRA BLANCA RGNL |  |  |  |  | NEW YORK J F KENNEDY INT AR |  | TULSA INTERNATIONAL AIRPORT | TIMMINS AP | PORTLAND INTERNATIONAL AP | PHILADELPHIA NE PHILADELPHIA |  | QUEBEC AP | [6 empty] | COX FLD |  | MARION / WYTHEVILLE |  |  | PULLMAN/MOSCOW RGNL | PHILLIPS/PRICE CO. |  |  |  | 14 | ID | -
USA | AK | ADAK NAS |  | #N/A |  | USA | FL |  |  | BIG RIVER LAKE |  | SPRINGDALE MUNI | TUCSON INTERNATIONAL AP | NORTH VANCOUVER |  | CONCORD CONCORD-BUCHANAN FIEL | DURANGO/LA PLATA CO |  |  | MARATHON AIRPORT | MARIETTA DOBBINS AFB |  | DENISON |  | ROCKFORD GREATER ROCKFORD AP |  | MCCONNELL AFB |  | SHREVEPORT DOWNTOWN | WESTFIELD BARNES MUNI AP |  |  | WISCASSET | HOUGHTON LAKE ROSCOMMON CO AR | DULUTH INTERNATIONAL ARPT | ST LOUIS SPIRIT OF ST LOUIS A |  | MISSOULA INTERNATIONAL AP |  | NEW BERN CRAVEN CO REGL AP |  | MCCOOK MUNICIPAL |  |  |  | TAOS MUNI APT(AWOS) |  |  |  |  | NEW YORK LAGUARDIA ARPT |  | VANCE AFB | TORONTO AP | PORTLAND/HILLSBORO | PITTSBURGH ALLEGHENY CO AP |  | SHERBROOKE AP | [6 empty] | DALHART MUNICIPAL AP |  | MARTINSVILLE |  |  | QUILLAYUTE STATE AIRPORT | RHINELANDER ONEIDA |  |  |  | 15 | IL | -
USA | AK | AMBLER |  | #N/A |  | USA | GA |  |  | BIRCHWOOD |  | STUTTGART (AWOS) | WINSLOW MUNICIPAL AP | PENTICTON AP |  | CRESCENT CITY FAA AI | EAGLE COUNTY AP |  |  | MAYPORT NS | MOODY AFB/VALDOSTA |  | DES MOINES INTL AP |  | SOUTHERN ILLINOIS |  | NEWTON (AWOS) |  | SHREVEPORT REGIONAL ARPT | WORCESTER REGIONAL ARPT |  |  |  | HOWELL | ELY MUNI | VICHY ROLLA NATL ARPT |  | SIDNEY-RICHLAND |  | NEW RIVER MCAF |  | NORFOLK KARL STEFAN MEM ARPT |  |  |  | TRUTH OR CONSEQUENCES MUNI AP |  |  |  |  | NIAGARA FALLS AF |  |  | TORONTO ISLAND AP | PORTLAND/TROUTDALE | PITTSBURGH INTERNATIONAL AP |  | ST ANICET | [6 empty] | DALLAS-FORT WORTH INTL AP |  | MELFA/ACCOMACK ARPT |  |  | RENTON MUNI | RICE LAKE MUNICIPAL |  |  |  | 16 | IN | -
USA | AK | ANAKTUVUK PASS |  | #N/A |  | USA | HI |  |  | COLD BAY ARPT |  | TEXARKANA WEBB FIELD | YUMA INTL ARPT | PITT MEADOWS |  | DAGGETT BARSTOW-DAGGETT AP | FORT COLLINS (AWOS) |  |  | MELBOURNE REGIONAL AP | ROME R B RUSSELL AP |  | DUBUQUE REGIONAL AP |  | SPRINGFIELD CAPITAL AP |  | OLATHE/JOHNSON CO. | [6 empty] | IRON MOUNTAIN/FORD | EVELETH MUNI (AWOS) | WHITEMAN AFB |  | WOLF POINT INTL [FORT PECK - SURFRAD] |  | PITT GREENVILLE ARP |  | NORTH PLATTE REGIONAL AP | [8 empty] | POUGHKEEPSIE DUTCHESS CO AP |  |  | TORONTO | REDMOND ROBERTS FIELD | READING SPAATZ FIELD |  | STE ANNE DE BELLEVUE | [6 empty] | DALLAS/ADDISON ARPT |  | NEWPORT NEWS |  |  | SEATTLE BOEING FIELD [ISIS] | STURGEON BAY |  |  |  | 17 | KS | -
USA | AK | ANCHORAGE INTL AP |  | #N/A |  | USA | IA |  |  | CORDOVA |  | WALNUT RIDGE (AWOS) | YUMA MCAS | PRINCE GEORGE |  | EDWARDS AFB | GRAND JUNCTION WALKER FIELD |  |  | MIAMI INTL AP | SAVANNAH INTL AP |  | ESTHERVILLE MUNI |  | STERLING ROCKFALLS |  | RUSSELL MUNICIPAL AP | [6 empty] | IRONWOOD (AWOS) | FAIRMONT MUNI(AWOS) |  |  |  |  | RALEIGH DURHAM INTERNATIONAL |  | OMAHA EPPLEY AIRFIELD | [8 empty] | REPUBLIC |  |  | TRENTON AP | ROSEBURG REGIONAL AP | STATE COLLEGE [PENN STATE - SURFRAD] |  | STE FOY | [6 empty] | DALLAS/REDBIRD ARPT |  | NORFOLK INTERNATIONAL AP |  |  | SEATTLE SEATTLE-TACOMA INTL A | WATERTOWN |  |  |  | 18 | KY | -
USA | AK | ANCHORAGE MERRILL FIELD |  | #N/A |  | USA | ID |  |  | DEADHORSE |  |  |  | SMITHERS AP |  | FRESNO YOSEMITE INTL AP | GREELEY/WELD (AWOS) |  |  | MIAMI/KENDALL-TAMIA | VALDOSTA WB AIRPORT |  | FAIR FIELD |  | UNIV OF ILLINOIS WI [BONDVILLE - SURFRAD] |  | SALINA MUNICIPAL AP | [6 empty] | JACKSON REYNOLDS FIELD | FARIBAULT MUNI AWOS |  |  |  |  | ROCKY MOUNT WILSON |  | OMAHA WSFO | [8 empty] | ROCHESTER GREATER ROCHESTER I |  |  | WINDSOR | SALEM MCNARY FIELD | WASHINGTON (AWOS) |  | TROIS RIVIERES | [6 empty] | DEL RIO [UT] |  | NORFOLK NAS |  |  | SNOHOMISH CO | WAUSAU MUNICIPAL ARPT |  |  |  | 19 | LA | -
USA | AK | ANCHORAGE/ELMENDORF |  | #N/A |  | USA | IL |  |  | DILLINGHAM (AMOS) |  |  |  | SUMMERLAND |  | FULLERTON MUNICIPAL | GUNNISON CO. (AWOS) |  |  | MIAMI/OPA LOCKA | WARNER ROBINS AFB |  | FORT DODGE (AWOS) |  | W. CHICAGO/DU PAGE |  | TOPEKA FORBES FIELD | [6 empty] | KALAMAZOO BATTLE CR | FLYING CLOUD |  |  |  |  | SOUTHERN PINES AWOS |  | SCOTTSBLUFF W B HEILIG FIELD | [8 empty] | STEWART FIELD |  |  |  | SEXTON SUMMIT | WILKES-BARRE SCRANTON INTL AP |  | VARENNES | [6 empty] | DEL RIO LAUGHLIN AFB |  | OCEANA NAS |  |  | SPOKANE INTERNATIONAL AP [CHENEY - UO] | WITTMAN RGNL |  |  |  | 20 | MA | -
USA | AK | ANIAK AIRPORT |  | #N/A |  | USA | IN |  |  | DUTCH HARBOR |  |  |  | VANCOUVER |  | HAYWARD AIR TERM | HAYDEN/YAMPA (AWOS) |  |  | NAPLES MUNICIPAL |  |  | FORT MADISON |  |  |  | TOPEKA MUNICIPAL AP | [6 empty] | LANSING CAPITAL CITY ARPT | FOSSTON(AWOS) |  |  |  |  | WILMINGTON INTERNATIONAL ARPT |  | SIDNEY MUNICIPAL AP | [8 empty] | SYRACUSE HANCOCK INT ARPT |  |  |  |  | WILLIAMSPORT REGIONAL AP | [8 empty] | DRAUGHON MILLER CEN |  | QUANTICO MCAS |  |  | STAMPEDE PASS |  |  |  |  | 21 | MD | -
USA | AK | ANNETTE ISLAND AP |  | #N/A |  | India | IN |  |  | EMMONAK |  |  |  | VERNON |  | IMPERIAL | LA JUNTA MUNICIPAL AP |  |  | NASA SHUTTLE FCLTY |  |  | KEOKUK MUNI |  |  |  | WICHITA MID-CONTINENT AP | [6 empty] | MANISTEE (AWOS) | GLENWOOD (ASOS) |  |  |  |  | WINSTON-SALEM REYNOLDS AP |  | TEKAMAH (ASOS) | [8 empty] | UTICA ONEIDA COUNTY AP |  |  |  |  | WILLOW GROVE NAS | [8 empty] | EL PASO INTERNATIONAL AP [UT] |  | RICHMOND INTERNATIONAL AP |  |  | TACOMA MCCHORD AFB |  |  |  |  | 22 | ME | -
USA | AK | ANVIK |  | #N/A |  | USA | KS |  |  | FAIRBANKS INTL ARPT |  |  |  | VICTORIA AP |  | JACK NORTHROP FLD H | LAMAR MUNICIPAL |  |  | OCALA MUNI (AWOS) |  |  | KNOXVILLE |  |  |  | WICHITA/COL. JABARA | [6 empty] | MENOMINEE (AWOS) | GRAND RAPIDS(AWOS) | [6 empty] | VALENTINE MILLER FIELD | [8 empty] | WATERTOWN AP | [13 empty] | FORT HOOD |  | ROANOKE REGIONAL AP |  |  | TACOMA NARROWS |  |  |  |  | 23 | MI | -
USA | AK | BARROW W POST-W ROGERS ARPT [NSA - ARM] |  | #N/A |  | USA | KY |  |  | FAIRBANKS/EIELSON A |  |  |  | VICTORIA |  | LANCASTER GEN WM FOX FIELD | LEADVILLE/LAKE CO. |  |  | ORLANDO EXECUTIVE AP |  |  | LE MARS | [10 empty] | MOUNT CLEMENS SELFRIDGE FLD | HALLOCK | [15 empty] | WESTHAMPTON GABRESKI AP | [13 empty] | FORT WORTH ALLIANCE |  | SHANNON ARPT |  |  | THE DALLES MUNICIPAL ARPT |  |  |  |  | 24 | MN | -
USA | AK | BETHEL AIRPORT |  | #N/A |  | USA | LA |  |  | FORT YUKON |  |  |  | VICTORIA UNIV |  | LEMOORE REEVES NAS | LIMON |  |  | ORLANDO INTL ARPT |  |  | MASON CITY MUNICIPAL ARPT | [10 empty] | MUSKEGON COUNTY ARPT | HIBBING CHISHOLM-HIBBING AP | [15 empty] | WHITE PLAINS WESTCHESTER CO A | [13 empty] | FORT WORTH MEACHAM |  | STAUNTON/SHENANDOAH |  |  | WALLA WALLA CITY COUNTY AP |  |  |  |  | 25 | MO | -
USA | AK | BETTLES FIELD |  | #N/A |  | USA | MA |  |  | GAMBELL |  |  |  | W VANCOUVER |  | LIVERMORE MUNICIPAL | MONTROSE CO. ARPT |  |  | ORLANDO SANFORD AIRPORT |  |  | MONTICELLO MUNI | [10 empty] | OAKLAND CO INTL | HUTCHINSON (AWOS) | [29 empty] | FORT WORTH NAS |  | VIRGINIA TECH ARPT |  |  | WENATCHEE/PANGBORN |  |  |  |  | 26 | MS | -
USA | AK | BIG DELTA ALLEN AAF |  | #N/A |  | USA | MB |  |  | GULKANA INTERMEDIATE FIELD |  |  |  | WHISTLER |  | LOMPOC (AWOS) | PUEBLO MEMORIAL AP |  |  | PANAMA CITY BAY CO |  |  | MUSCATINE | [10 empty] | OSCODA WURTSMITH AFB | INTERNATIONAL FALLS INTL AP | [29 empty] | GALVESTON/SCHOLES |  | WASHINGTON DC DULLES INT AR [STERLING - ISIS] |  |  | WHIDBEY ISLAND NAS |  |  |  |  | 27 | MT | -
USA | AK | BIG RIVER LAKE |  | #N/A |  | USA | MD |  |  | GUSTAVUS |  |  |  | WHITE ROCK |  | LONG BEACH DAUGHERTY FLD | RIFLE/GARFIELD RGNL |  |  | PENSACOLA FOREST SHERMAN NAS |  |  | NEWTON MUNI | [10 empty] | PELLSTON EMMET COUNTY AP | LITCHFIELD MUNI | [29 empty] | GEORGETOWN (AWOS) |  | WASHINGTON DC REAGAN AP |  |  | WILLIAM R FAIRCHILD |  |  |  |  | 28 | NC | -
USA | AK | BIRCHWOOD |  | #N/A |  | USA | ME |  |  | HOMER ARPT | [5 empty] | LOS ANGELES INTL ARPT | TRINIDAD LAS ANIMAS COUNTY AP |  |  | PENSACOLA REGIONAL AP |  |  | OELWEN | [10 empty] | SAGINAW TRI CITY INTL AP | LITTLE FALLS (AWOS) | [29 empty] | HARLINGEN RIO GRANDE VALLEY I |  | WINCHESTER RGNL |  |  | YAKIMA AIR TERMINAL |  |  |  |  | 29 | ND | -
USA | AK | COLD BAY ARPT |  | #N/A |  | USA | MI |  |  | HOOPER BAY | [5 empty] | MARCH AFB |  |  |  | SARASOTA BRADENTON |  |  | ORANGE CITY | [10 empty] | SAULT STE MARIE SANDERSON FIE | MANKATO(AWOS) | [29 empty] | HONDO MUNICIPAL AP |  | WISE/LONESOME PINE | [7 empty] | 30 | NE | -
USA | AK | CORDOVA |  | #N/A |  | USA | MN |  |  | HYDABURG SEAPLANE | [5 empty] | MERCED/MACREADY FLD |  |  |  | SOUTHWEST FLORIDA I |  |  | OTTUMWA INDUSTRIAL AP | [10 empty] | ST.CLAIR COUNTY INT | MINNEAPOLIS-ST PAUL INT ARP | [29 empty] | HOUSTON BUSH INTERCONTINENTAL | [9 empty] | 31 | NL | -
USA | AK | DEADHORSE |  | #N/A |  | USA | MO |  |  | ILIAMNA ARPT | [5 empty] | MODESTO CITY-COUNTY AP |  |  |  | ST LUCIE CO INTL |  |  | RED OAK | [10 empty] | TRAVERSE CITY CHERRY CAPITAL | MINNEAPOLIS/CRYSTAL | [29 empty] | HOUSTON ELLINGTON AFB [CLEAR LAKE - UT] | [9 empty] | 32 | NH | -
USA | AK | DILLINGHAM (AMOS) |  | #N/A |  | USA | MS |  |  | JUNEAU INT ARPT | [5 empty] | MONTAGUE SISKIYOU COUNTY AP |  |  |  | ST PETERSBURG ALBERT WHITTED |  |  | SHELDON | [11 empty] | MORA MUNI (AWOS) | [29 empty] | HOUSTON WILLIAM P HOBBY AP | [9 empty] | 33 | NJ | -
USA | AK | DUTCH HARBOR |  | #N/A |  | USA | MT |  |  | KAKE SEAPLANE BASE | [5 empty] | MONTEREY NAF |  |  |  | ST PETERSBURG CLEAR |  |  | SHENANDOAH MUNI | [11 empty] | MORRIS MUNI (AWOS) | [29 empty] | HOUSTON/D.W. HOOKS | [9 empty] | 34 | NM | -
USA | AK | EMMONAK |  | #N/A |  | Canada | NB |  |  | KENAI MUNICIPAL AP | [5 empty] | MOUNTAIN VIEW MOFFETT FLD NAS |  |  |  | TALLAHASSEE REGIONAL AP [ISIS] |  |  | SIOUX CITY SIOUX GATEWAY AP | [11 empty] | NEW ULM MUNI (AWOS) | [29 empty] | KINGSVILLE | [9 empty] | 35 | NS | -
USA | AK | FAIRBANKS INTL ARPT |  | #N/A |  | USA | NC |  |  | KETCHIKAN INTL AP | [5 empty] | NAPA CO. AIRPORT |  |  |  | TAMPA INTERNATIONAL AP |  |  | SPENCER | [11 empty] | ORR | [29 empty] | LAREDO INTL AP [UT] | [9 empty] | 36 | NT | -
USA | AK | FAIRBANKS/EIELSON A |  | #N/A |  | USA | ND |  |  | KING SALMON ARPT | [5 empty] | NEEDLES AIRPORT |  |  |  | TYNDALL AFB |  |  | STORM LAKE | [11 empty] | OWATONNA (AWOS) | [29 empty] | LONGVIEW GREGG COUNTY AP [OVERTON - UT] | [9 empty] | 37 | NU | -
USA | AK | FORT YUKON |  | #N/A |  | USA | NE |  |  | KODIAK AIRPORT | [5 empty] | OAKLAND METROPOLITAN ARPT |  |  |  | VALPARAISO EGLIN AFB |  |  | WASHINGTON | [11 empty] | PARK RAPIDS MUNICIPAL AP | [29 empty] | LUBBOCK INTERNATIONAL AP | [9 empty] | 38 | NV | -
USA | AK | GAMBELL |  | #N/A |  | USA | NL |  |  | KOTZEBUE RALPH WEIN MEMORIAL | [5 empty] | OXNARD AIRPORT |  |  |  | VALPARAISO HURLBURT |  |  | WATERLOO MUNICIPAL AP | [11 empty] | PIPESTONE (AWOS) | [29 empty] | LUFKIN ANGELINA CO | [9 empty] | 39 | NY | -
USA | AK | GULKANA INTERMEDIATE FIELD |  | #N/A |  | USA | NH |  |  | LAKE HOOD SEAPLANE | [5 empty] | PALM SPRINGS INTL |  |  |  | VERO BEACH MUNICIPAL ARPT |  |  | WEBSTER CITY | [11 empty] | RED WING | [29 empty] | MARFA AP | [9 empty] | 40 | OH | -
USA | AK | GUSTAVUS |  | #N/A |  | USA | NJ |  |  | MCGRATH ARPT | [5 empty] | PALM SPRINGS THERMAL AP |  |  |  | WHITING FIELD NAAS | [14 empty] | REDWOOD FALLS MUNI | [29 empty] | MC GREGOR (AWOS) | [9 empty] | 41 | OK | -
USA | AK | HOMER ARPT |  | #N/A |  | USA | NM |  |  | MEKORYUK | [5 empty] | PALMDALE AIRPORT | [18 empty] | ROCHESTER INTERNATIONAL ARPT | [29 empty] | MCALLEN MILLER INTL AP [EDINBURG - UT] | [9 empty] | 42 | OR | -
USA | AK | HOOPER BAY |  | #N/A |  | USA | NS |  |  | MIDDLETON ISLAND AUT | [5 empty] | PASO ROBLES MUNICIPAL ARPT | [18 empty] | ROSEAU MUNI (AWOS) | [29 empty] | MIDLAND INTERNATIONAL AP | [9 empty] | 43 | PA | -
USA | AK | HYDABURG SEAPLANE |  | #N/A |  | USA | NT |  |  | NENANA MUNICIPAL AP | [5 empty] | POINT MUGU NF | [18 empty] | SILVER BAY | [29 empty] | MINERAL WELLS MUNICIPAL AP | [9 empty] | 44 | RI | -
USA | AK | ILIAMNA ARPT |  | #N/A |  | USA | NU |  |  | NOME MUNICIPAL ARPT | [5 empty] | PORTERVILLE (AWOS) | [18 empty] | SOUTH ST PAUL MUNI | [29 empty] | NACOGDOCHES (AWOS) | [9 empty] | 45 | SC | -
USA | AK | JUNEAU INT ARPT |  | #N/A |  | USA | NV |  |  | NORTHWAY AIRPORT | [5 empty] | RED BLUFF MUNICIPAL ARPT | [18 empty] | ST CLOUD REGIONAL ARPT | [29 empty] | PALACIOS MUNICIPAL AP | [9 empty] | 46 | SD | -
USA | AK | KAKE SEAPLANE BASE |  | #N/A |  | USA | NY |  |  | PALMER MUNICIPAL | [5 empty] | REDDING MUNICIPAL ARPT | [18 empty] | ST PAUL DOWNTOWN AP | [29 empty] | PORT ARTHUR JEFFERSON COUNTY | [9 empty] | 47 | TN | -
USA | AK | KENAI MUNICIPAL AP |  | #N/A |  | USA | OH |  |  | PETERSBURG | [5 empty] | RIVERSIDE MUNI | [18 empty] | THIEF RIVER(AWOS) | [29 empty] | RANDOLPH AFB | [9 empty] | 48 | TX | -
USA | AK | KETCHIKAN INTL AP |  | #N/A |  | USA | OK |  |  | POINT HOPE (AWOS) | [5 empty] | SACRAMENTO EXECUTIVE ARPT | [18 empty] | WHEATON NDB (AWOS) | [29 empty] | ROCKPORT/ARANSAS CO | [9 empty] | 49 | UT | -
USA | AK | KING SALMON ARPT |  | #N/A |  | Canada | ON |  |  | PORT HEIDEN | [5 empty] | SACRAMENTO METROPOLITAN AP | [18 empty] | WILLMAR | [29 empty] | SAN ANGELO MATHIS FIELD | [9 empty] | 50 | VA | -
USA | AK | KODIAK AIRPORT |  | #N/A |  | USA | OR |  |  | SAINT MARY`S (AWOS) | [5 empty] | SALINAS MUNICIPAL AP | [18 empty] | WINONA MUNI (AWOS) | [29 empty] | SAN ANTONIO INTL AP | [9 empty] | 51 | VT | -
USA | AK | KOTZEBUE RALPH WEIN MEMORIAL |  | #N/A |  | USA | PA |  |  | SAND POINT | [5 empty] | SAN DIEGO LINDBERGH FIELD | [18 empty] | WORTHINGTON (AWOS) | [29 empty] | SAN ANTONIO KELLY FIELD AFB | [9 empty] | 52 | WA | -
USA | AK | LAKE HOOD SEAPLANE |  | #N/A |  | Canada | PE |  |  | SAVOONGA | [5 empty] | SAN DIEGO MIRAMAR NAS | [48 empty] | SAN ANTONIO/STINSON | [9 empty] | 53 | WI | -
USA | AK | MCGRATH ARPT |  | #N/A |  | Canada | QC |  |  | SELAWIK | [5 empty] | SAN DIEGO NORTH ISLAND NAS | [48 empty] | TYLER/POUNDS FLD | [9 empty] | 54 | WV | -
USA | AK | MEKORYUK |  | #N/A |  | USA | RI |  |  | SEWARD | [5 empty] | SAN DIEGO/MONTGOMER | [48 empty] | VICTORIA REGIONAL AP | [9 empty] | 55 | WY | -
USA | AK | MIDDLETON ISLAND AUT |  |  |  | Saudi Arabia | SA |  |  | SHEMYA AFB | [5 empty] | SAN FRANCISCO INTL AP | [48 empty] | WACO REGIONAL AP | [9 empty] | 56
USA | AK | NENANA MUNICIPAL AP |  |  |  | USA | SC |  |  | SHISHMAREF (AWOS) | [5 empty] | SAN JOSE INTL AP | [48 empty] | WICHITA FALLS MUNICIPAL ARPT | [9 empty] | 57
USA | AK | NOME MUNICIPAL ARPT |  |  |  | USA | SD |  |  | SITKA JAPONSKI AP | [5 empty] | SAN LUIS CO RGNL | [48 empty] | WINK WINKLER COUNTY AP | [9 empty] | 58
USA | AK | NORTHWAY AIRPORT |  |  |  | Canada | SK |  |  | SKAGWAY AIRPORT | [5 empty] | SANDBERG | [58 empty] | 59
USA | AK | PALMER MUNICIPAL |  |  |  | USA | TN |  |  | SLEETMUTE | [5 empty] | SANTA BARBARA MUNICIPAL AP | [58 empty] | 60
USA | AK | PETERSBURG |  |  |  | USA | TX |  |  | SOLDOTNA | [5 empty] | SANTA MARIA PUBLIC ARPT | [58 empty] | 61
USA | AK | POINT HOPE (AWOS) |  |  |  | USA | UT |  |  | ST PAUL ISLAND ARPT | [5 empty] | SANTA MONICA MUNI | [58 empty] | 62
USA | AK | PORT HEIDEN |  |  |  | USA | VA |  |  | TALKEETNA STATE ARPT | [5 empty] | SANTA ROSA (AWOS) | [58 empty] | 63
USA | AK | SAINT MARY`S (AWOS) |  |  |  | USA | VT |  |  | TANANA RALPH M CALHOUN MEM AP | [5 empty] | STOCKTON METROPOLITAN ARPT | [58 empty] | 64
USA | AK | SAND POINT |  |  |  | USA | WA |  |  | TOGIAK VILLAGE AWOS | [5 empty] | TRAVIS FIELD AFB | [58 empty] | 65
USA | AK | SAVOONGA |  |  |  | USA | WI |  |  | UNALAKLEET FIELD | [5 empty] | TRUCKEE-TAHOE | [58 empty] | 66
USA | AK | SELAWIK |  |  |  | USA | WV |  |  | VALDEZ PIONEER FIEL | [5 empty] | UKIAH MUNICIPAL AP | [58 empty] | 67
USA | AK | SEWARD |  |  |  | USA | WY |  |  | VALDEZ WSO | [5 empty] | VAN NUYS AIRPORT | [58 empty] | 68
USA | AK | SHEMYA AFB |  |  |  | Canada | YT |  |  | WHITTIER | [5 empty] | VISALIA MUNI (AWOS) | [58 empty] | 69
USA | AK | SHISHMAREF (AWOS) |  |  |  | Colombia | Cartagena |  |  | WRANGELL | [5 empty] | YUBA CO | [58 empty] | 70
USA | AK | SITKA JAPONSKI AP | [7 empty] | YAKUTAT STATE ARPT | [64 empty] | 71
USA | AK | SKAGWAY AIRPORT | [72 empty] | 72
USA | AK | SLEETMUTE | [72 empty] | 73
USA | AK | SOLDOTNA | [72 empty] | 74
USA | AK | ST PAUL ISLAND ARPT | [72 empty] | 75
USA | AK | TALKEETNA STATE ARPT | [72 empty] | 76
USA | AK | TANANA RALPH M CALHOUN MEM AP | [72 empty] | 77
USA | AK | TOGIAK VILLAGE AWOS | [72 empty] | 78
USA | AK | UNALAKLEET FIELD | [72 empty] | 79
USA | AK | VALDEZ PIONEER FIEL | [72 empty] | 80
USA | AK | VALDEZ WSO | [72 empty] | 81
USA | AK | WHITTIER | [72 empty] | 82
USA | AK | WRANGELL | [72 empty] | 83
USA | AK | YAKUTAT STATE ARPT | [72 empty] | 84
USA | AL | ANNISTON METROPOLITAN AP | [72 empty] | 85
USA | AL | AUBURN-OPELIKA APT | [72 empty] | 86
USA | AL | BIRMINGHAM MUNICIPAL AP | [72 empty] | 87
USA | AL | CAIRNS FIELD FORT RUCKER | [72 empty] | 88
USA | AL | DOTHAN MUNICIPAL AP | [72 empty] | 89
USA | AL | HUNTSVILLE INTL/JONES FIELD | [72 empty] | 90
USA | AL | MAXWELL AFB | [72 empty] | 91
USA | AL | MOBILE DOWNTOWN AP | [72 empty] | 92
USA | AL | MOBILE REGIONAL AP | [72 empty] | 93
USA | AL | MONTGOMERY DANNELLY FIELD | [72 empty] | 94
USA | AL | MUSCLE SHOALS REGIONAL AP | [72 empty] | 95
USA | AL | TUSCALOOSA MUNICIPAL AP | [72 empty] | 96
USA | AR | BATESVILLE (AWOS) | [72 empty] | 97
USA | AR | BENTONVILLE (AWOS) | [72 empty] | 98
USA | AR | EL DORADO GOODWIN FIELD | [72 empty] | 99
USA | AR | FAYETTEVILLE DRAKE FIELD | [72 empty] | 100
USA | AR | FLIPPIN (AWOS) | [72 empty] | 101
USA | AR | FORT SMITH REGIONAL AP | [72 empty] | 102
USA | AR | HARRISON FAA AP | [72 empty] | 103
USA | AR | JONESBORO MUNI | [72 empty] | 104
USA | AR | LITTLE ROCK ADAMS FIELD | [72 empty] | 105
USA | AR | LITTLE ROCK AFB | [72 empty] | 106
USA | AR | PINE BLUFF FAA AP | [72 empty] | 107
USA | AR | ROGERS (AWOS) | [72 empty] | 108
USA | AR | SILOAM SPRING(AWOS) | [72 empty] | 109
USA | AR | SPRINGDALE MUNI | [72 empty] | 110
USA | AR | STUTTGART (AWOS) | [72 empty] | 111
USA | AR | TEXARKANA WEBB FIELD | [72 empty] | 112
USA | AR | WALNUT RIDGE (AWOS) | [72 empty] | 113
USA | AZ | CASA GRANDE (AWOS) | [72 empty] | 114
USA | AZ | DAVIS MONTHAN AFB | [72 empty] | 115
USA | AZ | DEER VALLEY/PHOENIX | [72 empty] | 116
USA | AZ | DOUGLAS BISBEE-DOUGLAS INTL A | [72 empty] | 117
USA | AZ | FLAGSTAFF PULLIAM ARPT | [72 empty] | 118
USA | AZ | GRAND CANYON NATL P | [72 empty] | 119
USA | AZ | KINGMAN (AMOS) | [72 empty] | 120
USA | AZ | LUKE AFB | [72 empty] | 121
USA | AZ | PAGE MUNI (AMOS) | [72 empty] | 122
USA | AZ | PHOENIX SKY HARBOR INTL AP | [72 empty] | 123
USA | AZ | PRESCOTT LOVE FIELD | [72 empty] | 124
USA | AZ | SAFFORD (AMOS) | [72 empty] | 125
USA | AZ | SCOTTSDALE MUNI | [72 empty] | 126
USA | AZ | TUCSON INTERNATIONAL AP | [72 empty] | 127
USA | AZ | WINSLOW MUNICIPAL AP | [72 empty] | 128
USA | AZ | YUMA INTL ARPT | [72 empty] | 129
USA | AZ | YUMA MCAS | [72 empty] | 130
Canada | BC | ABBOTSFORD AP | [72 empty] | 131
Canada | BC | AGASSIZ CDA | [72 empty] | 132
Canada | BC | BALLENAS ISLAND | [72 empty] | 133
Canada | BC | COMOX AP | [72 empty] | 134
Canada | BC | CRANBROOK AP | [72 empty] | 135
Canada | BC | DISCOVERY ISLAND | [72 empty] | 136
Canada | BC | ENTRANCE ISLAND | [72 empty] | 137
Canada | BC | ESQUIMALT HARBOUR | [72 empty] | 138
Canada | BC | FORT NELSON | [72 empty] | 139
Canada | BC | FORT SAINT JOHN | [72 empty] | 140
Canada | BC | KAMLOOPS AP | [72 empty] | 141
Canada | BC | KELOWNA AP | [72 empty] | 142
Canada | BC | MALAHAT | [72 empty] | 143
Canada | BC | NORTH VANCOUVER | [72 empty] | 144
Canada | BC | PENTICTON AP | [72 empty] | 145
Canada | BC | PITT MEADOWS | [72 empty] | 146
Canada | BC | PRINCE GEORGE | [72 empty] | 147
Canada | BC | SMITHERS AP | [72 empty] | 148
Canada | BC | SUMMERLAND | [72 empty] | 149
Canada | BC | VANCOUVER | [72 empty] | 150
Canada | BC | VERNON | [72 empty] | 151
Canada | BC | VICTORIA AP | [72 empty] | 152
Canada | BC | VICTORIA | [72 empty] | 153
Canada | BC | VICTORIA UNIV | [72 empty] | 154
Canada | BC | W VANCOUVER | [72 empty] | 155
Canada | BC | WHISTLER | [72 empty] | 156
Canada | BC | WHITE ROCK | [72 empty] | 157
India | BD | DHAKA | [72 empty] | 158
USA | CA | ALTURAS | [72 empty] | 159
USA | CA | ARCATA AIRPORT | [72 empty] | 160
USA | CA | BAKERSFIELD MEADOWS FIELD | [72 empty] | 161
USA | CA | BEALE AFB | [72 empty] | 162
USA | CA | BISHOP AIRPORT | [72 empty] | 163
USA | CA | BLUE CANYON AP | [72 empty] | 164
USA | CA | BLYTHE RIVERSIDE CO ARPT | [72 empty] | 165
USA | CA | BURBANK-GLENDALE-PASADENA AP | [72 empty] | 166
USA | CA | CAMARILLO (AWOS) | [72 empty] | 167
USA | CA | CAMP PENDLETON MCAS | [72 empty] | 168
USA | CA | CARLSBAD/PALOMAR | [72 empty] | 169
USA | CA | CHINO AIRPORT | [72 empty] | 170
USA | CA | CHULA VISTA BROWN FIELD NAAS | [72 empty] | 171
USA | CA | CONCORD CONCORD-BUCHANAN FIEL | [72 empty] | 172
USA | CA | CRESCENT CITY FAA AI | [72 empty] | 173
USA | CA | DAGGETT BARSTOW-DAGGETT AP | [72 empty] | 174
USA | CA | EDWARDS AFB | [72 empty] | 175
USA | CA | FRESNO YOSEMITE INTL AP | [72 empty] | 176
USA | CA | FULLERTON MUNICIPAL | [72 empty] | 177
USA | CA | HAYWARD AIR TERM | [72 empty] | 178
USA | CA | IMPERIAL | [72 empty] | 179
USA | CA | JACK NORTHROP FLD H | [72 empty] | 180
USA | CA | LANCASTER GEN WM FOX FIELD | [72 empty] | 181
USA | CA | LEMOORE REEVES NAS | [72 empty] | 182
USA | CA | LIVERMORE MUNICIPAL | [72 empty] | 183
USA | CA | LOMPOC (AWOS) | [72 empty] | 184
USA | CA | LONG BEACH DAUGHERTY FLD | [72 empty] | 185
USA | CA | LOS ANGELES INTL ARPT | [72 empty] | 186
USA | CA | MARCH AFB | [72 empty] | 187
USA | CA | MERCED/MACREADY FLD | [72 empty] | 188
USA | CA | MODESTO CITY-COUNTY AP | [72 empty] | 189
USA | CA | MONTAGUE SISKIYOU COUNTY AP | [72 empty] | 190
USA | CA | MONTEREY NAF | [72 empty] | 191
USA | CA | MOUNTAIN VIEW MOFFETT FLD NAS | [72 empty] | 192
USA | CA | NAPA CO. AIRPORT | [72 empty] | 193
USA | CA | NEEDLES AIRPORT | [72 empty] | 194
USA | CA | OAKLAND METROPOLITAN ARPT | [72 empty] | 195
USA | CA | OXNARD AIRPORT | [72 empty] | 196
USA | CA | PALM SPRINGS INTL | [72 empty] | 197
USA | CA | PALM SPRINGS THERMAL AP | [72 empty] | 198
USA | CA | PALMDALE AIRPORT | [72 empty] | 199
USA | CA | PASO ROBLES MUNICIPAL ARPT | [72 empty] | 200
USA | CA | POINT MUGU NF | [72 empty] | 201
USA | CA | PORTERVILLE (AWOS) | [72 empty] | 202
USA | CA | RED BLUFF MUNICIPAL ARPT | [72 empty] | 203
USA | CA | REDDING MUNICIPAL ARPT | [72 empty] | 204
USA | CA | RIVERSIDE MUNI | [72 empty] | 205
USA | CA | SACRAMENTO EXECUTIVE ARPT | [72 empty] | 206
USA | CA | SACRAMENTO METROPOLITAN AP | [72 empty] | 207
USA | CA | SALINAS MUNICIPAL AP | [72 empty] | 208
USA | CA | SAN DIEGO LINDBERGH FIELD | [72 empty] | 209
USA | CA | SAN DIEGO MIRAMAR NAS | [72 empty] | 210
USA | CA | SAN DIEGO NORTH ISLAND NAS | [72 empty] | 211
USA | CA | SAN DIEGO/MONTGOMER | [72 empty] | 212
USA | CA | SAN FRANCISCO INTL AP | [72 empty] | 213
USA | CA | SAN JOSE INTL AP | [72 empty] | 214
USA | CA | SAN LUIS CO RGNL | [72 empty] | 215
USA | CA | SANDBERG | [72 empty] | 216
USA | CA | SANTA BARBARA MUNICIPAL AP | [72 empty] | 217
USA | CA | SANTA MARIA PUBLIC ARPT | [72 empty] | 218
USA | CA | SANTA MONICA MUNI | [72 empty] | 219
USA | CA | SANTA ROSA (AWOS) | [72 empty] | 220
USA | CA | STOCKTON METROPOLITAN ARPT | [72 empty] | 221
USA | CA | TRAVIS FIELD AFB | [72 empty] | 222
USA | CA | TRUCKEE-TAHOE | [72 empty] | 223
USA | CA | UKIAH MUNICIPAL AP | [72 empty] | 224
USA | CA | VAN NUYS AIRPORT | [72 empty] | 225
USA | CA | VISALIA MUNI (AWOS) | [72 empty] | 226
USA | CA | YUBA CO | [72 empty] | 227
USA | CO | AKRON WASHINGTON CO AP | [72 empty] | 228
USA | CO | ALAMOSA SAN LUIS VALLEY RGNL | [72 empty] | 229
USA | CO | ASPEN PITKIN CO SAR | [72 empty] | 230
USA | CO | AURORA BUCKLEY FIELD ANGB | [72 empty] | 231
Colombia | CO | BARRANQUILLA | [72 empty] | 232
USA | CO | BROOMFIELD/JEFFCO [BOULDER - SURFRAD] | [72 empty] | 233
Colombia | CO | CALI | [72 empty] | 234
Colombia | CO | CARTAGENA | [72 empty] | 235
USA | CO | COLORADO SPRINGS MUNI AP | [72 empty] | 236
Colombia | CO | CORTEZ/MONTEZUMA | [72 empty] | 237
USA | CO | CRAIG-MOFFAT | [72 empty] | 238
USA | CO | DENVER INTL AP | [72 empty] | 239
USA | CO | DENVER/CENTENNIAL [GOLDEN - NREL] | [72 empty] | 240
USA | CO | DURANGO/LA PLATA CO | [72 empty] | 241
USA | CO | EAGLE COUNTY AP | [72 empty] | 242
USA | CO | FORT COLLINS (AWOS) | [72 empty] | 243
USA | CO | GRAND JUNCTION WALKER FIELD | [72 empty] | 244
USA | CO | GREELEY/WELD (AWOS) | [72 empty] | 245
USA | CO | GUNNISON CO. (AWOS) | [72 empty] | 246
USA | CO | HAYDEN/YAMPA (AWOS) | [72 empty] | 247
USA | CO | LA JUNTA MUNICIPAL AP | [72 empty] | 248
USA | CO | LAMAR MUNICIPAL | [72 empty] | 249
USA | CO | LEADVILLE/LAKE CO. | [72 empty] | 250
USA | CO | LIMON | [72 empty] | 251
USA | CO | MONTROSE CO. ARPT | [72 empty] | 252
USA | CO | PUEBLO MEMORIAL AP | [72 empty] | 253
USA | CO | RIFLE/GARFIELD RGNL | [72 empty] | 254
USA | CO | TRINIDAD LAS ANIMAS COUNTY AP | [72 empty] | 255
USA | CT | BRIDGEPORT SIKORSKY MEMORIAL | [72 empty] | 256
USA | CT | DANBURY MUNICIPAL | [72 empty] | 257
USA | CT | GROTON NEW LONDON AP | [72 empty] | 258
USA | CT | HARTFORD BRADLEY INTL AP | [72 empty] | 259
USA | CT | HARTFORD BRAINARD FD | [72 empty] | 260
USA | CT | NEW HAVEN TWEED AIRPORT | [72 empty] | 261
USA | CT | OXFORD (AWOS) | [72 empty] | 262
USA | DE | DOVER AFB | [72 empty] | 263
USA | DE | WILMINGTON NEW CASTLE CNTY AP | [72 empty] | 264
USA | FL | CRESTVIEW BOB SIKES AP | [72 empty] | 265
USA | FL | DAYTONA BEACH INTL AP | [72 empty] | 266
USA | FL | FORT LAUDERDALE | [72 empty] | 267
USA | FL | FORT LAUDERDALE HOLLYWOOD INT | [72 empty] | 268
USA | FL | FORT MYERS PAGE FIELD | [72 empty] | 269
USA | FL | GAINESVILLE REGIONAL AP | [72 empty] | 270
USA | FL | HOMESTEAD AFB | [72 empty] | 271
USA | FL | JACKSONVILLE INTL ARPT | [72 empty] | 272
USA | FL | JACKSONVILLE NAS | [72 empty] | 273
USA | FL | JACKSONVILLE/CRAIG | [72 empty] | 274
USA | FL | KEY WEST INTL ARPT | [72 empty] | 275
USA | FL | KEY WEST NAS | [72 empty] | 276
USA | FL | MACDILL AFB | [72 empty] | 277
USA | FL | MARATHON AIRPORT | [72 empty] | 278
USA | FL | MAYPORT NS | [72 empty] | 279
USA | FL | MELBOURNE REGIONAL AP | [72 empty] | 280
USA | FL | MIAMI INTL AP | [72 empty] | 281
USA | FL | MIAMI/KENDALL-TAMIA | [72 empty] | 282
USA | FL | MIAMI/OPA LOCKA | [72 empty] | 283
USA | FL | NAPLES MUNICIPAL | [72 empty] | 284
USA | FL | NASA SHUTTLE FCLTY | [72 empty] | 285
USA | FL | OCALA MUNI (AWOS) | [72 empty] | 286
USA | FL | ORLANDO EXECUTIVE AP | [72 empty] | 287
USA | FL | ORLANDO INTL ARPT | [72 empty] | 288
USA | FL | ORLANDO SANFORD AIRPORT | [72 empty] | 289
USA | FL | PANAMA CITY BAY CO | [72 empty] | 290
USA | FL | PENSACOLA FOREST SHERMAN NAS | [72 empty] | 291
USA | FL | PENSACOLA REGIONAL AP | [72 empty] | 292
USA | FL | SARASOTA BRADENTON | [72 empty] | 293
USA | FL | SOUTHWEST FLORIDA I | [72 empty] | 294
USA | FL | ST LUCIE CO INTL | [72 empty] | 295
USA | FL | ST PETERSBURG ALBERT WHITTED | [72 empty] | 296
USA | FL | ST PETERSBURG CLEAR | [72 empty] | 297
USA | FL | TALLAHASSEE REGIONAL AP [ISIS] | [72 empty] | 298
USA | FL | TAMPA INTERNATIONAL AP | [72 empty] | 299
USA | FL | TYNDALL AFB | [72 empty] | 300
USA | FL | VALPARAISO EGLIN AFB | [72 empty] | 301
USA | FL | VALPARAISO HURLBURT | [72 empty] | 302
USA | FL | VERO BEACH MUNICIPAL ARPT | [72 empty] | 303
USA | FL | WHITING FIELD NAAS | [72 empty] | 304
USA | GA | ALBANY DOUGHERTY COUNTY AP | [72 empty] | 305
USA | GA | ALMA BACON COUNTY AP | [72 empty] | 306
USA | GA | ATHENS BEN EPPS AP | [72 empty] | 307
USA | GA | ATLANTA HARTSFIELD INTL AP | [72 empty] | 308
USA | GA | AUGUSTA BUSH FIELD | [72 empty] | 309
USA | GA | BRUNSWICK GOLDEN IS | [72 empty] | 310
USA | GA | BRUNSWICK MALCOLM MCKINNON AP | [72 empty] | 311
USA | GA | COLUMBUS METROPOLITAN ARPT | [72 empty] | 312
USA | GA | DEKALB PEACHTREE | [72 empty] | 313
USA | GA | FORT BENNING LAWSON | [72 empty] | 314
USA | GA | FULTON CO ARPT BROW | [72 empty] | 315
USA | GA | HUNTER AAF | [72 empty] | 316
USA | GA | MACON MIDDLE GA REGIONAL AP | [72 empty] | 317
USA | GA | MARIETTA DOBBINS AFB | [72 empty] | 318
USA | GA | MOODY AFB/VALDOSTA | [72 empty] | 319
USA | GA | ROME R B RUSSELL AP | [72 empty] | 320
USA | GA | SAVANNAH INTL AP | [72 empty] | 321
USA | GA | VALDOSTA WB AIRPORT | [72 empty] | 322
USA | GA | WARNER ROBINS AFB | [72 empty] | 323
USA | HI | BARBERS POINT NAS | [72 empty] | 324
USA | HI | HILO INTERNATIONAL AP | [72 empty] | 325
USA | HI | HONOLULU INTL ARPT | [72 empty] | 326
USA | HI | KAHULUI AIRPORT | [72 empty] | 327
USA | HI | KANEOHE BAY MCAS | [72 empty] | 328
USA | HI | KONA INTL AT KEAHOL | [72 empty] | 329
USA | HI | LIHUE AIRPORT | [72 empty] | 330
USA | HI | MOLOKAI (AMOS) | [72 empty] | 331
USA | IA | ALGONA | [72 empty] | 332
USA | IA | ATLANTIC | [72 empty] | 333
USA | IA | BOONE MUNI | [72 empty] | 334
USA | IA | BURLINGTON MUNICIPAL AP | [72 empty] | 335
USA | IA | CARROLL | [72 empty] | 336
USA | IA | CEDAR RAPIDS MUNICIPAL AP | [72 empty] | 337
USA | IA | CHARITON | [72 empty] | 338
USA | IA | CHARLES CITY | [72 empty] | 339
USA | IA | CLARINDA | [72 empty] | 340
USA | IA | CLINTON MUNI (AWOS) | [72 empty] | 341
USA | IA | COUNCIL BLUFFS | [72 empty] | 342
USA | IA | CRESTON | [72 empty] | 343
USA | IA | DECORAH | [72 empty] | 344
USA | IA | DENISON | [72 empty] | 345
USA | IA | DES MOINES INTL AP | [72 empty] | 346
USA | IA | DUBUQUE REGIONAL AP | [72 empty] | 347
USA | IA | ESTHERVILLE MUNI | [72 empty] | 348
USA | IA | FAIR FIELD | [72 empty] | 349
USA | IA | FORT DODGE (AWOS) | [72 empty] | 350
USA | IA | FORT MADISON | [72 empty] | 351
USA | IA | KEOKUK MUNI | [72 empty] | 352
USA | IA | KNOXVILLE | [72 empty] | 353
USA | IA | LE MARS | [72 empty] | 354
USA | IA | MASON CITY MUNICIPAL ARPT | [72 empty] | 355
USA | IA | MONTICELLO MUNI | [72 empty] | 356
USA | IA | MUSCATINE | [72 empty] | 357
USA | IA | NEWTON MUNI | [72 empty] | 358
USA | IA | OELWEN | [72 empty] | 359
USA | IA | ORANGE CITY | [72 empty] | 360
USA | IA | OTTUMWA INDUSTRIAL AP | [72 empty] | 361
USA | IA | RED OAK | [72 empty] | 362
USA | IA | SHELDON | [72 empty] | 363
USA | IA | SHENANDOAH MUNI | [72 empty] | 364
USA | IA | SIOUX CITY SIOUX GATEWAY AP | [72 empty] | 365
USA | IA | SPENCER | [72 empty] | 366
USA | IA | STORM LAKE | [72 empty] | 367
USA | IA | WASHINGTON | [72 empty] | 368
USA | IA | WATERLOO MUNICIPAL AP | [72 empty] | 369
USA | IA | WEBSTER CITY | [72 empty] | 370
USA | ID | BOISE AIR TERMINAL [UO] | [72 empty] | 371
USA | ID | BURLEY MUNICIPAL ARPT | [72 empty] | 372
USA | ID | CALDWELL (AWOS) | [72 empty] | 373
USA | ID | COEUR D`ALENE(AWOS) | [72 empty] | 374
USA | ID | IDAHO FALLS FANNING FIELD | [72 empty] | 375
USA | ID | JOSLIN FLD MAGIC VA [TWIN FALLS - UO] | [72 empty] | 376
USA | ID | LEWISTON NEZ PERCE CNTY AP | [72 empty] | 377
USA | ID | MOUNTAIN HOME AFB | [72 empty] | 378
USA | ID | POCATELLO REGIONAL AP | [72 empty] | 379
USA | ID | SALMON/LEMHI (AWOS) | [72 empty] | 380
USA | IL | AURORA MUNICIPAL | [72 empty] | 381
USA | IL | BELLEVILLE SCOTT AFB | [72 empty] | 382
USA | IL | CAHOKIA/ST. LOUIS | [72 empty] | 383
USA | IL | CENTRAL ILLINOIS RG | [72 empty] | 384
USA | IL | CHICAGO MIDWAY AP | [72 empty] | 385
USA | IL | CHICAGO OHARE INTL AP | [72 empty] | 386
USA | IL | CHICAGO/WAUKEGAN | [72 empty] | 387
USA | IL | DECATUR | [72 empty] | 388
USA | IL | MARION REGIONAL | [72 empty] | 389
USA | IL | MOLINE QUAD CITY INTL AP | [72 empty] | 390
USA | IL | MOUNT VERNON (AWOS) | [72 empty] | 391
USA | IL | PEORIA GREATER PEORIA AP | [72 empty] | 392
USA | IL | QUINCY MUNI BALDWIN FLD | [72 empty] | 393
USA | IL | ROCKFORD GREATER ROCKFORD AP | [72 empty] | 394
USA | IL | SOUTHERN ILLINOIS | [72 empty] | 395
USA | IL | SPRINGFIELD CAPITAL AP | [72 empty] | 396
USA | IL | STERLING ROCKFALLS | [72 empty] | 397
USA | IL | UNIV OF ILLINOIS WI [BONDVILLE - SURFRAD] | [72 empty] | 398
USA | IL | W. CHICAGO/DU PAGE | [72 empty] | 399
USA | IN | DELAWARE CO JOHNSON | [72 empty] | 400
USA | IN | EVANSVILLE REGIONAL AP | [72 empty] | 401
USA | IN | FORT WAYNE INTL AP | [72 empty] | 402
USA | IN | GRISSOM ARB | [72 empty] | 403
USA | IN | HUNTINGBURG | [72 empty] | 404
USA | IN | INDIANAPOLIS INTL AP | [72 empty] | 405
USA | IN | LAFAYETTE PURDUE UNIV AP | [72 empty] | 406
USA | IN | MONROE CO | [72 empty] | 407
India | IN | NEW DELHI SAFDARJUNG AP | [72 empty] | 408
India | IN | PATNA | [72 empty] | 409
USA | IN | SOUTH BEND MICHIANA RGNL AP | [72 empty] | 410
USA | IN | TERRE HAUTE HULMAN REGIONAL A | [72 empty] | 411
USA | KS | CHANUTE MARTIN JOHNSON AP | [72 empty] | 412
USA | KS | CONCORDIA BLOSSER MUNI AP | [72 empty] | 413
USA | KS | DODGE CITY REGIONAL AP | [72 empty] | 414
USA | KS | EMPORIA MUNICIPAL AP | [72 empty] | 415
USA | KS | FORT RILEY MARSHALL AAF | [72 empty] | 416
USA | KS | GARDEN CITY MUNICIPAL AP | [72 empty] | 417
USA | KS | GOODLAND RENNER FIELD | [72 empty] | 418
USA | KS | GREAT BEND (AWOS) | [72 empty] | 419
USA | KS | HAYS MUNI (AWOS) | [72 empty] | 420
USA | KS | HILL CITY MUNICIPAL AP | [72 empty] | 421
USA | KS | HUTCHINSON MUNICIPAL AP | [72 empty] | 422
USA | KS | LIBERAL MUNI | [72 empty] | 423
USA | KS | MANHATTAN RGNL | [72 empty] | 424
USA | KS | MCCONNELL AFB | [72 empty] | 425
USA | KS | NEWTON (AWOS) | [72 empty] | 426
USA | KS | OLATHE/JOHNSON CO. | [72 empty] | 427
USA | KS | RUSSELL MUNICIPAL AP | [72 empty] | 428
USA | KS | SALINA MUNICIPAL AP | [72 empty] | 429
USA | KS | TOPEKA FORBES FIELD | [72 empty] | 430
USA | KS | TOPEKA MUNICIPAL AP | [72 empty] | 431
USA | KS | WICHITA MID-CONTINENT AP | [72 empty] | 432
USA | KS | WICHITA/COL. JABARA | [72 empty] | 433
USA | KY | BOWLING GREEN WARREN CO AP | [72 empty] | 434
USA | KY | CINCINNATI NORTHERN KY AP | [72 empty] | 435
USA | KY | FORT CAMPBELL AAF | [72 empty] | 436
USA | KY | FORT KNOX GODMAN AAF | [72 empty] | 437
USA | KY | HENDERSON CITY | [72 empty] | 438
USA | KY | JACKSON JULIAN CARROLL AP | [72 empty] | 439
USA | KY | LEXINGTON BLUEGRASS AP | [72 empty] | 440
USA | KY | LONDON-CORBIN AP | [72 empty] | 441
USA | KY | LOUISVILLE BOWMAN FIELD | [72 empty] | 442
USA | KY | LOUISVILLE STANDIFORD FIELD | [72 empty] | 443
USA | KY | PADUCAH BARKLEY REGIONAL AP | [72 empty] | 444
USA | KY | SOMERSET(AWOS) | [72 empty] | 445
USA | LA | ALEXANDRIA ESLER REGIONAL AP | [72 empty] | 446
USA | LA | BARKSDALE AFB | [72 empty] | 447
USA | LA | BATON ROUGE RYAN ARPT | [72 empty] | 448
USA | LA | ENGLAND AFB | [72 empty] | 449
USA | LA | FORT POLK AAF | [72 empty] | 450
USA | LA | LAFAYETTE REGIONAL AP | [72 empty] | 451
USA | LA | LAKE CHARLES REGIONAL ARPT | [72 empty] | 452
USA | LA | MONROE REGIONAL AP | [72 empty] | 453
USA | LA | NEW IBERIA NAAS | [72 empty] | 454
USA | LA | NEW ORLEANS ALVIN CALLENDER F | [72 empty] | 455
USA | LA | NEW ORLEANS INTL ARPT | [72 empty] | 456
USA | LA | NEW ORLEANS LAKEFRONT AP | [72 empty] | 457
USA | LA | PATTERSON MEMORIAL | [72 empty] | 458
USA | LA | SHREVEPORT DOWNTOWN | [72 empty] | 459
USA | LA | SHREVEPORT REGIONAL ARPT | [72 empty] | 460
USA | MA | BARNSTABLE MUNI BOA | [72 empty] | 461
USA | MA | BEVERLY MUNI | [72 empty] | 462
USA | MA | BOSTON LOGAN INT ARPT | [72 empty] | 463
USA | MA | CHICOPEE FALLS WESTO | [72 empty] | 464
USA | MA | LAWRENCE MUNI | [72 empty] | 465
USA | MA | MARTHAS VINEYARD | [72 empty] | 466
USA | MA | NANTUCKET MEMORIAL AP | [72 empty] | 467
USA | MA | NEW BEDFORD RGNL | [72 empty] | 468
USA | MA | NORTH ADAMS | [72 empty] | 469
USA | MA | NORWOOD MEMORIAL | [72 empty] | 470
USA | MA | OTIS ANGB | [72 empty] | 471
USA | MA | PLYMOUTH MUNICIPAL | [72 empty] | 472
USA | MA | PROVINCETOWN (AWOS) | [72 empty] | 473
USA | MA | WESTFIELD BARNES MUNI AP | [72 empty] | 474
USA | MA | WORCESTER REGIONAL ARPT | [72 empty] | 475
USA | MB | WINNIPEG | [72 empty] | 476
USA | MD | ANDREWS AFB | [72 empty] | 477
USA | MD | BALTIMORE BLT-WASHNGTN INT | [72 empty] | 478
USA | MD | HAGERSTOWN RGNL RIC | [72 empty] | 479
USA | MD | PATUXENT RIVER NAS | [72 empty] | 480
USA | MD | SALISBURY WICOMICO CO AP | [72 empty] | 481
USA | ME | AUBURN-LEWISTON | [72 empty] | 482
USA | ME | AUGUSTA AIRPORT | [72 empty] | 483
USA | ME | BANGOR INTERNATIONAL AP | [72 empty] | 484
USA | ME | BAR HARBOR (AWOS) | [72 empty] | 485
USA | ME | CARIBOU MUNICIPAL ARPT | [72 empty] | 486
USA | ME | HOULTON INTL ARPT | [72 empty] | 487
USA | ME | MILLINOCKET MUNICIPAL AP | [72 empty] | 488
USA | ME | NORTHERN AROOSTOOK | [72 empty] | 489
USA | ME | PORTLAND INTL JETPORT | [72 empty] | 490
USA | ME | PRESQUE ISLE MUNICIP | [72 empty] | 491
USA | ME | ROCKLAND/KNOX(AWOS) | [72 empty] | 492
USA | ME | SANFORD MUNI (AWOS) | [72 empty] | 493
USA | ME | WATERVILLE (AWOS) | [72 empty] | 494
USA | ME | WISCASSET | [72 empty] | 495
USA | MI | ALPENA COUNTY REGIONAL AP | [72 empty] | 496
USA | MI | ANN ARBOR MUNICIPAL | [72 empty] | 497
USA | MI | BATTLE CREEK KELLOGG AP | [72 empty] | 498
USA | MI | BENTON HARBOR/ROSS | [72 empty] | 499
USA | MI | CADILLAC WEXFORD CO AP | [72 empty] | 500
USA | MI | CHIPPEWA CO INTL | [72 empty] | 501
USA | MI | DETROIT CITY AIRPORT | [72 empty] | 502
USA | MI | DETROIT METROPOLITAN ARPT | [72 empty] | 503
USA | MI | DETROIT WILLOW RUN AP | [72 empty] | 504
USA | MI | ESCANABA (AWOS) | [72 empty] | 505
USA | MI | FLINT BISHOP INTL ARPT | [72 empty] | 506
USA | MI | GRAND RAPIDS KENT COUNTY INT | [72 empty] | 507
USA | MI | HANCOCK HOUGHTON CO AP | [72 empty] | 508
USA | MI | HOUGHTON LAKE ROSCOMMON CO AR | [72 empty] | 509
USA | MI | HOWELL | [72 empty] | 510
USA | MI | IRON MOUNTAIN/FORD | [72 empty] | 511
USA | MI | IRONWOOD (AWOS) | [72 empty] | 512
USA | MI | JACKSON REYNOLDS FIELD | [72 empty] | 513
USA | MI | KALAMAZOO BATTLE CR | [72 empty] | 514
USA | MI | LANSING CAPITAL CITY ARPT | [72 empty] | 515
USA | MI | MANISTEE (AWOS) | [72 empty] | 516
USA | MI | MENOMINEE (AWOS) | [72 empty] | 517
USA | MI | MOUNT CLEMENS SELFRIDGE FLD | [72 empty] | 518
USA | MI | MUSKEGON COUNTY ARPT | [72 empty] | 519
USA | MI | OAKLAND CO INTL | [72 empty] | 520
USA | MI | OSCODA WURTSMITH AFB | [72 empty] | 521
USA | MI | PELLSTON EMMET COUNTY AP | [72 empty] | 522
USA | MI | SAGINAW TRI CITY INTL AP | [72 empty] | 523
USA | MI | SAULT STE MARIE SANDERSON FIE | [72 empty] | 524
USA | MI | ST.CLAIR COUNTY INT | [72 empty] | 525
USA | MI | TRAVERSE CITY CHERRY CAPITAL | [72 empty] | 526
USA | MN | AITKIN NDB(AWOS) | [72 empty] | 527
USA | MN | ALBERT LEA (AWOS) | [72 empty] | 528
USA | MN | ALEXANDRIA MUNICIPAL AP | [72 empty] | 529
USA | MN | AUSTIN MUNI | [72 empty] | 530
USA | MN | BAUDETTE INTERNATIONAL AP | [72 empty] | 531
USA | MN | BEMIDJI MUNICIPAL | [72 empty] | 532
USA | MN | BENSON MUNI | [72 empty] | 533
USA | MN | BRAINERD/WIELAND | [72 empty] | 534
USA | MN | CAMBRIDGE MUNI | [72 empty] | 535
USA | MN | CLOQUET (AWOS) | [72 empty] | 536
USA | MN | CRANE LAKE (AWOS) | [72 empty] | 537
USA | MN | CROOKSTON MUNI FLD | [72 empty] | 538
USA | MN | DETROIT LAKES(AWOS) | [72 empty] | 539
USA | MN | DULUTH INTERNATIONAL ARPT | [72 empty] | 540
USA | MN | ELY MUNI | [72 empty] | 541
USA | MN | EVELETH MUNI (AWOS) | [72 empty] | 542
USA | MN | FAIRMONT MUNI(AWOS) | [72 empty] | 543
USA | MN | FARIBAULT MUNI AWOS | [72 empty] | 544
USA | MN | FLYING CLOUD | [72 empty] | 545
USA | MN | FOSSTON(AWOS) | [72 empty] | 546
USA | MN | GLENWOOD (ASOS) | [72 empty] | 547
USA | MN | GRAND RAPIDS(AWOS) | [72 empty] | 548
USA | MN | HALLOCK | [72 empty] | 549
USA | MN | HIBBING CHISHOLM-HIBBING AP | [72 empty] | 550
USA | MN | HUTCHINSON (AWOS) | [72 empty] | 551
USA | MN | INTERNATIONAL FALLS INTL AP | [72 empty] | 552
USA | MN | LITCHFIELD MUNI | [72 empty] | 553
USA | MN | LITTLE FALLS (AWOS) | [72 empty] | 554
USA | MN | MANKATO(AWOS) | [72 empty] | 555
USA | MN | MINNEAPOLIS-ST PAUL INT ARP | [72 empty] | 556
USA | MN | MINNEAPOLIS/CRYSTAL | [72 empty] | 557
USA | MN | MORA MUNI (AWOS) | [72 empty] | 558
USA | MN | MORRIS MUNI (AWOS) | [72 empty] | 559
USA | MN | NEW ULM MUNI (AWOS) | [72 empty] | 560
USA | MN | ORR | [72 empty] | 561
USA | MN | OWATONNA (AWOS) | [72 empty] | 562
USA | MN | PARK RAPIDS MUNICIPAL AP | [72 empty] | 563
USA | MN | PIPESTONE (AWOS) | [72 empty] | 564
USA | MN | RED WING | [72 empty] | 565
USA | MN | REDWOOD FALLS MUNI | [72 empty] | 566
USA | MN | ROCHESTER INTERNATIONAL ARPT | [72 empty] | 567
USA | MN | ROSEAU MUNI (AWOS) | [72 empty] | 568
USA | MN | SILVER BAY | [72 empty] | 569
USA | MN | SOUTH ST PAUL MUNI | [72 empty] | 570
USA | MN | ST CLOUD REGIONAL ARPT | [72 empty] | 571
USA | MN | ST PAUL DOWNTOWN AP | [72 empty] | 572
USA | MN | THIEF RIVER(AWOS) | [72 empty] | 573
USA | MN | WHEATON NDB (AWOS) | [72 empty] | 574
USA | MN | WILLMAR | [72 empty] | 575
USA | MN | WINONA MUNI (AWOS) | [72 empty] | 576
USA | MN | WORTHINGTON (AWOS) | [72 empty] | 577
USA | MO | CAPE GIRARDEAU MUNICIPAL AP | [72 empty] | 578
USA | MO | COLUMBIA REGIONAL AIRPORT | [72 empty] | 579
USA | MO | FARMINGTON | [72 empty] | 580
USA | MO | JEFFERSON CITY MEM | [72 empty] | 581
USA | MO | JOPLIN MUNICIPAL AP | [72 empty] | 582
USA | MO | KAISER MEM (AWOS) | [72 empty] | 583
USA | MO | KANSAS CITY DOWNTOWN AP | [72 empty] | 584
USA | MO | KANSAS CITY INT ARPT | [72 empty] | 585
USA | MO | KIRKSVILLE REGIONAL AP | [72 empty] | 586
USA | MO | POPLAR BLUFF(AMOS) | [72 empty] | 587
USA | MO | SPRINGFIELD REGIONAL ARPT | [72 empty] | 588
USA | MO | ST JOSEPH ROSECRANS MEMORIAL | [72 empty] | 589
USA | MO | ST LOUIS LAMBERT INT ARPT | [72 empty] | 590
USA | MO | ST LOUIS SPIRIT OF ST LOUIS A | [72 empty] | 591
USA | MO | VICHY ROLLA NATL ARPT | [72 empty] | 592
USA | MO | WHITEMAN AFB | [72 empty] | 593
USA | MS | COLUMBUS AFB | [72 empty] | 594
USA | MS | GOLDEN TRI(AWOS) | [72 empty] | 595
USA | MS | GREENWOOD LEFLORE ARPT | [72 empty] | 596
USA | MS | GULFPORT BILOXI INT | [72 empty] | 597
USA | MS | HATTIESBURG LAUREL | [72 empty] | 598
USA | MS | JACKSON INTERNATIONAL AP | [72 empty] | 599
USA | MS | KEESLER AFB | [72 empty] | 600
USA | MS | MCCOMB PIKE COUNTY AP | [72 empty] | 601
USA | MS | MERIDIAN KEY FIELD | [72 empty] | 602
USA | MS | MERIDIAN NAAS | [72 empty] | 603
USA | MS | NATCHEZ/HARDY(AWOS) | [72 empty] | 604
USA | MS | TUPELO C D LEMONS ARPT | [72 empty] | 605
USA | MT | BILLINGS LOGAN INT ARPT | [72 empty] | 606
USA | MT | BOZEMAN GALLATIN FIELD | [72 empty] | 607
USA | MT | BUTTE BERT MOONEY ARPT | [72 empty] | 608
USA | MT | CUT BANK MUNI AP | [72 empty] | 609
USA | MT | GLASGOW INTL ARPT | [72 empty] | 610
USA | MT | GLENDIVE(AWOS) | [72 empty] | 611
USA | MT | GREAT FALLS INTL ARPT | [72 empty] | 612
USA | MT | HAVRE CITY-COUNTY AP | [72 empty] | 613
USA | MT | HELENA REGIONAL AIRPORT | [72 empty] | 614
USA | MT | KALISPELL GLACIER PK INT AR | [72 empty] | 615
USA | MT | LEWISTOWN MUNICIPAL ARPT | [72 empty] | 616
USA | MT | LIVINGSTON MISSION FIELD | [72 empty] | 617
USA | MT | MILES CITY MUNICIPAL ARPT | [72 empty] | 618
USA | MT | MISSOULA INTERNATIONAL AP | [72 empty] | 619
USA | MT | SIDNEY-RICHLAND | [72 empty] | 620
USA | MT | WOLF POINT INTL [FORT PECK - SURFRAD] | [72 empty] | 621
Canada | NB | FREDERICTON | [72 empty] | 622
Canada | NB | MONCTON AP | [72 empty] | 623
USA | NC | ASHEVILLE REGIONAL ARPT | [72 empty] | 624
USA | NC | CAPE HATTERAS NWS BLDG | [72 empty] | 625
USA | NC | CHARLOTTE DOUGLAS INTL ARPT | [72 empty] | 626
USA | NC | CHERRY POINT MCAS | [72 empty] | 627
USA | NC | DARE CO RGNL | [72 empty] | 628
USA | NC | ELIZABETH CITY COAST GUARD AI [NREL] | [72 empty] | 629
USA | NC | FAYETTEVILLE POPE AFB | [72 empty] | 630
USA | NC | FAYETTEVILLE RGNL G | [72 empty] | 631
USA | NC | FORT BRAGG SIMMONS AAF | [72 empty] | 632
USA | NC | GOLDSBORO SEYMOUR JOHNSON AFB | [72 empty] | 633
USA | NC | GREENSBORO PIEDMONT TRIAD INT | [72 empty] | 634
USA | NC | HICKORY REGIONAL AP | [72 empty] | 635
USA | NC | JACKSONVILLE (AWOS) | [72 empty] | 636
USA | NC | NEW BERN CRAVEN CO REGL AP | [72 empty] | 637
USA | NC | NEW RIVER MCAF | [72 empty] | 638
USA | NC | PITT GREENVILLE ARP | [72 empty] | 639
USA | NC | RALEIGH DURHAM INTERNATIONAL | [72 empty] | 640
USA | NC | ROCKY MOUNT WILSON | [72 empty] | 641
USA | NC | SOUTHERN PINES AWOS | [72 empty] | 642
USA | NC | WILMINGTON INTERNATIONAL ARPT | [72 empty] | 643
USA | NC | WINSTON-SALEM REYNOLDS AP | [72 empty] | 644
USA | ND | BISMARCK MUNICIPAL ARPT [ISIS] | [72 empty] | 645
USA | ND | DEVILS LAKE(AWOS) | [72 empty] | 646
USA | ND | DICKINSON MUNICIPAL AP | [72 empty] | 647
USA | ND | FARGO HECTOR INTERNATIONAL AP | [72 empty] | 648
USA | ND | GRAND FORKS AF | [72 empty] | 649
USA | ND | GRAND FORKS INTERNATIONAL AP | [72 empty] | 650
USA | ND | JAMESTOWN MUNICIPAL ARPT | [72 empty] | 651
USA | ND | MINOT AFB | [72 empty] | 652
USA | ND | MINOT FAA AP | [72 empty] | 653
USA | ND | WILLISTON SLOULIN INTL AP | [72 empty] | 654
USA | NE | AINSWORTH MUNICIPAL | [72 empty] | 655
USA | NE | ALLIANCE MUNICIPAL | [72 empty] | 656
USA | NE | BEATRICE MUNICIPAL | [72 empty] | 657
USA | NE | BELLEVUE OFFUTT AFB | [72 empty] | 658
USA | NE | BREWSTER FIELD ARPT | [72 empty] | 659
USA | NE | BROKEN BOW MUNI | [72 empty] | 660
USA | NE | COLUMBUS MUNI | [72 empty] | 661
USA | NE | FALLS CITY/BRENNER | [72 empty] | 662
USA | NE | FREMONT MUNI ARPT | [72 empty] | 663
USA | NE | GRAND ISLAND CENTRAL NE REGIO | [72 empty] | 664
USA | NE | HASTINGS MUNICIPAL | [72 empty] | 665
USA | NE | KEARNEY MUNI (AWOS) | [72 empty] | 666
USA | NE | LINCOLN MUNICIPAL ARPT | [72 empty] | 667
USA | NE | MCCOOK MUNICIPAL | [72 empty] | 668
USA | NE | NORFOLK KARL STEFAN MEM ARPT | [72 empty] | 669
USA | NE | NORTH PLATTE REGIONAL AP | [72 empty] | 670
USA | NE | OMAHA EPPLEY AIRFIELD | [72 empty] | 671
USA | NE | OMAHA WSFO | [72 empty] | 672
USA | NE | SCOTTSBLUFF W B HEILIG FIELD | [72 empty] | 673
USA | NE | SIDNEY MUNICIPAL AP | [72 empty] | 674
USA | NE | TEKAMAH (ASOS) | [72 empty] | 675
USA | NE | VALENTINE MILLER FIELD | [72 empty] | 676
USA | NL | ST JOHNS | [72 empty] | 677
USA | NH | BERLIN MUNICIPAL | [72 empty] | 678
USA | NH | CONCORD MUNICIPAL ARPT | [72 empty] | 679
USA | NH | DILLANT HOPKINS | [72 empty] | 680
USA | NH | LACONIA MUNI (AWOS) | [72 empty] | 681
USA | NH | LEBANON MUNICIPAL | [72 empty] | 682
USA | NH | MANCHESTER AIRPORT | [72 empty] | 683
USA | NH | MOUNT WASHINGTON | [72 empty] | 684
USA | NH | PEASE INTL TRADEPOR | [72 empty] | 685
USA | NJ | ATLANTIC CITY INTL AP | [72 empty] | 686
USA | NJ | BELMAR ASC | [72 empty] | 687
USA | NJ | CALDWELL/ESSEX CO. | [72 empty] | 688
USA | NJ | CAPE MAY CO | [72 empty] | 689
USA | NJ | MCGUIRE AFB | [72 empty] | 690
USA | NJ | MILLVILLE MUNICIPAL AP | [72 empty] | 691
USA | NJ | NEWARK INTERNATIONAL ARPT | [72 empty] | 692
USA | NJ | TETERBORO AIRPORT | [72 empty] | 693
USA | NJ | TRENTON MERCER COUNTY AP | [72 empty] | 694
USA | NM | ALBUQUERQUE INTL ARPT [ISIS] | [72 empty] | 695
USA | NM | CARLSBAD CAVERN CITY AIR TERM | [72 empty] | 696
USA | NM | CLAYTON MUNICIPAL AIRPARK | [72 empty] | 697
USA | NM | CLOVIS CANNON AFB | [72 empty] | 698
USA | NM | CLOVIS MUNI (AWOS) | [72 empty] | 699
USA | NM | DEMING MUNI | [72 empty] | 700
USA | NM | FARMINGTON FOUR CORNERS REGL | [72 empty] | 701
USA | NM | GALLUP SEN CLARKE FLD | [72 empty] | 702
USA | NM | HOLLOMAN AFB | [72 empty] | 703
USA | NM | LAS VEGAS MUNICIPAL ARPT | [72 empty] | 704
USA | NM | ROSWELL INDUSTRIAL AIR PARK | [72 empty] | 705
USA | NM | SANTA FE COUNTY MUNICIPAL AP | [72 empty] | 706
USA | NM | SIERRA BLANCA RGNL | [72 empty] | 707
USA | NM | TAOS MUNI APT(AWOS) | [72 empty] | 708
USA | NM | TRUTH OR CONSEQUENCES MUNI AP | [72 empty] | 709
USA | NS | GREENWOOD AP | [72 empty] | 710
USA | NS | HALIFAX | [72 empty] | 711
USA | NS | SHEARWATER | [72 empty] | 712
USA | NS | SYDNEY AP | [72 empty] | 713
USA | NT | YELLOWKNIFE AP | [72 empty] | 714
USA | NU | IQALUIT | [72 empty] | 715
USA | NV | ELKO MUNICIPAL ARPT | [72 empty] | 716
USA | NV | ELY YELLAND FIELD | [72 empty] | 717
USA | NV | FALLON NAAS | [72 empty] | 718
USA | NV | LAS VEGAS MCCARRAN INTL AP | [72 empty] | 719
USA | NV | LOVELOCK DERBY FIELD | [72 empty] | 720
USA | NV | MERCURY DESERT ROCK AP [SURFRAD] | [72 empty] | 721
USA | NV | NELLIS AFB | [72 empty] | 722
USA | NV | RENO TAHOE INTERNATIONAL AP | [72 empty] | 723
USA | NV | TONOPAH AIRPORT | [72 empty] | 724
USA | NV | WINNEMUCCA MUNICIPAL ARPT | [72 empty] | 725
USA | NY | ADIRONDACK RGNL | [72 empty] | 726
USA | NY | ALBANY COUNTY AP | [72 empty] | 727
USA | NY | BINGHAMTON EDWIN A LINK FIELD | [72 empty] | 728
USA | NY | BUFFALO NIAGARA INTL AP | [72 empty] | 729
USA | NY | ELMIRA CORNING REGIONAL AP | [72 empty] | 730
USA | NY | FORT DRUM/WHEELER-S | [72 empty] | 731
USA | NY | GLENS FALLS AP | [72 empty] | 732
USA | NY | ISLIP LONG ISL MACARTHUR AP | [72 empty] | 733
USA | NY | JAMESTOWN (AWOS) | [72 empty] | 734
USA | NY | MASSENA AP | [72 empty] | 735
USA | NY | MONTICELLO(AWOS) | [72 empty] | 736
USA | NY | NEW YORK CENTRAL PRK OBS BELV | [72 empty] | 737
USA | NY | NEW YORK J F KENNEDY INT AR | [72 empty] | 738
USA | NY | NEW YORK LAGUARDIA ARPT | [72 empty] | 739
USA | NY | NIAGARA FALLS AF | [72 empty] | 740
USA | NY | POUGHKEEPSIE DUTCHESS CO AP | [72 empty] | 741
USA | NY | REPUBLIC | [72 empty] | 742
USA | NY | ROCHESTER GREATER ROCHESTER I | [72 empty] | 743
USA | NY | STEWART FIELD | [72 empty] | 744
USA | NY | SYRACUSE HANCOCK INT ARPT | [72 empty] | 745
USA | NY | UTICA ONEIDA COUNTY AP | [72 empty] | 746
USA | NY | WATERTOWN AP | [72 empty] | 747
USA | NY | WESTHAMPTON GABRESKI AP | [72 empty] | 748
USA | NY | WHITE PLAINS WESTCHESTER CO A | [72 empty] | 749
USA | OH | AKRON AKRON-CANTON REG AP | [72 empty] | 750
USA | OH | BURKE LAKEFRONT | [72 empty] | 751
USA | OH | CINCINNATI MUNICIPAL AP LUNKI | [72 empty] | 752
USA | OH | CLEVELAND HOPKINS INTL AP | [72 empty] | 753
USA | OH | COLUMBUS PORT COLUMBUS INTL A | [72 empty] | 754
USA | OH | DAYTON INTERNATIONAL AIRPORT | [72 empty] | 755
USA | OH | FINDLAY AIRPORT | [72 empty] | 756
USA | OH | MANSFIELD LAHM MUNICIPAL ARPT | [72 empty] | 757
USA | OH | OHIO STATE UNIVERSI | [72 empty] | 758
USA | OH | TOLEDO EXPRESS AIRPORT | [72 empty] | 759
USA | OH | YOUNGSTOWN REGIONAL AIRPORT | [72 empty] | 760
USA | OH | ZANESVILLE MUNICIPAL AP | [72 empty] | 761
USA | OK | ALTUS AFB | [72 empty] | 762
USA | OK | CLINTON-SHERMAN | [72 empty] | 763
USA | OK | FORT SILL POST FIELD AF | [72 empty] | 764
USA | OK | GAGE AIRPORT | [72 empty] | 765
USA | OK | HOBART MUNICIPAL AP | [72 empty] | 766
USA | OK | LAWTON MUNICIPAL | [72 empty] | 767
USA | OK | MCALESTER MUNICIPAL AP | [72 empty] | 768
USA | OK | OKLAHOMA CITY TINKER AFB | [72 empty] | 769
USA | OK | OKLAHOMA CITY WILL ROGERS WOR | [72 empty] | 770
USA | OK | OKLAHOMA CITY/WILEY | [72 empty] | 771
USA | OK | PONCA CITY MUNICIPAL AP [SGP - ARM] | [72 empty] | 772
USA | OK | STILLWATER RGNL | [72 empty] | 773
USA | OK | TULSA INTERNATIONAL AIRPORT | [72 empty] | 774
USA | OK | VANCE AFB | [72 empty] | 775
Canada | ON | BEAUSOLEIL | [72 empty] | 776
Canada | ON | BURLINGTON PIERS | [72 empty] | 777
Canada | ON | ERIEAU | [72 empty] | 778
Canada | ON | LAGOON CITY | [72 empty] | 779
Canada | ON | LONDON AP | [72 empty] | 780
Canada | ON | NORTH BAY AP | [72 empty] | 781
Canada | ON | OTTAWA | [72 empty] | 782
Canada | ON | PETERBOROUGH AP | [72 empty] | 783
Canada | ON | PORT WELLER | [72 empty] | 784
Canada | ON | SAULT STE MARIE | [72 empty] | 785
Canada | ON | SUDBURY AP | [72 empty] | 786
Canada | ON | THUNDER BAY AP | [72 empty] | 787
Canada | ON | TIMMINS AP | [72 empty] | 788
Canada | ON | TORONTO AP | [72 empty] | 789
Canada | ON | TORONTO ISLAND AP | [72 empty] | 790
Canada | ON | TORONTO | [72 empty] | 791
Canada | ON | TRENTON AP | [72 empty] | 792
Canada | ON | WINDSOR | [72 empty] | 793
USA | OR | ASTORIA REGIONAL AIRPORT | [72 empty] | 794
USA | OR | AURORA STATE | [72 empty] | 795
USA | OR | BAKER MUNICIPAL AP | [72 empty] | 796
USA | OR | BURNS MUNICIPAL ARPT [UO] | [72 empty] | 797
USA | OR | CORVALLIS MUNI | [72 empty] | 798
USA | OR | EUGENE MAHLON SWEET ARPT [UO] | [72 empty] | 799
USA | OR | KLAMATH FALLS INTL AP [UO] | [72 empty] | 800
USA | OR | LA GRANDE MUNI AP | [72 empty] | 801
USA | OR | LAKEVIEW (AWOS) | [72 empty] | 802
USA | OR | MEDFORD ROGUE VALLEY INTL AP [ASHLAND - UO] | [72 empty] | 803
USA | OR | NORTH BEND MUNI AIRPORT | [72 empty] | 804
USA | OR | PENDLETON E OR REGIONAL AP | [72 empty] | 805
USA | OR | PORTLAND INTERNATIONAL AP | [72 empty] | 806
USA | OR | PORTLAND/HILLSBORO | [72 empty] | 807
USA | OR | PORTLAND/TROUTDALE | [72 empty] | 808
USA | OR | REDMOND ROBERTS FIELD | [72 empty] | 809
USA | OR | ROSEBURG REGIONAL AP | [72 empty] | 810
USA | OR | SALEM MCNARY FIELD | [72 empty] | 811
USA | OR | SEXTON SUMMIT | [72 empty] | 812
USA | PA | ALLENTOWN LEHIGH VALLEY INTL | [72 empty] | 813
USA | PA | ALTOONA BLAIR CO ARPT | [72 empty] | 814
USA | PA | BRADFORD REGIONAL AP | [72 empty] | 815
USA | PA | BUTLER CO (AWOS) | [72 empty] | 816
USA | PA | DUBOIS FAA AP | [72 empty] | 817
USA | PA | ERIE INTERNATIONAL AP | [72 empty] | 818
USA | PA | FRANKLIN | [72 empty] | 819
USA | PA | HARRISBURG CAPITAL CITY ARPT | [72 empty] | 820
USA | PA | JOHNSTOWN CAMBRIA COUNTY AP | [72 empty] | 821
USA | PA | LANCASTER | [72 empty] | 822
USA | PA | MIDDLETOWN HARRISBURG INTL AP | [72 empty] | 823
USA | PA | PHILADELPHIA INTERNATIONAL AP | [72 empty] | 824
USA | PA | PHILADELPHIA NE PHILADELPHIA | [72 empty] | 825
USA | PA | PITTSBURGH ALLEGHENY CO AP | [72 empty] | 826
USA | PA | PITTSBURGH INTERNATIONAL AP | [72 empty] | 827
USA | PA | READING SPAATZ FIELD | [72 empty] | 828
USA | PA | STATE COLLEGE [PENN STATE - SURFRAD] | [72 empty] | 829
USA | PA | WASHINGTON (AWOS) | [72 empty] | 830
USA | PA | WILKES-BARRE SCRANTON INTL AP | [72 empty] | 831
USA | PA | WILLIAMSPORT REGIONAL AP | [72 empty] | 832
USA | PA | WILLOW GROVE NAS | [72 empty] | 833
Canada | PE | CHARLOTTETOWN | [72 empty] | 834
Canada | QC | JONQUIERE | [72 empty] | 835
Canada | QC | LA BAIE | [72 empty] | 836
Canada | QC | LACADIE | [72 empty] | 837
Canada | QC | LASSOMPTION | [72 empty] | 838
Canada | QC | LENNOXVILLE | [72 empty] | 839
Canada | QC | MC TAVISH | [72 empty] | 840
Canada | QC | MONT JOLI AB | [72 empty] | 841
Canada | QC | MONT-ORFORD | [72 empty] | 842
Canada | QC | MONTREAL | [72 empty] | 843
Canada | QC | MONTREAL-MIRABEL | [72 empty] | 844
Canada | QC | NICOLET | [72 empty] | 845
Canada | QC | POINT-AU-PERE | [72 empty] | 846
Canada | QC | QUEBEC AP | [72 empty] | 847
Canada | QC | SHERBROOKE AP | [72 empty] | 848
Canada | QC | ST ANICET | [72 empty] | 849
Canada | QC | STE ANNE DE BELLEVUE | [72 empty] | 850
Canada | QC | STE FOY | [72 empty] | 851
Canada | QC | TROIS RIVIERES | [72 empty] | 852
Canada | QC | VARENNES | [72 empty] | 853
USA | RI | BLOCK ISLAND STATE ARPT | [72 empty] | 854
USA | RI | PAWTUCKET (AWOS) | [72 empty] | 855
USA | RI | PROVIDENCE T F GREEN STATE AR | [72 empty] | 856
Saudi Arabia | SA | RIYADH | [72 empty] | 857
USA | SC | ANDERSON COUNTY AP | [72 empty] | 858
USA | SC | BEAUFORT MCAS | [72 empty] | 859
USA | SC | CHARLESTON INTL ARPT | [72 empty] | 860
USA | SC | COLUMBIA METRO ARPT | [72 empty] | 861
USA | SC | FLORENCE REGIONAL AP | [72 empty] | 862
USA | SC | GREENVILLE DOWNTOWN AP | [72 empty] | 863
USA | SC | GREER GREENV-SPARTANBRG AP | [72 empty] | 864
USA | SC | MYRTLE BEACH AFB | [72 empty] | 865
USA | SC | SUMTER SHAW AFB | [72 empty] | 866
USA | SD | ABERDEEN REGIONAL ARPT | [72 empty] | 867
USA | SD | BROOKINGS (AWOS) | [72 empty] | 868
USA | SD | CHAN GURNEY MUNI | [72 empty] | 869
USA | SD | ELLSWORTH AFB | [72 empty] | 870
USA | SD | HURON REGIONAL ARPT | [72 empty] | 871
USA | SD | MITCHELL (AWOS) | [72 empty] | 872
USA | SD | MOBRIDGE | [72 empty] | 873
USA | SD | PIERRE MUNICIPAL AP | [72 empty] | 874
USA | SD | RAPID CITY REGIONAL ARPT | [72 empty] | 875
USA | SD | SIOUX FALLS FOSS FIELD | [72 empty] | 876
USA | SD | WATERTOWN MUNICIPAL AP | [72 empty] | 877
Canada | SK | MOOSE JAW AP | [72 empty] | 878
Canada | SK | PRINCE ALBERT AP | [72 empty] | 879
Canada | SK | REGINA | [72 empty] | 880
Canada | SK | SASKATOON | [72 empty] | 881
USA | TN | BRISTOL TRI CITY AIRPORT | [72 empty] | 882
USA | TN | CHATTANOOGA LOVELL FIELD AP | [72 empty] | 883
USA | TN | CROSSVILLE MEMORIAL AP | [72 empty] | 884
USA | TN | DYERSBURG MUNICIPAL AP | [72 empty] | 885
USA | TN | JACKSON MCKELLAR-SIPES REGL A | [72 empty] | 886
USA | TN | KNOXVILLE MCGHEE TYSON AP | [72 empty] | 887
USA | TN | MEMPHIS INTERNATIONAL AP | [72 empty] | 888
USA | TN | NASHVILLE INTERNATIONAL AP | [72 empty] | 889
USA | TX | ABILENE DYESS AFB | [72 empty] | 890
USA | TX | ABILENE REGIONAL AP [UT] | [72 empty] | 891
USA | TX | ALICE INTL AP | [72 empty] | 892
USA | TX | AMARILLO INTERNATIONAL AP [CANYON - UT] | [72 empty] | 893
USA | TX | AUSTIN MUELLER MUNICIPAL AP [UT] | [72 empty] | 894
USA | TX | BROWNSVILLE S PADRE ISL INTL | [72 empty] | 895
USA | TX | CAMP MABRY | [72 empty] | 896
USA | TX | CHILDRESS MUNICIPAL AP | [72 empty] | 897
USA | TX | COLLEGE STATION EASTERWOOD FL | [72 empty] | 898
USA | TX | CORPUS CHRISTI INTL ARPT [UT] | [72 empty] | 899
USA | TX | CORPUS CHRISTI NAS | [72 empty] | 900
USA | TX | COTULLA FAA AP | [72 empty] | 901
USA | TX | COX FLD | [72 empty] | 902
USA | TX | DALHART MUNICIPAL AP | [72 empty] | 903
USA | TX | DALLAS-FORT WORTH INTL AP | [72 empty] | 904
USA | TX | DALLAS/ADDISON ARPT | [72 empty] | 905
USA | TX | DALLAS/REDBIRD ARPT | [72 empty] | 906
USA | TX | DEL RIO [UT] | [72 empty] | 907
USA | TX | DEL RIO LAUGHLIN AFB | [72 empty] | 908
USA | TX | DRAUGHON MILLER CEN | [72 empty] | 909
USA | TX | EL PASO INTERNATIONAL AP [UT] | [72 empty] | 910
USA | TX | FORT HOOD | [72 empty] | 911
USA | TX | FORT WORTH ALLIANCE | [72 empty] | 912
USA | TX | FORT WORTH MEACHAM | [72 empty] | 913
USA | TX | FORT WORTH NAS | [72 empty] | 914
USA | TX | GALVESTON/SCHOLES | [72 empty] | 915
USA | TX | GEORGETOWN (AWOS) | [72 empty] | 916
USA | TX | HARLINGEN RIO GRANDE VALLEY I | [72 empty] | 917
USA | TX | HONDO MUNICIPAL AP | [72 empty] | 918
USA | TX | HOUSTON BUSH INTERCONTINENTAL | [72 empty] | 919
USA | TX | HOUSTON ELLINGTON AFB [CLEAR LAKE - UT] | [72 empty] | 920
USA | TX | HOUSTON WILLIAM P HOBBY AP | [72 empty] | 921
USA | TX | HOUSTON/D.W. HOOKS | [72 empty] | 922
USA | TX | KINGSVILLE | [72 empty] | 923
USA | TX | LAREDO INTL AP [UT] | [72 empty] | 924
USA | TX | LONGVIEW GREGG COUNTY AP [OVERTON - UT] | [72 empty] | 925
USA | TX | LUBBOCK INTERNATIONAL AP | [72 empty] | 926
USA | TX | LUFKIN ANGELINA CO | [72 empty] | 927
USA | TX | MARFA AP | [72 empty] | 928
USA | TX | MC GREGOR (AWOS) | [72 empty] | 929
USA | TX | MCALLEN MILLER INTL AP [EDINBURG - UT] | [72 empty] | 930
USA | TX | MIDLAND INTERNATIONAL AP | [72 empty] | 931
USA | TX | MINERAL WELLS MUNICIPAL AP | [72 empty] | 932
USA | TX | NACOGDOCHES (AWOS) | [72 empty] | 933
USA | TX | PALACIOS MUNICIPAL AP | [72 empty] | 934
USA | TX | PORT ARTHUR JEFFERSON COUNTY | [72 empty] | 935
USA | TX | RANDOLPH AFB | [72 empty] | 936
USA | TX | ROCKPORT/ARANSAS CO | [72 empty] | 937
USA | TX | SAN ANGELO MATHIS FIELD | [72 empty] | 938
USA | TX | SAN ANTONIO INTL AP | [72 empty] | 939
USA | TX | SAN ANTONIO KELLY FIELD AFB | [72 empty] | 940
USA | TX | SAN ANTONIO/STINSON | [72 empty] | 941
USA | TX | TYLER/POUNDS FLD | [72 empty] | 942
USA | TX | VICTORIA REGIONAL AP | [72 empty] | 943
USA | TX | WACO REGIONAL AP | [72 empty] | 944
USA | TX | WICHITA FALLS MUNICIPAL ARPT | [72 empty] | 945
USA | TX | WINK WINKLER COUNTY AP | [72 empty] | 946
USA | UT | CEDAR CITY MUNICIPAL AP | [72 empty] | 947
USA | UT | MOAB/CANYONLANDS [UO] | [72 empty] | 948
USA | UT | OGDEN HILL AFB | [72 empty] | 949
USA | UT | OGDEN HINKLEY AIRPORT | [72 empty] | 950
USA | UT | PROVO MUNI (AWOS) | [72 empty] | 951
USA | UT | SAINT GEORGE (AWOS) | [72 empty] | 952
USA | UT | SALT LAKE CITY INT ARPT [ISIS] | [72 empty] | 953
USA | UT | VERNAL | [72 empty] | 954
USA | UT | WENDOVER USAF AUXILIARY FIELD | [72 empty] | 955
USA | VA | ABINGDON | [72 empty] | 956
USA | VA | CHARLOTTESVILLE FAA | [72 empty] | 957
USA | VA | DANVILLE FAA AP | [72 empty] | 958
USA | VA | DAVISON AAF | [72 empty] | 959
USA | VA | FARMVILLE | [72 empty] | 960
USA | VA | FRANKLIN NAAS | [72 empty] | 961
USA | VA | HILLSVILLE | [72 empty] | 962
USA | VA | HOT SPRINGS/INGALLS | [72 empty] | 963
USA | VA | LANGLEY AFB | [72 empty] | 964
USA | VA | LEESBURG/GODFREY | [72 empty] | 965
USA | VA | LYNCHBURG REGIONAL ARPT | [72 empty] | 966
USA | VA | MANASSAS MUNI(AWOS) | [72 empty] | 967
USA | VA | MARION / WYTHEVILLE | [72 empty] | 968
USA | VA | MARTINSVILLE | [72 empty] | 969
USA | VA | MELFA/ACCOMACK ARPT | [72 empty] | 970
USA | VA | NEWPORT NEWS | [72 empty] | 971
USA | VA | NORFOLK INTERNATIONAL AP | [72 empty] | 972
USA | VA | NORFOLK NAS | [72 empty] | 973
USA | VA | OCEANA NAS | [72 empty] | 974
USA | VA | QUANTICO MCAS | [72 empty] | 975
USA | VA | RICHMOND INTERNATIONAL AP | [72 empty] | 976
USA | VA | ROANOKE REGIONAL AP | [72 empty] | 977
USA | VA | SHANNON ARPT | [72 empty] | 978
USA | VA | STAUNTON/SHENANDOAH | [72 empty] | 979
USA | VA | VIRGINIA TECH ARPT | [72 empty] | 980
USA | VA | WASHINGTON DC DULLES INT AR [STERLING - ISIS] | [72 empty] | 981
USA | VA | WASHINGTON DC REAGAN AP | [72 empty] | 982
USA | VA | WINCHESTER RGNL | [72 empty] | 983
USA | VA | WISE/LONESOME PINE | [72 empty] | 984
USA | VT | BURLINGTON INTERNATIONAL AP | [72 empty] | 985
USA | VT | HO CHI MIHN | [72 empty] | 986
USA | VT | MONTPELIER AP | [72 empty] | 987
USA | VT | RUTLAND STATE | [72 empty] | 988
USA | VT | SPRINGFIELD/HARTNES | [72 empty] | 989
USA | WA | BELLINGHAM INTL AP | [72 empty] | 990
USA | WA | BREMERTON NATIONAL | [72 empty] | 991
USA | WA | EPHRATA AP FCWOS | [72 empty] | 992
USA | WA | FAIRCHILD AFB | [72 empty] | 993
USA | WA | FELTS FLD | [72 empty] | 994
USA | WA | GRAY AAF | [72 empty] | 995
USA | WA | HANFORD | [72 empty] | 996
USA | WA | HOQUIAM AP | [72 empty] | 997
USA | WA | KELSO WB AP | [72 empty] | 998
USA | WA | MOSES LAKE GRANT COUNTY AP | [72 empty] | 999
USA | WA | OLYMPIA AIRPORT | [72 empty] | 1000
USA | WA | PASCO | [72 empty] | 1001
USA | WA | PULLMAN/MOSCOW RGNL | [72 empty] | 1002
USA | WA | QUILLAYUTE STATE AIRPORT | [72 empty] | 1003
USA | WA | RENTON MUNI | [72 empty] | 1004
USA | WA | SEATTLE BOEING FIELD [ISIS] | [72 empty] | 1005
USA | WA | SEATTLE SEATTLE-TACOMA INTL A | [72 empty] | 1006
USA | WA | SNOHOMISH CO | [72 empty] | 1007
USA | WA | SPOKANE INTERNATIONAL AP [CHENEY - UO] | [72 empty] | 1008
USA | WA | STAMPEDE PASS | [72 empty] | 1009
USA | WA | TACOMA MCCHORD AFB | [72 empty] | 1010
USA | WA | TACOMA NARROWS | [72 empty] | 1011
USA | WA | THE DALLES MUNICIPAL ARPT | [72 empty] | 1012
USA | WA | WALLA WALLA CITY COUNTY AP | [72 empty] | 1013
USA | WA | WENATCHEE/PANGBORN | [72 empty] | 1014
USA | WA | WHIDBEY ISLAND NAS | [72 empty] | 1015
USA | WA | WILLIAM R FAIRCHILD | [72 empty] | 1016
USA | WA | YAKIMA AIR TERMINAL | [72 empty] | 1017
USA | WI | APPLETON/OUTAGAMIE | [72 empty] | 1018
USA | WI | EAU CLAIRE COUNTY AP | [72 empty] | 1019
USA | WI | GREEN BAY AUSTIN STRAUBEL INT | [72 empty] | 1020
USA | WI | JANESVILLE/ROCK CO. | [72 empty] | 1021
USA | WI | LA CROSSE MUNICIPAL ARPT | [72 empty] | 1022
USA | WI | LONE ROCK FAA AP | [72 empty] | 1023
USA | WI | MADISON DANE CO REGIONAL ARPT [ISIS] | [72 empty] | 1024
USA | WI | MANITOWOC MUNI AWOS | [72 empty] | 1025
USA | WI | MARSHFIELD MUNI | [72 empty] | 1026
USA | WI | MILWAUKEE MITCHELL INTL AP | [72 empty] | 1027
USA | WI | MINOCQUA/WOODRUFF | [72 empty] | 1028
USA | WI | MOSINEE/CENTRAL WI | [72 empty] | 1029
USA | WI | PHILLIPS/PRICE CO. | [72 empty] | 1030
USA | WI | RHINELANDER ONEIDA | [72 empty] | 1031
USA | WI | RICE LAKE MUNICIPAL | [72 empty] | 1032
USA | WI | STURGEON BAY | [72 empty] | 1033
USA | WI | WATERTOWN | [72 empty] | 1034
USA | WI | WAUSAU MUNICIPAL ARPT | [72 empty] | 1035
USA | WI | WITTMAN RGNL | [72 empty] | 1036
USA | WV | BECKLEY RALEIGH CO MEM AP | [72 empty] | 1037
USA | WV | BLUEFIELD/MERCER CO [NREL] | [72 empty] | 1038
USA | WV | CHARLESTON YEAGER ARPT | [72 empty] | 1039
USA | WV | ELKINS ELKINS-RANDOLPH CO ARP | [72 empty] | 1040
USA | WV | HARRISON MARION RGN | [72 empty] | 1041
USA | WV | HUNTINGTON TRI-STATE ARPT | [72 empty] | 1042
USA | WV | LEWISBURG/GREENBRIE | [72 empty] | 1043
USA | WV | MARTINSBURG EASTERN WV REG AP | [72 empty] | 1044
USA | WV | MORGANTOWN HART FIELD | [72 empty] | 1045
USA | WV | PARKERSBURG WOOD COUNTY AP | [72 empty] | 1046
USA | WV | WHEELING OHIO COUNTY AP | [72 empty] | 1047
USA | WY | CASPER NATRONA CO INTL AP | [72 empty] | 1048
USA | WY | CHEYENNE MUNICIPAL ARPT | [72 empty] | 1049
USA | WY | CODY MUNI (AWOS) | [72 empty] | 1050
USA | WY | GILLETTE/GILLETTE-C | [72 empty] | 1051
USA | WY | JACKSON HOLE | [72 empty] | 1052
USA | WY | LANDER HUNT FIELD | [72 empty] | 1053
USA | WY | LARAMIE GENERAL BREES FIELD | [72 empty] | 1054
USA | WY | RAWLINS MUNICIPAL AP | [72 empty] | 1055
USA | WY | RIVERTON MUNICIPL AP | [72 empty] | 1056
USA | WY | SHERIDAN COUNTY ARPT | [72 empty] | 1057
USA | WY | WORLAND MUNICIPAL | [72 empty] | 1058
Canada | YT | WHITEHORSE | [72 empty] | 1059