## Cover Sheet
Phius Quality Assurance Workbook* for Non-Residential Projects - v26.1.0 (May 2026)
*For projects with multiple non-residential buildings, or comprised of a combination of non-residential and residential portions, please complete a Phius QA Non-Residential Workbook for each non-residential building or non-residential portion of the project, and complete a Phius QA MF Workbook for each residential building or residential portion of the project.
Project Information
Project Name | Phius Project Number | Building Permit Date | Number of Stories | Total # Dwelling Units | Country
[Select Dropdown]
Street Address | City |  | State/Province | Zip Code | Phius Project Path | Phius Project Certification Standard
|  |  | [Select Dropdown] |  | Performance | [Select Dropdown]
Confirm most current set of building drawings used by Verifier have been included in the project documentation folder: |  |  |  |  | [Select Dropdown]
Please save the Non-Residential QA Workbook using the following naming convention: (#### is the Phius Project Number) |  |  |  |  | ####_NR QA Workbook_YYYY.MM.DD
Project Team | Company Name |  |  |  | Contact Name
Phius Certified Verifier1:
Phius Certified Consultant (CPHC):
Architect:
General Contractor / Builder:
Mechanical Systems Designer:
HVAC Contractor:
Commissioning Agent:
Building Owner:
CO-REQUISITE PROGRAM ELIGIBILITY2,3 |  |  |  | CO-REQUISITE PROGRAM VERSION2,3
Select the applicable eligibility based on the Phius Certification Guidebook Section 1.5.3 Program Eligibility Criteria |  |  |  | Use the appropriate program checklist, as a guide, as applicable.
Program | Program Eligibility |  |  | Program |  | Program Checklist Requirements
DOE ENERGY STAR Multifamily New Construction | Exempt from certification requirement however, co-requisite program checklists are required. |  |  | DOE ENERGY STAR Multifamily New Construction (MFNC) |  | Apply checklist items as appropriate.
EPA Indoor AirPlus | Exempt from certification requirement however, co-requisite program checklists are required. |  |  | EPA Indoor AirPlus |  | Apply checklist items as appropriate.
DOE Efficient New Homes Multifamily4 | Exempt from certification requirement however, co-requisite program checklists are required. |  |  | DOE Efficient New Homes Multifamily Version |  | Apply checklist items as appropriate.
Welcome to the Phius Quality Assurance Workbook for Non-Residential projects!
Using This Workbook This workbook shall be used by a Phius certified Verifier for all non-residential projects, regardless of size, including hotels and motels, and for the non-residential part of a mixed-use building.
Certification Criteria The Phius Certification process for non-residential projects includes energy modeling and design consulting performed by a Phius Certified Consultant (CPHC) to demonstrate compliance with Phius program energy performance metrics, as well as on-site verification of all critical project energy features by a Phius Certified Verifier. The purpose of this workbook is to create a single, organized data collection form that shall be used by PHIUS+ Verifiers to document required on-site verification measures that are required for PHIUS+ Certification of non-residential projects. Non-residential projects shall use the criteria for the DOE ENERGY STAR Multifamily New Construction program (MFNC), EPA Indoor AirPlus (IAP), and DOE Efficient New Homes programs and follow checklist requirements of those programs.4,5 Non-residential Projects shall be exempt from certifying under those programs however, the certification checklist criteria for these programs shall still be achieved in order to help ensure that non-residential projects seeking PHIUS+ Certification are not only energy efficient, but are also durable, comfortable and healthy buildings. For full program requirements, please see the Phius Certification Guidebook (https://www.phius.org/phius-certification-guidebook).
There are twelve (12) worksheets to complete (see the tabs below).
Responsible parties for completing each tab:
0-Key Documents (Key Docs) |  |  |  | Phius Certified Verifier
1.1-Building Envelope Air Tightness Testing Whole Building (AirTight WB)
1.2-Building Envelope Air Tightness Testing Compartmentalization (AirTight Comp)
2.1-Ventilation Systems ERV/HRV (Vent ERV_HRV)
2.2-Ventilation Auxiliary Supply & Exhaust Only (Vent Auxiliary)
3-Heating & Cooling (Heat & Cool) |  |  |  | HVAC Designer/Contractor, Phius Certified Verifier
4-Domestic Hot Water (DHW) |  |  |  | Phius Certified Verifier
5.1-Appliances & Electrical Loads (Office Equipment)
5.2-Appliances & Electrical Loads (Kitchen)
5.3-Appliances & Electrical Loads (Lighting)
5.4-Appliances & Electrical Loads (Process Loads)
6-Renewables & Electrification
Phius Certified Verifiers are welcome to add their own custom sheets to this workbook for instance, to track project notes.
Questions regarding particular checklist items should be directed first to the Phius Verifier for the project. - Contact the Phius QA/QC Manager at QA@phius.org for questions on the nuances between certifying an entire building under Phius and certifying individual dwelling units within such buildings under Energy Star / DOE Efficient New Homes. - Contact https://www.phius.org/help for questions regarding the certification process for any project.
Footnotes:
1Refer to the Phius Guidebook for specific guidance on eligibility of Raters to serve as Verifiers on a project.
2Projects located outside of the United States, or in California or Alaska, will not be required to meet DOE Energy Star, EPA Indoor AirPlus, and DOE Efficient New Homes certifications, regardless of their configuration.
3See Phius 2024 Passive Building Standards Certification Guidebook v.25.1.0, Table 1.3.0 and Section 1.5.3 for additional Co-Requisite Program Requirements.
4In this QA Workbook the following acronyms will be used as abbreviations for the co-requisite programs: DOE ENERGY STAR (ES), EPA Indoor AirPlus (IAP), DOE Efficient New Homes (ENH).
5In September 2025 DOE announced DOE Efficient New Homes is the successor program to DOE Zero Energy Ready Home. The Phius 2025.1.0 Guidebook refers to the DOE program as the Zero Energy Ready Home (ZERH) program, as the Guidebook was published before the successor program was announced.

## 0-Key Docs
Phius NR Quality Assurance Workbook 0-Key Documents1
0 | 0 - Certificates & Summaries / Co-requisite Programs | Rater Confirmed | N/A | PROG. REQ.
0.0.1 | Provide completed Phius Quality Control Field Checklist (v25.1.0, or newer). | FALSE | FALSE | Phius
0.0.2 | Provide signed DOE ENERGY STAR Multifamily New Construction National Rater Field Checklist.2,3 | FALSE | FALSE | ES
0.0.3 | Provide signed EPA Indoor AirPlus Verification Checklist.2 | FALSE | FALSE | IAP
0.0.4 | Provide signed DOE Efficient New Homes Multifamily National Rater Checklist.2 | FALSE | FALSE | ENH
0.1 | 1 - Building Envelope | Rater Confirmed | N/A | PROG. REQ.
0.1.1 | Insulated Assemblies (Material & R-value verification)
0.1.1.1 | Provide technical datasheets1of any insulation type installed that was not uploaded to folder: 2. Datasheets & Specifications / 4. Insulation. | FALSE | FALSE | Phius
0.1.2 | Windows & Doors
0.1.2.1 | If no photo of NFRC sticker is available, provide Window Purchase Order or Shop Drawings. | FALSE | FALSE | Phius
0.1.2.2 | Provide technical datasheets of any product that has been changed since Phius Design Review. | FALSE | FALSE | Phius
0.1.3 | Airtightness
0.1.3.1 | Provide Whole Building Blower Door Testing Plan. | FALSE | FALSE | Phius
0.1.3.2 | Provide Final Operational (Untaped) Air Tightness Test Report (depressurization and pressurization), and Durability (Taped) Test if conducted, and list within the notes section of the blower door test results any items taped. All non-threatening items allowed for the taped test can be found at Section C-2.2 Non-Threatening Air Leakage, Phius 2024 Passive Building Standards Certification Guidebook v25.1.0. | FALSE | FALSE | Phius
0.2 | 2 - Ventilation | Rater Confirmed | N/A | PROG. REQ.
0.2.1 | If ventilation system is a Minotair, provide a completed Phius MINOTAIR PentaCare calculator. | FALSE | FALSE | Phius
0.2.2 | Provide Testing and Balancing (TAB) report of ducted ventilation system. | FALSE | FALSE | Phius
0.3 | 3 - Heating & Cooling | Rater Confirmed | N/A | PROG. REQ.
0.3.1 | Provide AHRI certificate and/or manufacturer's detailed specs of each installed heating, cooling, and DHW system.3 | FALSE | FALSE | Phius
0.3.2 | Provide as-built Mechanical Drawings, if available, if changes were made since design certification was issued. | FALSE | FALSE | Phius
0.3.3 | Provide Heating & Cooling Testing and Balancing report for ducted heating and/or cooling systems. | FALSE | FALSE | Phius
0.3.4 | All items under Line 4, "Air Balancing of Supply Registers & Return Grilles," of the Energy Star Multifamily New Construction National HVAC Functional Testing Checklist, Version 1.1 / 1.2 / 1.3 (Rev. 05 or newer) are required.4 | FALSE | FALSE | Phius
0.4 | 4 - Domestic Hot Water | Rater Confirmed | N/A | PROG. REQ.
0.4.1 | Provide Energy Star Certificate (https://www.energystar.gov/products) or AHRI Certificate for each installed DHW system. | FALSE | FALSE | Phius
0.5 | 5 - Appliances & Electrical Loads | Rater Confirmed | N/A | PROG. REQ.
0.5.1 | Office Equipment: If available, provide Energy Star Certificate (https://www.energystar.gov/products) for each builder-installed office equipment. | FALSE | FALSE | Phius
0.5.2 | Office Equipment: For all other office equipment provide manufacturer's technical datasheet that indicates Power (Watts) and Power Rating (Watts) in Saving/Sleep Mode. | FALSE | FALSE | Phius
0.5.3 | Kitchen Equipment: Provide Energy Star Certificate (https://www.energystar.gov/products) for each builder-installed kitchen appliance. | FALSE | FALSE | Phius
0.5.4 | Kitchen Equipment: For all other Kitchen Equipment, provide equivalent documentation. | FALSE | FALSE | Phius
0.5.5 | Process Loads: If available, provide Energy Star Certificate (https://www.energystar.gov/products) for each builder-installed process load. | FALSE | FALSE | Phius
0.5.6 | Process Loads: For all other process loads provide manufacturer's technical datasheet that shows energy use in kWh/yr. | FALSE | FALSE | Phius
0.5.7 | Lighting: Provide Reflected Ceiling Plans to confirm light fixture types and quantities. | FALSE | FALSE | Phius
0.5.8 | Lighting: Provide completed/updated Phius Non-Residential Lighting Calculator (https://www.phius.org/phius-non-residential-lighting-calculator). | FALSE | FALSE | Phius
0.6 | 6 - Renewables & Electrification | Rater Confirmed | N/A | PROG. REQ.
0.6.1 | Provide shop drawings or documentation that show the tilt, azimuth, and kW size of each installed PV system. | FALSE | FALSE | Phius
0.6.2 | Provide completed DOE Efficient New Homes Multifamily PV-Ready Checklist. | FALSE | FALSE | ENH
0.6.3 | Provide contract documents for any off-site renewable production that align with Appendix N-4.3 (Off-Site Renewable Energy Requirements) of the Phius 2024 Passive Building Standards Certification Guidebook v25.1.0. | FALSE | FALSE | Phius
Notes:
Footnotes
1Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."
2For projects certifying under Phius 2024 use the version of the co-requisite program (or a newer version) required for Non-Residential listed within Table 1.3.0 of the Phius 2024 Passive Building Standards Certification Guidebook v25.1.0. For projects certifying under Phius 2021, 2018, and 2015 this Workbook does not apply. Use the version of the Workbook that applies to the corresponding Program Version Eligibility Dates listed at: https://www.phius.org/phius-certification-program-version-eligibility-dates.
3Non-residential projects seeking to pursue Energy Star recognition should follow the instructions to "Achieve Designed to Earn the ENERGY STAR" (https://www.energystar.gov/buildings/resources_audience/service_product_providers/commercial-new-construction/achieve-designed-earn-energy-star). and the ENERGY STAR Design Guide (https://www.energystar.gov/buildings/tools-and-resources/energy-star-design-guide).
4Energy Star Multifamily New Construction National HVAC Functional Testing Checklist: https://www.energystar.gov/partner-resources/residential-new/multifamily-national-page

## 1.1-AirTight WB
Phius NR Quality Assurance Workbook 1.1-Building Envelope Airtightness Testing (Whole Building)
| 1.1 | Whole Building Airtightness Testing
| 1.1.1 | Blower Door Test Threshold Calculator |  | Building is 5+ stories in height & non-combustible construction? |  | [Select Dropdown]
Building Envelope Area (ft2)
|  |  |  | Project Threshold (CFM50/ft2) |  | Pending Input Cell L6
|  |  |  | Project Threshold (CFM50) |  | Pending Input Cells L7&L8
| 1.1.2 | Was a durability test performed during final blower door testing? (For more information on what is allowed on a durability test, see Phius Certification Guidebook 2025, Appendix C-2.3)1,2,3 |  | [Select Dropdown]
#REF! | 1.1.3 | Preliminary test: Preliminary whole building blower door test is: | Optional | Preliminary Test | (CFM50/ft2) | CFM50
Depressurization Test Result
Pressurization Test Result
Average Test Result
| 1.1.4 | Operational test: Final whole building blower door multi-point test4 is: | Mandatory | Final Test (Operational - mandatory) | (CFM50/ft2) | CFM50
Depressurization Test Result
Pressurization Test Result
Average Test Result
Criteria Passed?
| 1.1.5 | If operational test, please list those items taped:
| 1.1.6 | Durability test: Final whole building blower door multi-point test2 is: | If necessary | Final Test (Durability - if necessary) | (CFM50/ft2) | CFM50
Depressurization Test Result
Pressurization Test Result
Average Test Result
|  |  |  | Criteria Passed? |  | Pending Input Cell L6
| 1.1.7 | If durability test, please list those items taped:
Notes:
Footnotes:
1If testing at 75 Pa, use the Airtightness Pressure Conversion Calculator found in the Phius Resource Library to convert tested pressures from 75Pa to 50Pa, and enter into this page of the Workbook the values at 50Pa.
2The Phius requirement of 0.06 cfm50/sqft must be met through a durability test. If an operational test result is less than 0.06 cfm50/sqft, a durability test is not necessary.
3In accordance with ANSI/RESNET/ICC 380-2022 or latest version. NOTE: For Large MF or Non-Res. Bldgs- Alternative Test methods and building set up - per ABAA Standard Method for Building Enclosure Airtightness Compliance Testing, ASTM E-3158 or ASTM E-779.
4The result of the operational test is always input into the WUFI model. An operational test is always required.

## 1.2-AirTight Comp
Phius NR Quality Assurance Workbook 1.2-Building Envelope Airtightness Testing (Compartmentalization) (if applicable)
Sleeping Unit Compartmentalization Test: Compartmentalization testing shall be performed to test air tightness of individual sleeping units at the same stage of construction within a 90-calendar day period in accordance with Chapter 6 - RESENT National Standards for Sampled Ratings (https://standards.resnet.us/docs/resnet-hers-standards). Please discuss SAMPLING with your RESNET QA Provider and Phius to ensure your RESNET QA Provider and Phius will support sampling being applied to the project. Then develop a Sampling Plan approved by your RESNET QA Provider PRIOR TO initiating sampling. Sampling shall be conducted in accordance with the Sampling Plan. To qualify for sampling a builder must complete a Verification Set prior to completing a Qualification Set, and prior to qualifying for Sampling. Sample Sets that include multiple buildings with five (5) units or more per building shall have a minimum of one unit tested per building. The measured air tightness of an individual sleeping unit in the Qualification Set that fails to meet the Threshold Specification shall be corrected and re-inspected and/or retested until it meets the Threshold Specification. Testing may be performed in either depressurization or pressurization mode.
1.2.1 | Project Specifications
Total # of Sleeping Units in project: Note: A Sample Set that includes multifamily buildings with five (5) units or more per building shall total the number of Sleeping Units among all buildings.
Total # of Sleeping Units at the same stage of construction within a 90-day period eligible to be included in the Sample Set:1
| Total # of Sleeping Units that are not at the same stage of construction within a 90-day period, and that are not included in the Sample Set: | [8 empty] | -
| Indoor Airplus (IAP) Version: | [8 empty] | [Select Dropdown]
| Test Threshold Specification (cfm50/ft2): | [8 empty] | -
1.2.2 | Testing Protocol
| Verifier has discussed sleeping unit sampling plan with RESNET QA Provider and Phius prior to initiating sampling, and has provided Phius a copy of the Sampling Plan per RESNET National Standard for Sampled Ratings (https://standards.resnet.us/docs/resnet-hers-standards): | [8 empty] | [Select Dropdown]
| Verifier understands they will confirm: 1) A Verification Set of 5 or more Sleeping Units (Section 1.2.4). 2) A Qualification Set that has been verified in five (5) consecutive Sleeping Units without any incidence of failure (Section 1.2.5). 3) A correction, re-inspection and/or retesting for any feature that failed to meet the Threshold Specification (Section 1.2.3) until the Threshold Specification has been verified in five (5) consecutive Sleeping Units without any incidence of failure. 4) A sample set that includes 20% of the remaining Sleeping Units (Section 1.2.6). | [8 empty] | [Select Dropdown]
1.2.3 | 1. Verification Set
A builder or developer shall complete and have verified the Threshold Specification has been met in a minimum of five (5) Sleeping Units prior to conducting a Qualification Set for testing airtightness of individual sleeping units.1
| Verification Unit 1 |  | Verification Unit 2 |  | Verification Unit 3 |  | Verification Unit 4 |  | Verification Unit 5
| Unit # | 100 | Unit # | 101 | Unit # |  | Unit # |  | Unit #
| Unit SFBE2 | 450 | Unit SFBE | 450 | Unit SFBE |  | Unit SFBE |  | Unit SFBE
| CFM@50 Pa3 | 88 | CFM@50 Pa | 120 | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa
| ELR4 | 0.19556 | ELR | 0.26667 | ELR | - | ELR | - | ELR | -
| Verified? | - | Verified? | - | Verified? | - | Verified? | - | Verified? | -
| Verifier has confirmed that the builder or developer has completed and has verified the Threshold Specification has been met in a minimum of five (5) Sleeping Units prior to conducting a Qualification Set for testing airtightness of individual sleeping units: | [8 empty] | [Select Dropdown]
Total number of Sleeping Units in Verification Set that meet the Threshold Specification:
1.2.4 | 2. Qualification Set
Any feature being Sampled must qualify for Sampling by being successfully verified to meet the Threshold Specification for five (5) CONSECUTIVE Sampled Features. To qualify for sampling a builder must complete a Qualification Set.1 A Qualification Set may be made up of five (5) Sleeping Units that meet the Threshold Specification in five (5) CONSECUTIVE Sleeping Units without incidence of failure. However, a Qualification Set shall be made up of more than five (5) Sleeping Units if a failure occurs while qualifying the feature. Any feature that fails to meet the Threshold Specification (Section 1.2.3) shall be corrected and re-inspected and/or retested until it meets the Threshold Specification. Enter in the table below the airtightness testing results for the Qualification Set, adding additional rows until the Threshold Specification has been met in five (5) CONSECUTIVE Sleeping Units.
| Qualification Unit 1 |  | Qualification Unit 2 |  | Qualification Unit 3 |  | Qualification Unit 4 |  | Qualification Unit 5
| Unit # |  | Unit # |  | Unit # |  | Unit # |  | Unit #
| Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE
| CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa
| ELR4 | - | ELR | - | ELR | - | ELR | - | ELR | -
| Verified? | - | Verified? | - | Verified? | - | Verified? | - | Verified? | -
| Verifier has confirmed that the Threshold Specification (<0.3 cfm50/ft2) has been met in five (5) consecutive Sleeping Units without any incidence of Failure: | [8 empty] | [Select Dropdown]
Total number of Sleeping Units in the Qualification Set that meet the Threshold Specification:
| Total number of Sleeping Units (# in Verification Set + # in Qualification Set) that meet the Threshold Specification: | [8 empty] | -
1.2.5 | 3. Sample Set5
After the Qualification Set is achieved, 20% of the remaining unsampled Sleeping Units become the Sample Set. Enter in the table below the airtightness testing results for the Sample Set, adding additional rows until the 20% Sample Set (quantity in cell M45) has been achieved. Sampling shall be conducted in accordance with the Sampling Plan.
| Total # of unsampled Sleeping Units eligible for sampling: [Total units in same 90 day period, cell M8 - (# in Verification + # in Qualification Set, cell M38)] | [8 empty] | -
| The total # of unsampled Sleeping Units required to be sampled to achieve the 20% Sample Set: Note: A Sample Set that includes multifamily buildings with five (5) units or more per building shall have a minimum of one unit verified per building. | [8 empty] | -
| Sampled Unit 1 |  | Sampled Unit 2 |  | Sampled Unit 3 |  | Sampled Unit 4 |  | Sampled Unit 5
| Unit # |  | Unit # |  | Unit # |  | Unit # |  | Unit #
| Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE
| CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa
| ELR | - | ELR | - | ELR | - | ELR | - | ELR | -
| Verified? | - | Verified? | - | Verified? | - | Verified? | - | Verified? | -
| Sampled Unit 6 |  | Sampled Unit 7 |  | Sampled Unit 8 |  | Sampled Unit 9 |  | Sampled Unit 10
| Unit # |  | Unit # |  | Unit # |  | Unit # |  | Unit #
| Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE
| CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa
| ELR4 | - | ELR | - | ELR | - | ELR | - | ELR | -
| Verified? | - | Verified? | - | Verified? | - | Verified? | - | Verified? | -
| Sampled Unit 11 |  | Sampled Unit 12 |  | Sampled Unit 13 |  | Sampled Unit 14 |  | Sampled Unit 15
| Unit # |  | Unit # |  | Unit # |  | Unit # |  | Unit #
| Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE
| CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa
| ELR4 | - | ELR | - | ELR | - | ELR | - | ELR | -
| Verified? | - | Verified? | - | Verified? | - | Verified? | - | Verified? | -
| Sampled Unit 16 |  | Sampled Unit 17 |  | Sampled Unit 18 |  | Sampled Unit 19 |  | Sampled Unit 20
| Unit # |  | Unit # |  | Unit # |  | Unit # |  | Unit #
| Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE |  | Unit SFBE
| CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa |  | CFM@50 Pa
| ELR4 | - | ELR | - | ELR | - | ELR | - | ELR | -
| Verified? | - | Verified? | - | Verified? | - | Verified? | - | Verified? | -
Notes:
Footnotes:
1If fewer than five (5) Sleeping Units are available for that phase of inspection, the Sample Set must be limited to the number of Sleeping Units that are available within that 90-day period.
2SFBE - Square Feet of Building Envelope
3CFM@50 Pa - Measured CFM at 50 Pascals
4ELR - Envelope Leakage Ratio
5If Sampling Needs to be adjusted, because it is determined that some of the Sleeping Units need to be removed from the sampling process (e.g. not fully completed), then see: Section 603.2.3, RESENT National Standards for Sampled Ratings, https://standards.resnet.us/docs/resnet-hers-standards).

## 2.1-Vent ERV_HRV
Phius NR Quality Assurance Workbook 2.1-Ventilation Systems (ERV/HRV)
This worksheet shall be completed for all E/HRV systems.
The airflow rates at the Ventilation Unit and at the individual registers shall be measured* at the design 24/7 ventilation rate.
The instructions for completing this tab can be found in the Phius Quality Control Field checklist, Section 2.1.7.
*Measured means either Verifier has measured or directly observed.
Ventilation System Installation & Airflow Testing Verification
2.1.1 | Measured at each Ventilation Unit | Measured at each Ventilation Unit at the design 24/7 Airflow Speed Setting
|  | ERV/HRV # or Tag # | Centralized or Decentralized | Location | System Type1 | Manufacturer | Model # | Merv Rating of Filter | Total Duct Insulation (R-value) |  | Type of ERV/HRV Defrost (External) | Design Airflow (cfm) |  | Airflows measured by: | Measured Airflow (cfm) |  | Measured Fan Power (Watts)2 | Equipment & Nameplate Photos Uploaded?3 | Electric Efficiency (W/cfm) | Measured Supply & Exhaust Airflow within 10%
[9 empty] | Supply | Exhaust |  | Supply | Exhaust |  | Supply | Exhaust
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
2.1.2 | Measured at each Register | Measured at Sampled Registers at the design 24/7 Airflow Speed Setting (if applicable, per instructions in Section 2.1.7 of the Field Checklist)
|  | Supply Airflow (24/7) | Supply Register | [10 empty] | Supply Airflow |  |  |  |  | Measured Airflow Status
|  |  | ERV/HRV # or Tag # | Space Tag # |  | Supply Register Location | [7 empty] | Airflows measured by | Design (cfm) | Measured (cfm) |  |  | Within +/- 5cfm or +/- 20% of design
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [7 empty] | [Select Dropdown]
|  | Exhaust Airflow (24/7) | Exhaust Register | [10 empty] | Exhaust Airflow |  |  |  |  | Measured Airflow Status
|  |  | ERV/HRV # or Tag # | Space Tag # |  | Exhaust Register Location | [7 empty] | Airflows measured by | Design (cfm) | Measured (cfm) |  |  | Within +/- 5cfm or +/- 20% of design
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
[6 empty] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [7 empty] | [Select Dropdown]
Ventilator Defrost Systems - Subsoil Heat Exchanger (If Applicable)
2.1.3 | ERV/HRV # or Tag # served by Ventilator Defrost System | [8 empty] | Loop length (ft) |  | Approximate depth (ft) |  | Measured loop pump power (W) |  | Project team has demonstrated the ground loop / earth tube control logic is set up properly.
[Select Dropdown]
[Select Dropdown]
[Select Dropdown]
[Select Dropdown]
Ventilation Dehumidifier (If Applicable)
2.1.4 | ERV/HRV # or Tag # served by Dehumidifier | [8 empty] | Manufacturer |  | Model |  | Quantity | l/kWh | Equipment & Nameplate Photos Uploaded?2
[Select Dropdown]
[Select Dropdown]
[Select Dropdown]
[Select Dropdown]
Notes:
Footnotes:
1A CERV or Minotair is considered an Integrated System
2Please see Phius Guidebook Section 1.5.2.4 Ventilation, Power Consumption.
3Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."

## 2.2-Vent Auxiliary
Phius NR Quality Assurance Workbook 2.2-Ventilation Auxiliary Airflow Systems (Supply Only & Exhaust Only) (If Applicable)
The airflow rates shall be measured* as indicated below.
*Measure means either Verifier has measured or directly observed.
Range Hood
2.2.1 | Room Type | Airflow Type | Equipment Location | Manufacturer | Model # | Power readings (from manufacturer nameplate) |  |  | Direct Exhaust or Recirculation | If Direct Exhaust Measured Exhaust Airflow (at Median cfm) | Equipment & Nameplate Photos Uploaded?1
[6 empty] | Volts | Amps | Watts
| [Select Dropdown] | [Select Dropdown] | [6 empty] | [Select Dropdown] |  | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [6 empty] | [Select Dropdown] |  | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [6 empty] | [Select Dropdown] |  | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [6 empty] | [Select Dropdown] |  | [Select Dropdown]
Auxiliary - Ventilation Systems (if Applicable) (e.g., Make-up Air System, Trash Room, Compactor room, Computer Room, Elevator Machine Room, Auxiliary Exhaust Fan)
2.2.2 | System Type | Airflow Type | Equipment Location | Manufacturer | Model # | Power readings (from manufacturer nameplate) |  |  | Design Airflow (cfm) | Measured Airflow (at typical cfm)2 | Equipment & Nameplate Photos Uploaded?1
[6 empty] | Volts | Amps | Watts
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
Notes:
Footnotes:
1Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."
2The max airflow from manufacturer's datasheet will be used if the measured 24/7 airflow is not available.

## 3-Heat & Cool
Phius NR Quality Assurance Workbook 3-Heating & Cooling
3 | Heating/Cooling System - Outdoor Component | [9 empty] | Rater Confirmed | n/a | PROG. REQ.
3.0.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Manufacturer | Model# | Quantity | MERV Rating of Filter | Heating/Cooling System Type | Ducted or Non-Ducted? |  | AHRI Certificate Uploaded?1 | Equipment & Nameplate Photos Uploaded?1
3.0.1.1 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE | Phius
3.0.1.2 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.3 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.4 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.5 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.6 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.7 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.8 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.9 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.10 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.2 | Describe any supplemental heating/cooling systems installed:
[11 empty] | FALSE | FALSE | Phius
Notes:
3.1 | Heating/Cooling System - Indoor Component | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
3.1.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Manufacturer | Model# | Quantity | MERV Rating of Filter | Heating/Cooling System Type | Ducted or Non-Ducted? | Serves which Outdoor Unit? (select Tag Name)
3.1.1.1 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE | Phius
3.1.1.2 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.3 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.4 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.5 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.6 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.7 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.8 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.9 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.10 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.2 | Describe any supplemental heating/cooling systems installed:
[11 empty] | FALSE | FALSE | Phius
Notes:
3.2 | Heating/Cooling System - Fans associated with the ASHP System | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
3.2.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Manufacturer | Model# | Quantity | Fan Power Rating from Nameplate (Watts)
[5 empty] | Heating | Cooling2
3.2.1.1 | [10 empty] | FALSE | FALSE | Phius
3.2.1.2 | [10 empty] | FALSE | FALSE
3.2.1.3 | [10 empty] | FALSE | FALSE
3.2.1.4 | [10 empty] | FALSE | FALSE
3.2.1.5 | [10 empty] | FALSE | FALSE
3.2.2 | Review the ASHP Fan Schedule contained within the MEP drawings. Document any changes that have been made to the ASHP schedule since design, by identifying the manufacture, model, and power (wattage) of the new ASHP fan. | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
[11 empty] | FALSE | FALSE | Phius
3.2.3 | Provide Datasheet of ASHP pump manufacture and model that lists the Power (Watts) for fans associated with the Heating & Cooling system that are non-ducted or do not have energy efficiency data following AHRI Standard 1230. | [9 empty] | FALSE | FALSE | Phius
Notes:
3.3 | Heating/Cooling System - Pumps associated with the Ground Source or Hydronic System | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
3.3.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Manufacturer | Model# | Quantity | Pump Power
[5 empty] | Verified Flowrate (gal/min) | Head (ft) from Mechanical Schedule | Efficiency (%) from datasheet | Power Rating (Watts) | or | Power Rating (Watts) on pump nameplate
3.3.1.1 | [10 empty] | FALSE | FALSE | Phius
3.3.1.2 | [10 empty] | FALSE | FALSE
3.3.1.3 | [10 empty] | FALSE | FALSE
3.3.1.4 | [10 empty] | FALSE | FALSE
3.3.1.5 | [10 empty] | FALSE | FALSE
3.3.2 | Review the GSHP schedule contained within the MEP drawings. Document any changes that have been made to the GSHP schedule since design, by identifying the manufacture, model, and power (wattage) of the new pump. | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
[11 empty] | FALSE | FALSE | Phius
3.3.3 | Provide datasheet of GSHP pump manufacture and model that lists the Power (Watts), or Flow Rate and Head, for pumps associated with the Heating & Cooling system. | [9 empty] | FALSE | FALSE | Phius
Notes:
Footnotes:
1 Only one photo required per model number. Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."
2 If only Heating Wattage is given, enter the same value for Cooling as entered for Heating.

## 4-DHW
Phius NR Quality Assurance Workbook 4-Domestic Hot Water (DHW)
4 | DHW Water Heater | [11 empty] | Verifier Confirmed | n/a | PROG. REQ.
4.0.1 | Tag Name (aligned with Plumbing Schedule, e.g., WH-1) | Water Heater Type | Manufacturer |  | Model # | Quantity | Energy Star Certificate Uploaded?1 | Equipment & Nameplate Photos Uploaded?1
4.0.1.1 |  | [Select Dropdown] |  |  |  |  | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE | Phius
4.0.1.2 |  | [Select Dropdown] |  |  |  |  | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.0.1.3 |  | [Select Dropdown] |  |  |  |  | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.0.1.4 |  | [Select Dropdown] |  |  |  |  | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
Notes:
4.1 | DHW Storage Tank (if Applicable) | [11 empty] | Verifier Confirmed | n/a | PROG. REQ.
4.1.1 | Tag Name (aligned with Plumbing Schedule, e.g., WH-1) |  | Manufacturer |  | Model # | Quantity | Energy Star Certificate Uploaded?1 | Equipment & Nameplate Photos Uploaded?1
4.1.1.1 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE | Phius
4.1.1.2 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.1.1.3 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.1.1.4 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
Notes:
4.2 | DHW Swing Tank (if Applicable) | [11 empty] | Verifier Confirmed | n/a | PROG. REQ.
4.2.1 | Tag Name (aligned with Plumbing Schedule, e.g., WH-1) |  | Manufacturer |  | Model # | Quantity | Energy Star Certificate Uploaded?1 | Equipment & Nameplate Photos Uploaded?1
4.2.1.1 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE | Phius
4.2.1.2 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.2.1.3 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.2.1.4 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
Notes:
4.3 | DHW Pump (if Applicable) | [11 empty] | Verifier Confirmed | n/a | PROG. REQ.
4.3.1 | Tag Name (aligned with Plumbing Schedule, e.g., WH-1) | DHW Configuration | DHW Recirculation Types | Manufacturer | Model # | Quantity | Pump Power
[7 empty] | Verified Flow Rate (gal/min) | Head (ft) from Plumbing Schedule | Efficiency (%) from datasheet | Power Rating (Watts) | or | Power Rating (Watts) on pump nameplate
4.3.1.1 |  | [Select Dropdown] | [Select Dropdown] | [9 empty] | FALSE | FALSE | Phius
4.3.1.2 |  | [Select Dropdown] | [Select Dropdown] | [9 empty] | FALSE | FALSE
4.3.1.3 |  | [Select Dropdown] | [Select Dropdown] | [9 empty] | FALSE | FALSE
4.3.1.4 |  | [Select Dropdown] | [Select Dropdown] | [9 empty] | FALSE | FALSE
4.3.1.5 | Review the Pump Schedule contained within the MEP drawings. Document any changes that have been made to the pump schedule, by identifying the manufacture, model, and power (wattage) of the new pump. | [11 empty] | Verifier Confirmed | n/a | PROG. REQ.
[13 empty] | FALSE | FALSE | Phius
4.3.1.6 | Provide Datasheet of pump manufacture and model that lists the Power (Watts), or Flow Rate, Head, and Efficiency. | [11 empty] | FALSE | FALSE
Notes:
4.4 | DHW Delivery Verification | [11 empty] | Verifier Confirmed | n/a | PROG. REQ.
4.4.1 | Using the Field Verification method, no more than 2 gallons (7.6 liters) of water is collected from the furthest hot water fixture before hot water is delivered. Alternatively, once the water reaches 2 gallons (7.6 liters), the temperature of the water flow must increase by ≥ 10 °F in comparison of the final to the initial temperature reading. | [11 empty] | FALSE | FALSE | ENH
Notes:
4.5 | DHW Pipe insulation | [11 empty] | Verifer Confirmed | No
4.5.1 | Confirm DHW pipes are insulated. | [11 empty] | FALSE | FALSE | ENH
Notes:
Footnotes:
1Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."
2https://www.ahrinet.org/search-standards/ahri-1230-i-p-performance-rating-variable-refrigerant-flow-vrf-multi-split-air-conditioning-and-heat

## 5.1-Office Equip
Phius NR Quality Assurance Workbook 5.1-Appliances & Electrical Loads (Office Equipment)
Verify each office equipment has been installed by entering into Section 5.1.2 the office equipment the CPHC has listed in the Design Certification Feedback Form, and noting any changes, additions and deletions made between design and final installation into Section 5.1.1.
5.1.1 | Changes, Additions, and Deletions | [10 empty] | Verifier Confirmed | Prog Req.
Describe any changes, additions, or subtractions that were made to the manufacturer and model of the office equipment installed between design by the CPHC on the Design Certification Feedback Form and final installation.
5.1.1.1 | [11 empty] | FALSE | Phius
5.1.2 | Office Equipment | [10 empty] | Verifier Confirmed | Prog Req.
| Name | Type | Manufacturer | Model # | Quantity (Indicate "0" if not yet installed)1 | Within the Thermal Envelope? | Power Rating (Watts)2 | Power Rating in Saving/Sleep Mode (Watts) | Utilization hours per year (hrs/yr)3 | Energy Star Certificate, Manufacturer's Technical Datasheet, or Submittal Uploaded?4 | Equipment & Nameplate Photos Uploaded?4
5.1.2.1 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE | Phius
5.1.2.2 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.3 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.4 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.5 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.6 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.7 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.8 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.9 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.10 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.11 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.12 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.13 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.14 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.2.15 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.1.16 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.1.17 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.1.18 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.1.19 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
5.1.1.20 |  | [Select Dropdown] |  |  |  | [Select Dropdown] |  |  | no input needed | [Select Dropdown] | [Select Dropdown] | FALSE
Notes:
Footnotes:
1If office equipment was not installed during Verifiers final visit, please provide purchase list of office equipment.
2Power Rating can be found on the equipment nameplate or in the user manual. Enter the highest power rating listed when a range is given.
3From 1.4.4.9 and Appendix I-3.11 ASHRAE Fundamentals 2017 Non-Residential Equipment Tables, Phius 2024 Passive Building Standards Certification Guidebook, v25.1.0 September 2025.
4Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."

## 5.2-Kitchen
Phius NR Quality Assurance Workbook 5.2-Appliances & Electrical Loads (Kitchen Equipment)
Verify each major kitchen equipment has been installed by entering into Section 5.2.2 the kitchen equipment the CPHC has listed in the Design Certification Feedback Form, and noting any changes, additions and deletions made between design and final installation in Section 5.2.1.
5.2.1 | Changes, Additions, and Deletions | [13 empty] | Verifier Confirmed | Prog Req.
5.2.1.1 | Describe any changes, additions, and deletions that were made to the type of major kitchen equipment (appliances that use more than 0.5 kWh/day or 182 kWh/yr) installed between design by the CPHC on the Design Certification Feedback form and final installation.
[15 empty] | FALSE | Phius
5.2.2 | Major Kitchen Equipment1 | [13 empty] | Verifier Confirmed | Prog Req.
| Type | Manufacturer | Model # | Location | Quantity | Energy Use (kWh/yr) | Energy Use (kWh/day) | # Occupants served by this appliance | # Meals / Utilization Day2 | # days utilized per year (days/yr)2 | Fuel type | Within the Thermal Envelope? | Equipment & Nameplate Photos Uploaded?3 | Energy Star Certificate Uploaded?3
5.2.2.1 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE | ENH & Phius
5.2.2.2 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.3 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.4 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.5 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.6 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.1 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.2 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.3 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.4 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.5 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.6 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.1 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.2 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.3 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.4 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.5 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.6 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.2.2.6 | [Select Dropdown] | [9 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
Notes:
Footnotes:
1Any kitchen equipment that has an electrical load of more than 0.5 kWh/day or 182 kWh/yr.
21.4.4.9 Non-Residential Internal Loads / Occupancy, Phius 2024 Passive Building Standards Certification Guidebook v25.1.0 September, 2025.
3Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."

## 5.3-Lighting
Phius NR Quality Assurance Workbook 5.3-Appliances & Electrical Loads (Lighting Loads)
Verify lighting listed by the CPHC in the Design Certification Feedback Form, by noting any changes, additions and deletions made between design and final installation into Section 5.3.1.1.
5.3.1 | Changes, Additions, Deletions | Verifier Confirmed | Prog Req.
5.3.1.1 | Space use type affects lighting load. In the space below, describe if any of the space types in the Architectural plans changed uses following Design Certification (e.g. rooms were combined to create a breakroom, an office became a classroom, etc.). In the project folder include a marked-up copy of reflected ceiling plan, if appropriate.
|  | [Select Dropdown] | Phius
5.3.2 | Lighting Power Density | Verifier Confirmed | Prog Req.
5.3.2.1 | Phius Non-Res Lighting Calculator_v26.1.0.has been completed and uploaded into folder: 4. On-Site Verification / 3. Photos / Lighting (https://www.phius.org/phius-non-residential-lighting-calculator) | FALSE | Phius
Notes:

## 5.4-Process Loads
Phius NR Quality Assurance Workbook 5.4-Appliances & Electrical Loads (Process Loads)1
Verify each process load has been installed by entering into Section 5.4.2 the process load the CPHC has listed in the Design Certification Feedback Form, and noting any changes, additions and deletions made between design and final installation in Section 5.4.1.
5.4.1 | Changes, Additions, and Deletions | [7 empty] | Verifier Confirmed | Prog Req.
5.4.2.1 | Describe any changes, additions, and deletions that were made to the name, make, model, quantity or total energy use (kWh/yr) of a process load between design by the CPHC on the Design Certification Feedback form and final installation.
[9 empty] | FALSE | Phius
5.4.2 | Process Loads1 | [7 empty] | Verifier Confirmed | Prog Req.
5.4.2.1 | Name | Manufacturer | Model # | Quantity | kWh/yr | Within the Thermal Envelope? | Energy Star Certificate, Manufacturer's Technical Datasheet, or Submittal Uploaded?2 | Equipment & Nameplate Photos Uploaded?2
5.4.2.1 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE | Phius
5.4.2.2 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.3 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.4 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.5 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.6 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.7 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.8 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.9 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.10 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.11 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.12 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.13 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.14 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.15 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.16 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.17 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.18 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.19 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.2.20 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | FALSE
5.4.3 | Pump Data | [7 empty] | Verifier Confirmed | Prog Req.
5.4.3.1 | Review the Pump Schedule contained within the MEP drawings. Document any changes that have been made to the pump schedule, by identifying the manufacture, model, and power (wattage) of the new pump.
[9 empty] | FALSE | Phius
5.4.3.2 | Provide Datasheet of pump manufacture and model that lists the Power (Watts), or Flow Rate and Head, for pumps or fans associated with the process load.2 | [7 empty] | FALSE
Notes:
Footnotes:
1A process load is energy consumed in support of a manufacturing, industrial, or commercial process other than conditioning spaces and maintaining comfort and amenities for the occupants of a building. Alternatively, a process load is a service provided to a customer or client in the building. Whether it is the customer or client using the energy (e.g. arcade, training center) or if the energy is used on their behalf (e.g. commercial kitchen in a restaurant), both situations may qualify as process loads.
2Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."

## 6-Renewables & Electrification
Phius NR Quality Assurance Workbook 6-Renewables & Electrification
6 | Renewable Energy Systems | [7 empty] | Array Photos Uploaded?1 | Verifier Confirmed | N/A | PROG. REQ.
6.0.1 | Solar thermal system installed? |  | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Manufacturer and Model: |  | [Select Dropdown] | FALSE | FALSE | N/A
6.0.2 | Solar photovoltaic system installed? | [8 empty] | FALSE | FALSE | N/A
| A | Array 1 | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Peak production (W): |  | [Select Dropdown] | FALSE |  | N/A
| B | Array 2 | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Peak production (W): |  | [Select Dropdown] | FALSE
| C | Array 3 | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Peak production (W): |  | [Select Dropdown] | FALSE
| D | Array 4 | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Peak production (W): |  | [Select Dropdown] | FALSE
Verifier Notes:
6.1 | Electric Vehicle (EV) Charging Infrastructure2 (For parking spaces serving the non-residential building or the non-residential part of the mixed-use building) | [8 empty] | Verifier Confirmed | N/A | PROG. REQ.
6.1.1 | Total number of parking spaces provided: | [8 empty] | FALSE | FALSE | Phius
6.1.2 | EV capability installed in compliance with the International Code Council’s “Electric Vehicles and Building Codes: A Strategy for Greenhouse Gas reductions” (2021), Table 1: Sample EV-Integrated Code Provisions following the Commercial column, if the Phius project occurs in one of the municipalities listed: https://iccsafe.org/wp-content/uploads/21-20604_COMM_EV_Strategy_RPT_v5.pdf | [7 empty] | % of Parking | FALSE | FALSE | Phius
6.1.2.1 | A | Total number of EV-Capable spaces provided: | [6 empty] | - | FALSE | FALSE
6.1.2.2 | B | Total number of EV-Ready spaces provided: | [6 empty] | - | FALSE | FALSE
6.1.2.3 | C | Total number of Electric Vehicle Supply Equipment (EVSE)3 spaces provided: | [6 empty] | - | FALSE | FALSE
6.1.2.4 | D | Total number of EV-Capable, EV-Ready, and EVSE spaces provided: | [5 empty] | - | - | FALSE | FALSE
6.1.3 | For Phius projects that occur in municipalities not listed in the above Table 1: | [7 empty] | % of Parking | ≥10% of total parking spaces |  | PROG. REQ.
6.1.3.1 | A | Total number of EV-Ready spaces provided: | [6 empty] | - | - |  | Phius
6.1.3.2 | B | Total number of Electric Vehicle Supply Equipment (EVSE) spaces provided: | [6 empty] | - | -
6.1.3.2 | C | Total number of EV-Ready and EVSE spaces provided: | [5 empty] | - | - | -
Notes:
#REF!
1
#REF!
Footnotes:
1Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."
2Phius equates the term ‘dwelling unit’ also applies to ‘sleeping units’.
3EVSE = EVSE Installed = EV-Installed.

## Update Page
Workbook updates:
v1.1 - 2/3/17: Updated kitchen exhaust criteria, spelling updates, added solar/renewable ready criteria.
v2.2 - 2/9/19: Updated for PHIUS+ 2018 Standards, Footnote (2)
v2.3 - 2/20/2020: Updated for EPA Energy Star MFNCP
v2.3 - 7-20-2021: Updates for current RESNET Standards and Energy Star MFNCP
v2.3 - 01-06-2022: Various wording and formatting updates
v2.3 - 09-26-2022: Alignment with Phius 2021. Electrification Readiness, Electric Vehicle Readiness Requirements, Re-organized Building Envelope, Heat+Cool, and Ventilation tabs, DHW temperature rise sampling table added.
v2.3.1 - 01-26-2023: Updates to the 'Ventilation'. Corrections made to 'pass' and 'fail' criteria for ventilation rates on individual rooms.
v2.3.2 - 04-17-2023: Updates to the 'Ventilation'. Corrections made to 'pass' and 'fail' criteria for Bedroom Pressure Difference inputs. Also updated 'pass' and 'fail' criteria for Heat + Cool for ducted systems.
v2.3.3 - 05-16-2023: Updated formulas for the preliminary blower door test on the 'Building Envelope' tab.
3.0.1 (3-4-14)
1) Ventilation - cells AB42, AC42, AB51, AC51 - added formula to sum the individual branch measurements for reference only
2) Ventilation - cell AF2 - added comment describing the "in balance" specification (+/-20% or 5cfm, whichever is greater)
3) DHW+Lights+Appliances - added item #3 for DHW model #, AHRI certificate and photo
4) Renewable Energy Ready - For item #1, updated the PV Watts hyperlink to the new PV Watts site…and added screen shot examples over to the right from PV Watts
5) Heating-Cooling: added note to item 1 "HVAC installer is required to be an accredited installer approved by Energy Star (for example, ACCA) if the heating or cooling system is a split air conditioner, unitary (packaged outside) air conditioner, air-source heat pump, water/ground source ("geothermal") heat pump up to 65,000Btu/hr with a ducted distribution system or a furnace up to 225,000Btu/hr with a ducted distribution system. All other permutations of equipment (e.g. boilers, mini-split / multi-split systems) and distribution systems are exempt."
3.0.2 (3-13-14)
1) Added more footnotes to Building Envelope 6.2 and 6.3
4.0.2 (5/18/17)
1) Totally revamped workbook to reflect newest ENERGY STAR, IAP and ZERH requirements
4.0 (8/10/17)
1) Requirement to supply fresh air to all bedrooms
2) Revised the previous 10' requirement for 'stretched string' distance between exhaust/supply ports on exterior of building. Now, recommend 10', requirement is a minimum 5' separation but must follow manufacturer's recommendations.
4.1 (1/2019)
1) Updated entire workbook to coincide with PHIUS 2018 Standard; Energy Star V3.1, Rev09; Indoor AirPLUS v1, Rev04 & DOE ZERH Requirements
4.2 (7/2021)
1) Updated to add Electric Vehicle Readiness Checklist items
2) Updated to add Electrification Readiness Checklist items
3) Updated to Phius Certified Rater/Verifier from PHIUS+ Rater/Verifier
4) Updated to align with ENERGY STAR v3.1 (Rev11)
5) Aligned Ventilation tab limits with those outlined in the Guidebook in terms of tolerance and allowed difference in measured vs planned ventilation rates
4.2.1 (5/2023)
1) Revised Intro page layout
2) Revised Building Envelope section for blower door testing inputs
3) Added ability to include multiple ventilation systems and aligned tab limits with those outlined in the guidebook.
24.1.0 (7/2024)
Removed co-requisite requirements, where possible, to streamline the Workbook.
24.1 (8/2024)
1) Updated entire Workbook to coincide with Phius 2024 Standard; Energy Star MFNC v3.2, Indoor AirPLUS v1, REV04 & DOE ZERH Multifamily Version 2 Requirements
26.1 (5/2026)
| 1 | Tab 0 - Key documents. Added 0.1.3.1 If Multifamily, provide Whole Building Blower Door Testing Plan. 0.1.3.1 was made a Phius requirement.
| 2 | Tab 0 - Key documents. Added "For duplexes and townhomes" to 0.3.3 For duplexes and townhomes: Provide Energy Star SFNH National HVAC Commissioning Checklist, Version 3 / 3.1 / 3.2 (Rev. 13), and all items under line 4, "Air Balancing of Supply Registers & Return Grilles," are required.
| 3 | Tab 0 - Key documents. Deleted 0.3.4 If Energy Star Multifamily New Construction (MFNC): All items under Line 4, "Air Balancing of Supply Registers & Return Grilles," of the National HVAC Functional Testing Checklist, Version 1 / 1.1 / 1.2 (Rev. 04) are required.
| 4 | Tab 0 - Key documents. At all occurrences changed from, “Save photos in Section 4 of the Phius On-Site QA folder” to “Save photos into project folder: 4. PHIUS+ On-Site Verification.
| 5 | Tabs 2.1, 2.2, and 2.3 - Ventilation. Room type for exhaust airflow changed from "1/2 bath" to "Half-Bath, Toilet, Powder."
| 6 | Tabs 2.1, 2.2, and 2.3 - Ventilation. Equation for >= Minimum was corrected to remove equation to reference cells that were removed during the 24.1 update
| 7 | Tabs 2.1, 2.2, and 2.3 - Ventilation. The equation for" Within +5 cfm or + 20%" was changed to correct the multiple from 1.25 (25%) to 1.20 (20%).
| 8 | Tabs 2.1, 2.2, and 2.3 - Ventilation. The heading "Minimum" was changed for clarity to read ">= Minimum cfm (bath 20; kitchen 25).
| 9 | Tabs 2.1, 2.2, and 2.3 - Ventilation. A section for Ventilation Unit Total Airflow Rates (24/7) was inserted at sections 2.2.14, 2.2.15, and 2.3.13 at Tabs 2.1, 2.2, and 2.3. Each subsequent section was renumbered, correspondingly.
| 10 | Tab 3 Heating & Cooling - Added Footnote: Only one photo required per model number.
| 11 | Tab 5 - Appliances & Electrical Loads. 5.08 Range hoods. Added column: If Direct Exhaust Measured Exhaust Airflow at median cfm
| 12 | All tabs - changed references to DOE Zero Energy Home program (ZERH) to DOE Efficient New Homes program, and changed all acronyms from ZERH to DOE.
| 13 | Cover Sheet - Changed the Tab Names in the table "Responsible parties from completion" to include shortened descriptions.
| 14 | All Tabs - changed the tab name to a shortened description to match what was shown on Cover Sheet.
| 15 | Cover Sheet - added a naming convention under which files could be saved.
| 16 | Coversheet - added a dropdown to distinguish if project was reviewed by a Verifier with MF designation, or a Rater.
| 17 | Entire Workbook-changed color scheme to align with Phius standard colors
| 18 | Cover Sheet - Co-requisite Programs - added "compliance" option for non-US projects
| 19 | Cover sheet - changed the order and moved paragraph "Using This Workbook" in front of paragraph "Certification Criteria"
| 20 | Cover Sheet - clarified definition of a Non-Residential building.
| 21 | Key Docs - Building Envelope. Combined 0.1.1.1 and 0.1.1.2 to: "Provide technical datasheets of any insulation type installed that was not uploaded to folder:"
| 22 | Key Docs - Building Envelope. Added requirement, "Provide Whole Building Blower Door Testing Plan if building is a duplex or townhouse."
| 23 | Key Docs - Removed all references to Multifamily projects to the MF QA Workbook.
| 24 | Key Docs - Added requirement to provide reflected ceiling plans if using custom lighting power densities.
| 25 | Cover Sheet - Added option to select "Performance" or "Prescriptive", depending on the Certification Path chosen.
| 26 | AirTight WB - Added option to connected to the CoverSheet, so when Performance Path is selected, the airtightness standard in 0.06 cfm50/ft2, and 0.04 cfm50/ft2 when Prescriptive Path is selected.
| 27 | Removed references to "taped" and "untaped" tests, and replaced these terms with "Durability" and "Operational", respectively.
| 28 | Vent ERV_HRV - Changed the format of this page to group all supply airflows and all exhaust airflows, and moved all Auxiliary supply only or exhaust only airflows to a separate tab, 2.2.
| 29 | Vent ERV_HRV - Added section for dehumidifier, if applicable.
| 30 | Vent ERV_HRV - Moved direct exhaust range fans from the Appliances & Electrical Loads tab to the Vent ERV_HRV tab.
| 31 | Vent Auxiliary - added option for make-up air supply or exhaust fan only as dropdown options.
| 32 | Heat & Cool - Divided worksheet into section for outdoor component and another section for indoor component, and added sections for ASHP fans and GSHP pumps.
| 33 | DHW - Added sections for DHW Storage Tank, DHW Swing Tank, DHW Delivery Verification, and DHW Pipe Insulation
| 34 | Appliances & Electrical Loads - Revised Page Layout. Range hood and Dehumidifier moved to Vent ERV_HRV tab.
| 35 | Renewables & Electrification - Added Photo confirmation for each Solar PV array.
| 36 | Renewables & Electrification - Removed Section 6.03 HERS® Index, as this section only applies to whole dwelling, single-family projects.
| 37 | Added header on each Worksheet as a legend to show: "required input cells", "select best option", "notes/Instructions", and "calculations"
| 38 | AirTight Comp - Compartmentalization tab added for testing sleeping units in hotels and motels.
| 39 | Ventliation Tabs: Centralized, Decentralized Dwelling Unit, Decentralized Common were combined as dropdown selections within tab Vent ERV_HRV.
| 40 | Appliances & Electrical Loads - Segregated into 4 tabs (Office Equip, Kitchen, 5.3 Lighting, 5.4 Process loads) to parallel entries in WUFI Passive.

## Dropdown menus (hidden)
Cover Sheet |  |  | 1-Building Envelope (WB) | 1.2-Building Envelope (Comp) | 2.1-Vent ERV_HRV | 2.2-Vent Exhaust Only | 3-Heating & Cooling | 4-Domestic Hot Water | 5.1-Appliances & Electrical (Office) | 5.2-Appliances & Electrical (Kitchen) | 5.3-Appliances & Electrical (Lighting) | 5.4-Appliances & Electrical (Process Load) | 6-Renewables & Electrification
Country | State | Project Path | Building Height | Verifier Confirmation | ERV/HRV Types | Room Type | Heating/Cooling System Type | Hot Water System Type | Office Equipment Type | Within the Thermal Envelope | Verifier Confirmed? | Within the Thermal Envelope | Solar Thermal Installed
[Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown]
United States | AK Alaska | Performance | Yes | Yes | Centralized - Common Spaces Only | Kitchen | air source heat pump | none | PC | Yes | Yes | Yes | Yes
Canada | AL Alabama | Prescriptive | No | No | Centralized - Sleeping Units Only | Other | water source heat pump | HPWH (inside) | Monitor | No | N/A | No | No
Mexico | AR Arkansas |  |  | N/A | Centralized - Common Spaces & Sleeping Units |  | ground source heat pump | HPWH (outside) | Copier
Afghanistan | AS American Samoa | Certification Path |  |  | Decentralized - Common Spaces Only |  | fan coil | Electric (tanked) | Printer
Albania | AZ Arizona | [Select Dropdown] | Durability Test | Indoor AirPlus Version | Decentralized - Sleeping Units Only | Air Flow Type | furnace | Electric (tankless) | Server | Equipment Photos Uploaded | 90% Florescent or LED | Energy Star Certificate Uploaded | Solar Photovoltaic Installed
Andorra | CA California | Phius CORE 2021 | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | hydronic | Gas (tanked) | Telephone System | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown]
Angola | CT Connecticut | Phius CORE 2024 | Yes | IAP V2 Certified |  | Continuous |  | Gas (tankless) | User Defined | Yes | PASS | Yes | Yes
Argentina | DC District of Columbia | Phius ZERO 2021 | No | IAP V2 Gold |  | Intermittent | Ducted/Non-Ducted |  |  | N/A | FAIL | N/A | N/A
Armenia | DE Delaware | Phius ZERO 2024 |  | N/A | Vent System Type |  | [Select Dropdown]
Australia | FL Florida |  |  |  | [Select Dropdown] |  | Ducted | Energy Star Certificate Uploaded | Within the Thermal Envelope
Azerbaijan | GA Georgia |  |  |  | HRV | Conditioned Space? | Non-Ducted | [Select Dropdown] | [Select Dropdown] |  | Lighting Power Density | Equipment Photos Uploaded | Photos Uploaded
Bahamas, The | HI Hawaii | Rater or Verifier |  |  | ERV | [Select Dropdown] | Mixed Ducted & Non-Ducted | Yes | Yes | Energy Star Certificate Uploaded | [Select Dropdown] | [Select Dropdown] | [Select Dropdown]
Bahrain | IA Iowa | [Select Dropdown] |  |  | Integrated | Yes |  | N/A | No | [Select Dropdown] | PASS | Yes | Yes
Bangladesh | ID Idaho | Verifier |  |  |  | No |  |  |  | Yes | FAIL | N/A | N/A
Barbados | IL Illinois | Rater (Verifier >200 mi) |  |  |  |  | Individual/Shared |  |  | N/A | N/A
Belgium | IN Indiana |  |  |  | ERV/HRV Defrost |  | [Select Dropdown] | Photos Uploaded | Energy Star Certificate Uploaded
Benin | KS Kansas |  |  |  | [Select Dropdown] | Exhaust Hood Type | Individual | [Select Dropdown] | [Select Dropdown]
Bhutan | KY Kentucky | Confirm Recent Drawings |  |  | n/a | [Select Dropdown] | Shared | Yes | Yes | Cooktop Fuel Type
Bolivia | LA Louisiana | [Select Dropdown] |  |  | Electric | Direct Exhaust |  | N/A | N/A | [Select Dropdown]
Bosnia & Herzegovina | MA Massachusetts | Yes |  |  | Hot Water Loop | Recirculation |  |  |  | Electric Induction
Botswana | MD Maryland | N/A |  |  | Ground Loop |  | AHRI Certificate Uploaded? |  |  | Electric Resistance
Brunei | MI Michigan |  |  |  | Earth Tube |  | [Select Dropdown] | DHW Configuration | Photos Uploaded | Gas
Bulgaria | MN Minnesota |  |  |  | Recirculation | Equipment & Nameplate Photos Uploaded? | Yes | [Select Dropdown] | [Select Dropdown]
Burkina Faso | MO Missouri |  |  |  |  | [Select Dropdown] | N/A | Centralized | Yes
Burma | MS Mississippi |  |  |  |  | Yes |  | Decentralized | N/A | Type of Kitchen Equipment
Burundi | MT Montana |  |  |  | Airflows measured by: | N/A |  |  |  | [Select Dropdown]
Cambodia | NC North Carolina |  |  |  | [Select Dropdown] |  | Photos Uploaded? |  |  | Refrigerator/Freezer
Cameroon | ND North Dakota |  |  |  | Verfifier |  | [Select Dropdown] | DHW Recirculation Types |  | Dishwasher
Cape Verde | NE Nebraska |  |  |  | TAB Contractor, Verifier Observed | Auxiliary Supply Ventilation System Type | Yes | [Select Dropdown] |  | Cooktop/Range
Cayman Islands | NH New Hampshire |  |  |  |  | [Select Dropdown] | N/A | None |  | Other
Central African Rep. | NJ New Jersey |  |  |  |  | Supply: Make-up Air |  | Continuous
Chad | NM New Mexico |  |  |  | Project team has demonstrated the ground loop / earth tube control logic is set up properly. | Supply: Miscellanous |  | Time based only
Chile | NV Nevada |  |  |  | [Select Dropdown] | Exhaust: Trash Room |  | Temperature based only
China | NY New York |  |  |  | Yes | Exhaust: Compactor Room |  | Temperature & Time based
Colombia | OH Ohio |  |  |  | N/A | Exhaust: Computer Room |  | On Demand (adaptive/smart, occupancy sensor or occupant control)
Comoros | OK Oklahoma |  |  |  |  | Exhaust: Elevator Machine Room
Congo, Dem. Rep. | OR Oregon |  |  |  |  | Other
Congo, Repub. of the | PA Pennsylvania |  |  |  | Equipment & Nameplate Photos Uploaded? |  |  | Tube Size (inches)
Cook Islands | PR Puerto Rico |  |  |  | [Select Dropdown] |  |  | [Select Dropdown]
Costa Rica | RI Rhode Island |  |  |  | Yes |  |  | < 1.5 inches
Cote d'Ivoire | SC South Carolina |  |  |  | N/A |  |  | ≥ 1.5 inches
Croatia | SD South Dakota
Cuba | TN Tennessee
Cyprus | TX Texas | [6 empty] | Insulation Thickness
Czech Republic | UT Utah | [6 empty] | [Select Dropdown]
Denmark | VA Virginia | [6 empty] | 1.5" (or R-10 minimum)
Djibouti | VT Vermont | [6 empty] | 2.0" (or R-12 minimum)
Dominica | WA Washington
Dominican Republic | WI Wisconsin
East Timor | WV West Virginia
Ecuador | WY Wyoming
Egypt
El Salvador | AB Alberta
Equatorial Guinea | BC British Columbia
Eritrea | MB Manitoba
Estonia | NB New Brunswick
Ethiopia | NF Newfoundland
Faroe Islands | NT Northwest Territories
Fiji | NU Nunavut
Finland | NS Nova Scotia
France | ON Ontario
French Guiana | PE Prince Edward Island
French Polynesia | QC Quebec
Gabon | SK Saskatchewan
Gambia, The | YT Yukon
Gaza Strip
Georgia
Germany
Ghana
Gibraltar
Greece
Greenland
Grenada
Guadeloupe
Guam
Guatemala
Guernsey
Guinea
Guinea-Bissau
Guyana
Haiti
Honduras
Hong Kong
Hungary
Iceland
India
Indonesia
Iran
Iraq
Ireland
Isle of Man
Israel
Italy
Jamaica
Japan
Jersey
Jordan
Kazakhstan
Kenya
Kiribati
Korea, North
Korea, South
Kuwait
Kyrgyzstan
Laos
Latvia
Lebanon
Lesotho
Liberia
Libya
Liechtenstein
Lithuania
Luxembourg
Macau
Macedonia
Madagascar
Malawi
Malaysia
Maldives
Mali
Malta
Marshall Islands
Martinique
Mauritania
Mauritius
Mayotte
Micronesia, Fed. St.
Moldova
Monaco
Mongolia
Montserrat
Morocco
Mozambique
Namibia
Nauru
Nepal
Netherlands
Netherlands Antilles
New Caledonia
New Zealand
Nicaragua
Niger
Nigeria
N. Mariana Islands
Norway
Oman
Pakistan
Palau
Panama
Papua New Guinea
Paraguay
Peru
Philippines
Poland
Portugal
Puerto Rico
Qatar
Reunion
Romania
Russia
Rwanda
Saint Helena
Saint Kitts & Nevis
Saint Lucia
St Pierre & Miquelon
Saint Vincent and the Grenadines
Samoa
San Marino
Sao Tome & Principe
Saudi Arabia
Senegal
Serbia
Seychelles
Sierra Leone
Singapore
Slovakia
Slovenia
Solomon Islands
Somalia
South Africa
Spain
Sri Lanka
Sudan
Suriname
Swaziland
Sweden
Switzerland
Syria
Taiwan
Tajikistan
Tanzania
Thailand
Togo
Tonga
Trinidad & Tobago
Tunisia
Turkey
Turkmenistan
Turks & Caicos Is
Tuvalu
Uganda
Ukraine
United Arab Emirates
United Kingdom
Uzbekistan
Vanuatu
Venezuela
Vietnam
Virgin Islands
Wallis and Futuna
West Bank
Western Sahara
Yemen
Zambia
Zimbabwe

## Templates (hidden)
Data entry cells are in blue. Checkbox cells are in teal and white. Notes cells are in light gray. Calculation cells are in lime. Do not change the calculation cells!
|  | Required input cells | Select best option | Notes / Instructions / Units | Calculations (do not change)
[Select Dropdown]
[Select Dropdown]
Conditional Formatting:
|  | #E5B8B7 |  | Fail
|  | #C2D69B |  | Pass
Ventilation Tab:
|  | #3D65A5 |  | Supply | https://www.datylon.com/blog/data-visualization-for-colorblind-readers#color-blind-palette
|  | #F05039 |  | Exhaust | https://www.datylon.com/blog/data-visualization-for-colorblind-readers#color-blind-palette