## Cover Sheet
Phius Quality Assurance Workbook for Multifamily Projects* - v26.2.0 (July 2026)
*For projects with multiple buildings, please create a Workbook for each building of the project.
Project Information
Project Name | Phius Project Number | Building Permit Date | Number of Stories | Total # Dwelling Units | Country
[Select Dropdown]
Street Address | City |  | State/Province | Zip Code | Phius Project Path | Phius Project Certification Standard
|  |  | [Select Dropdown] |  | Performance | [Select Dropdown]
Please save the Multifamily QA Workbook using the following naming convention: (#### is the Phius Project Number) |  |  |  |  | ####_MF QA Workbook_YYYY.MM.DD
Project Team | Company Name |  |  |  | Contact Name
Phius Certified Verifier (MF)1 or Rater (Townhouse only): |  |  |  |  | [Select Dropdown]
Phius Certified Consultant (CPHC):
Architect:
General Contractor / Builder: |  |  | DOE ZERH Builder ID#:
Mechanical Systems Designer:
HVAC Contractor:
Functional Testing Agent (FTA):
Building Owner:
Ducted heating/cooling systems in dwelling units: |  |  | [Select Dropdown]
HVAC Contractor must be H-QUITO / ESTAR Credentialed: |  |  | Pending input from cell F22
Functional Testing Agent (FTA) is qualified per: |  |  | [Select Dropdown]
CO-REQUISITE PROGRAM ELIGIBILITY2,3,4,5 |  |  |  | CO-REQUISITE PROGRAM VERSION2,3,4,5
Select the applicable eligibility based on the Phius Certification Guidebook Section 1.5.3 Program Eligibility Criteria |  |  |  | Input the applicable program version based on the project permit date and its geographic location based on co-requisite program guidelines.
Program | Program Eligibility |  |  | Program |  | Program Version & Revision Number
DOE ENERGY STAR Multifamily New Construction | Certification required in the US Compliance required for non-US |  |  | DOE ENERGY STAR Multifamily New Construction |  | [Select Dropdown]
EPA Indoor AirPlus | Certification required in the US Compliance required for non-US |  |  | EPA Indoor AirPlus |  | [Select Dropdown]
DOE Efficient New Homes Multifamily5 | Compliance required in the US Compliance required for non-US |  |  | DOE Efficient New Homes Multifamily |  | [Select Dropdown]
Welcome to the Phius Quality Assurance Workbook for Multifamily projects!
Using This Workbook This workbook shall be used by a Phius certified Verifier with Multifamily Designation for all multifamily projects, regardless of size. Multifamily projects are defined as anything residential other than "single-family" or "duplex" or "townhouse" and include residential or commercial dormitories, and the residential part of a mixed-use building.
Certification Criteria The Phius Certification process for multifamily projects includes energy modeling and design consulting performed by a Phius Certified Consultant (CPHC) to demonstrate compliance with Phius program energy performance metrics, as well as on-site verification of all critical project energy features by a Phius Certified Verifier. Projects within the United States must be certified under the DOE ENERGY STAR Multifamily New Construction (MFNC) and EPA Indoor AirPlus (IAP), and in compliance with DOE Efficient New Homes (ENH) Multifamily programs.6,7 Projects located outside of the United States must complete certification checklists for DOE ENERGY STAR Multifamily New Construction (MFNC) and EPA Indoor AirPlus (IAP), and in compliance with DOE Efficient New Homes (ENH) Multifamily programs. For full program requirements, please see the Phius Certification Guidebook (https://www.phius.org/phius-certification-guidebook).
There are eight (8) worksheets to complete (see the tabs below).
Responsible parties for completing each tab:
0-Key Documents (Key Docs) |  |  |  | Phius Certified Verifier (MF)
1.1-Building Envelope Air Tightness Testing Whole Building (AirTight WB)
2.1-Ventilation Systems ERV/HRV (Vent ERV_HRV)
2.2-Ventilation Auxiliary Supply & Exhaust Only (Vent Auxiliary)
3-Heating & Cooling (Heat & Cool) |  |  |  | HVAC Designer/Contractor, Phius Certified Verifier (MF)
4-Domestic Hot Water (DHW) |  |  |  | Phius Certified Verifier (MF)
5 - Appliances & Electrical Loads
6 - Renewables & Electrification
Phius Certified Verifiers are welcome to add their own custom sheets to this workbook for instance, to track project notes.
Questions regarding particular checklist items should be directed first to the Phius Verifier for the project. - Contact the Phius QA/QC Manager at QA@phius.org for questions on the nuances between certifying an entire building under Phius and certifying individual dwelling units within such buildings under Energy Star / DOE Efficient New Homes. - Contact https://www.phius.org/help for questions regarding the certification process for any project.
Footnotes:
1 A Verifier must have a Multifamily Designation identifier (MF) to become qualified to verify multifamily buildings.
2Projects located outside of the United States, or in California or Alaska, will not be required to meet DOE ENERGY STAR, EPA Indoor AirPlus, and DOE Efficient New Homes certifications, regardless of their configuration.
3Multi-Family Projects with a Building Permit date after July 1st, 2021 will be required to meet the DOE ENERGY STAR Multi-Family New Construction Program Certification Criteria. For projects permitted prior to that date, ENERGY STAR Certification can be attained by using either ENERGY STAR Homes OR the ENERGY STAR MFNCP subject to implementation dates required by the DOE for their programs.
4See Phius 2024 Passive Building Standards Certification Guidebook v.25.1.0, Table 1.3.0 and Section 1.5.3 for additional Co-Requisite Program Requirements.
5Multifamily projects pursuing Phius Certification are no longer required to earn DOE Efficient New Homes Multifamily Version 2 certifications (https://www.phius.org/doe-efficient-new-homes-requirement-paused-multifamily-phius-projects).
6In this QA Workbook the following acronyms will be used as abbreviations for the co-requiste programs: DOE ENERGY STAR (ES), EPA Indoor AirPlus (IAP), DOE Efficient New Homes (ENH).
7In September 2025 DOE announced DOE Efficient New Homes is the successor program to DOE Zero Energy Ready Home. The Phius 2025.1.0 Guidebook refers to the DOE program as the Zero Energy Ready Home (ZERH) program, as the Guidebook was published before the successor program was announced.

## 0-Key Docs
Phius MF Quality Assurance Workbook 0-Key Documents1
0 | 0 - Certificates & Summaries / Co-requisite Programs | Rater Confirmed | N/A | PROG. REQ.
0.0.1 | Provide completed Phius Quality Control Field Checklist (v25.1.0, or newer). | FALSE | FALSE | Phius
0.0.2 | Provide DOE Energy Star Certificate2 or Home Report. | FALSE | FALSE | ES
0.0.3 | Provide EPA Indoor AirPlus Certificate.2 | FALSE | FALSE | IAP
0.0.4 | Provide Phius Annotated: DOE Efficient New Homes Multifamily National Rater Checklist.3 | FALSE | FALSE | ENH
0.0.5 | Provide Building Summary from HERS® Rating Software. | FALSE | FALSE | Phius
0.1 | 1 - Building Envelope | Rater Confirmed | N/A | PROG. REQ.
0.1.1 | Insulated Assemblies (Material & R-value verification)
0.1.1.1 | Provide technical datasheets1 of any insulation type installed that was not uploaded to folder: 2. Datasheets & Specifications / 4. Insulation. | FALSE | FALSE | Phius
0.1.2 | Windows & Doors
0.1.2.1 | If no photo of NFRC sticker is available, provide Window Purchase Order or Shop Drawings. | FALSE | FALSE | Phius
0.1.2.2 | Provide technical datasheets of any product that has been changed since Phius Design Review. | FALSE | FALSE | Phius
0.1.3 | Airtightness
0.1.3.1 | Provide Whole Building Blower Door Testing Plan if building is a multifamily or townhouse. | FALSE | FALSE | Phius
0.1.3.2 | Provide Final Operational (Untaped) Air Tightness Test Report (depressurization and pressurization), and Durability (Taped) Test if conducted, and list within the notes section of the blower door test results any items taped. All non-threatening items allowed for the taped test can be found at Section C-2.2 Non-Threatening Air Leakage, Phius 2024 Passive Building Standards Certification Guidebook v25.1.0. | FALSE | FALSE | Phius
0.1.3.3 | If Energy Star Multifamily New Construction (MFNC) Program: Provide Energy Star Multifamily Workbook. | FALSE | FALSE | Phius
0.2 | 2 - Ventilation | Rater Confirmed | N/A | PROG. REQ.
0.2.1 | If ventilation system is a Minotair, provide a completed Phius MINOTAIR PentaCare calculator. | FALSE | FALSE | Phius
0.2.2 | If Energy Star Multifamily New Construction (MFNC) Program: Provide Testing and Balancing (TAB) report of ducted ventilation system. | FALSE | FALSE | Phius
0.3 | 3 - Heating & Cooling | Rater Confirmed | N/A | PROG. REQ.
0.3.1 | Provide AHRI certificate and/or manufacturer's detailed specs of each installed heating and cooling system. | FALSE | FALSE | Phius
0.3.2 | Provide as-built Mechanical Drawings, if available, if changes were made since design certification was issued. | FALSE | FALSE | Phius
0.3.3 | For multifamily and townhouse: Provide Heating & Cooling Testing and Balancing report for ducted heating and/or cooling systems. | FALSE | FALSE | Phius
0.3.4 | For duplexes and townhouses: Provide Energy Star SFNH National HVAC Commissioning Checklist, Version 3 / 3.1 / 3.2 (Rev. 14 or newer), and all items under line 4, "Air Balancing of Supply Registers & Return Grilles," are required.4 | FALSE | FALSE | Phius
0.3.5 | All items under Line 4, "Air Balancing of Supply Registers & Return Grilles," of the Energy Star Multifamily New Construction National HVAC Functional Testing Checklist, Version 1.1 / 1.2 / 1.3 (Rev. 05 or newer) are required.5 | FALSE | FALSE | Phius
0.4 | 4 - Domestic Hot Water | Rater Confirmed | N/A | PROG. REQ.
0.4.1 | Provide Energy Star Certificate (https://www.energystar.gov/products) or AHRI Certificate for each installed DHW system. | FALSE | FALSE | Phius
0.5 | 5 - Appliances & Electrical Loads | Rater Confirmed | N/A | PROG. REQ.
0.5.1 | Provide Energy Star Certificate (https://www.energystar.gov/products) for each builder-installed appliance and dehumidifier. | FALSE | FALSE | Phius
0.5.2 | For all other appliances, provide equivalent documentation. | FALSE | FALSE | Phius
0.5.3 | Provide Reflected Ceiling Plans if using custom lighting power densities for common areas (rather than the defaults for common areas outlined in the Phius Guidebook). | FALSE | FALSE | Phius
0.6 | 6 - Renewables & Electrification | Rater Confirmed | N/A | PROG. REQ.
0.6.1 | Provide shop drawings or documentation that show the tilt, azimuth, and kW size of each installed PV system. | FALSE | FALSE | Phius
0.6.2 | Provide completed DOE Efficient New Homes Multifamily PV-Ready Checklist. | FALSE | FALSE | ENH
0.6.3 | Provide completed DOE Efficient New Homes Multifamily EV-Ready Checklist. | FALSE | FALSE | ENH
0.6.4 | Provide contract documents for any off-site renewable production that align with Appendix N-4.3 (Off-Site Renewable Energy Requirements) of the Phius 2024 Passive Building Standards Certification Guidebook v25.1.0. | FALSE | FALSE | Phius
Notes:
Footnotes:
1Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."
2For projects certifying under Phius 2024 use the version of the co-requisite program (or a newer version) required for Duplexes and Townhouses, or Multifamily listed within Table 1.3.0 of the Phius 2024 Passive Building Standards Certification Guidebook v25.1.0. For projects certifying under Phius 2021, 2018, and 2015 use the version of the co-requisite program (or a new version) specified within their corresponding Phius Guidebook.
3https://www.phius.org/sites/default/files/2026-03/Phius%20Annotated_%20DOE%20Efficient%20New%20Homes%20Multifamily%20National%20Rater%20Checklist.pdf
4SFNH National HVAC Commissioning Checklist: https://www.energystar.gov/partner-resources/residential-new/national-page.
5Energy Star Multifamily New Construction National HVAC Functional Testing Checklist: https://www.energystar.gov/partner-resources/residential-new/multifamily-national-page.

## 1-AirTight WB
Phius MF Quality Assurance Workbook 1-Building Envelope Airtightness Testing (Whole Building)
| 1.1 | Whole Building Airtightness Testing
| 1.1.1 | Blower Door Test Threshold Calculator1 |  | Building is 5+ stories in height & non-combustible construction? |  | [Select Dropdown]
Building Envelope Area (ft2)
|  |  |  | Project Threshold (CFM50/ft2) |  | Pending Input Cell L8
|  |  |  | Project Threshold (CFM50) |  | Pending Input Cells L9&L10
| 1.1.2 | Was a durability test performed during final blower door testing? (For more information on what is allowed on a durability test, see Phius Certification Guidebook 2025, Appendix C-2.3)2,3 |  | [Select Dropdown]
#REF! | 1.1.3 | Preliminary test: Preliminary whole building blower door test4 is: | Optional | Preliminary Test | (CFM50/ft2) | CFM50
Depressurization Test Result
Pressurization Test Result
Average Test Result
| 1.1.4 | Operational test: Final whole building blower door multi-point test4 is: | Mandatory | Final Test (Operational - mandatory) | (CFM50/ft2) | CFM50
Depressurization Test Result
Pressurization Test Result
Average Test Result
Criteria Passed?
| 1.1.5 | Operational test: please list those items taped
| 1.1.6 | Durability test: Final whole building blower door multi-point test4 is: | If necessary | Final Test (Durability - if necessary) | (CFM50/ft2) | CFM50
Depressurization Test Result
Pressurization Test Result
Average Test Result
|  |  |  | Criteria Passed? |  | Pending Input Cell L6
| 1.1.7 | Durability test: please list those items taped
Notes:
Footnotes:
1If testing at 75 Pa, use the Airtightness Pressure Conversion Calculator found in the Phius Resource Library to convert tested pressures from 75 Pa to 50 Pa, and enter into this page of the Workbook the values at 50 Pa.
2The Phius requirement of 0.06 cfm50/sqft (or 0.08 cfm50/sqft 5+ stories, non-combustible construction) must be met through a durability test. If an operational test result is less than 0.06 cfm50/sqft (or 0.08 cfm50/sqft 5+ stories, non-combustible construction), a durability test is not necessary.
3The result of the operational test is always input into the WUFI model. An operational test is always required.
4In accordance with ANSI/RESNET/ICC 380-2022 or latest version. NOTE: For Large MF or Non-Res. Bldgs- Alternative Test methods and building set up - per ABAA Standard Method for Building Enclosure Airtightness Compliance Testing, ASTM E-3158 or ASTM E-779.

## 2.1-Vent ERV_HRV
Phius MF Quality Assurance Workbook 2.1-Ventilation Systems (ERV/HRV)
This worksheet shall be completed for all E/HRV systems.
The airflow rates at the Ventilation Unit and at the individual registers shall be measured* at the design 24/7 ventilation rate.
The instructions for completing this tab can be found in the Phius Quality Control Field checklist, Section 2.1.7.
*Measured means either Verifier has measured or directly observed.
Ventilation System Installation & Airflow Testing Verification
2.1.1 | Measured at each Ventilation Unit | Measured at each Ventilation Unit at the design 24/7 Airflow Speed Setting
|  | ERV/HRV # or Tag # | Centralized or Decentralized | Location | System Type1 | Manufacturer | Model # | Merv Rating of Filter | Total Duct Insulation (R-value) |  | Type of ERV/HRV Defrost (External) | Design Airflow (cfm) |  | Airflows measured by: | Measured Airflow (cfm) |  | Measured Fan Power (Watts)2 | Equipment & Nameplate Photos Uploaded?3 | Electric Efficiency (W/cfm) | Measured Supply & Exhaust Airflow within 10%
[9 empty] | Supply | Exhaust |  | Supply | Exhaust |  | Supply | Exhaust
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
|  |  | [Select Dropdown] |  | [Select Dropdown] | [5 empty] | [Select Dropdown] |  |  | [Select Dropdown] |  |  |  | [Select Dropdown]
2.1.2 | Measured at each Register | Measured at Sampled Registers at the design 24/7 Airflow Speed Setting
|  | Supply Airflow (24/7) | Supply Register | [10 empty] | Supply Airflow |  |  | Pressure |  | Measured Airflow Status
|  |  | ERV/HRV # or Tag # | Space Tag # | Space Type | Register Location (Supply) | [5 empty] | Room Type |  | Airflows measured by | Design (cfm) | Measured (cfm) | Room Pressure Difference [Pa] |  | Within +/- 5cfm or +/- 20% of design | and | <1 Pa Pressure Difference (Bedroom)
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown] | [5 empty] | and
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter supply register location here (Classroom, Office, Corridor, Bedroom, etc.) | [5 empty] | [Select Room Type - Supply] |  | [Select Dropdown]
|  | Exhaust Airflow (24/7) | Exhaust Register | [10 empty] | Exhaust Airflow |  |  |  |  | Measured Airflow Status
|  |  | ERV/HRV # or Tag # | Space Tag # | Space Type | Register Location (Exhaust) | [5 empty] | Room Type |  | Airflows measured by | Design (cfm) | Measured (cfm) |  |  | Within +/- 5cfm or +/- 20% of design | and | ≥Minimum cfm (bath 20; kitchen 25)
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown] | [5 empty] | and
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
[5 empty] | [Select Dropdown] | enter exhaust register location here (Kitchen, Bath, Trash, Laundry, Storage, etc.) | [5 empty] | [Select Room Type - Exhaust] |  | [Select Dropdown]
Ventilator Defrost Systems - Subsoil Heat Exchanger (If Applicable)
2.1.3 | ERV/HRV # or Tag # served by Ventilator Defrost System | [8 empty] | Loop length (ft) |  | Approximate depth (ft) |  | Measured loop pump power (W) |  | Project team has demonstrated the ground loop / earth tube control logic is set up properly.
[Select Dropdown]
[Select Dropdown]
[Select Dropdown]
[Select Dropdown]
Ventilation Dehumidifier (If Applicable)
2.1.4 | ERV/HRV # or Tag # served by Dehumidifier | [8 empty] | Manufacturer |  | Model |  | Quantity | l/kWh | Equipment & Nameplate Photos Uploaded?2
[Select Dropdown]
[Select Dropdown]
[Select Dropdown]
[Select Dropdown]
Notes:
Footnotes:
1A CERV or Minotair is considered an Integrated System
2Please see Phius Guidebook Section 1.5.2.4 Ventilation, Power Consumption.
3Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."

## 2.2-Vent Auxiliary
Phius MF Quality Assurance Workbook 2.2-Ventilation Auxiliary Airflow Systems (Supply Only & Exhaust Only) (If Applicable)
The airflow rates shall be measured* as indicated below.
*Measure means either Verifier has measured or directly observed.
Range Hood
2.2.1 | Room Type | Airflow Type | Equipment Location | Manufacturer | Model # |  |  |  | Direct Exhaust or Recirculation | If Direct Exhaust Measured Exhaust Airflow (at Median cfm) | Equipment & Nameplate Photos Uploaded?1
| [Select Dropdown] | [Select Dropdown] | [6 empty] | [Select Dropdown] |  | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [6 empty] | [Select Dropdown] |  | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [6 empty] | [Select Dropdown] |  | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [6 empty] | [Select Dropdown] |  | [Select Dropdown]
Auxiliary - Ventilation Systems (if Applicable) (e.g., Make-up Air System, Trash Room, Compactor room, Computer Room, Elevator Machine Room, Auxiliary Exhaust Fan)
2.2.2 | System Type | Airflow Type | Equipment Location | Manufacturer | Model # | Power readings (from manufacturer nameplate) |  |  | Design Airflow (cfm) | Measured Airflow (at typical cfm)2 | Equipment & Nameplate Photos Uploaded?1
[6 empty] | Volts | Amps | Watts
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
| [Select Dropdown] | [Select Dropdown] | [8 empty] | [Select Dropdown]
Notes:
Footnotes:
1Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."
2The max airflow from manufacturer's datasheet will be used if the measured 24/7 airflow is not available.

## 3-Heat & Cool
Phius MF Quality Assurance Workbook 3-Heating & Cooling
3 | Heating/Cooling System - Outdoor Component | [9 empty] | Rater Confirmed | n/a | PROG. REQ.
3.0.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Manufacturer | Model# | Quantity | MERV Rating of Filter | Heating/Cooling System Type | Ducted or Non-Ducted? |  | AHRI Certificate Uploaded?1 | Equipment & Nameplate Photos Uploaded?1
3.0.1.1 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE | Phius
3.0.1.2 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.3 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.4 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.5 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.6 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.7 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.8 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.9 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.10 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.11 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.12 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.13 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.14 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.15 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.16 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.17 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.18 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.19 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.20 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.21 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.22 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.23 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.24 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.1.25 | [5 empty] | [Select Dropdown] | [Select Dropdown] |  | [Select Dropdown] | [Select Dropdown] | FALSE | FALSE
3.0.2 | Describe any supplemental heating/cooling systems installed:
[11 empty] | FALSE | FALSE | Phius
Notes:
3.1 | Heating/Cooling System - Indoor Component | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
3.1.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Manufacturer | Model# | Quantity | MERV Rating of Filter | Heating/Cooling System Type | Ducted or Non-Ducted? | Serves which Outdoor Unit? (select Tag Name)
3.1.1.1 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE | Phius
3.1.1.2 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.3 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.4 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.5 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.6 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.7 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.8 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.9 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.10 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.11 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.12 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.13 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.14 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.15 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.16 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.17 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.18 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.19 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.20 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.21 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.22 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.23 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.24 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.1.25 | [5 empty] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] |  |  | FALSE | FALSE
3.1.2 | Describe any supplemental heating/cooling systems installed:
[11 empty] | FALSE | FALSE | Phius
Notes:
3.2 | Heating/Cooling System - Fans associated with the ASHP System | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
3.2.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Manufacturer | Model# | Quantity | Fan Power Rating from Nameplate (Watts)
[5 empty] | Heating | Cooling2
3.2.1.1 | [10 empty] | FALSE | FALSE | Phius
3.2.1.2 | [10 empty] | FALSE | FALSE
3.2.1.3 | [10 empty] | FALSE | FALSE
3.2.1.4 | [10 empty] | FALSE | FALSE
3.2.1.5 | [10 empty] | FALSE | FALSE
3.2.2 | Review the ASHP Fan Schedule contained within the MEP drawings. Document any changes that have been made to the ASHP schedule since design, by identifying the manufacture, model, and power (wattage) of the new ASHP fan. | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
[11 empty] | FALSE | FALSE | Phius
3.2.3 | Provide Datasheet of ASHP pump manufacture and model that lists the Power (Watts) for fans associated with the Heating & Cooling system that are non-ducted or do not have energy efficiency data following AHRI Standard 1230. | [9 empty] | FALSE | FALSE | Phius
Notes:
3.3 | Heating/Cooling System - Pumps associated with the Ground Source or Hydronic System | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
3.3.1 | Tag Name (aligned with Mechanical Schedule, e.g., HP-1) | Manufacturer | Model# | Quantity | Pump Power
[5 empty] | Verified Flowrate (gal/min) | Head (ft) from Mechanical Schedule | Efficiency (%) from datasheet | Power Rating (Watts) | or | Power Rating (Watts) on pump nameplate
3.3.1.1 | [10 empty] | FALSE | FALSE | Phius
3.3.1.2 | [10 empty] | FALSE | FALSE
3.3.1.3 | [10 empty] | FALSE | FALSE
3.3.1.4 | [10 empty] | FALSE | FALSE
3.3.1.5 | [10 empty] | FALSE | FALSE
3.3.2 | Review the GSHP schedule contained within the MEP drawings. Document any changes that have been made to the GSHP schedule since design, by identifying the manufacture, model, and power (wattage) of the new pump. | [9 empty] | Verifier Confirmed | n/a | PROG. REQ.
[11 empty] | FALSE | FALSE | Phius
3.3.3 | Provide datasheet of GSHP pump manufacture and model that lists the Power (Watts), or Flow Rate, Head, and Efficiency for pumps associated with the Heating & Cooling system. | [9 empty] | FALSE | FALSE | Phius
Notes:
Footnotes:
1 Only one photo required per model number. Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."
2 If only Heating Wattage is given, enter the same value for Cooling as entered for Heating.

## 4-DHW
Phius MF Quality Assurance Workbook 4-Domestic Hot Water (DHW)
4 | DHW Water Heater | [11 empty] | Verifer Confirmed | n/a | PROG. REQ.
4.0.1 | Tag Name (aligned with Plumbing Schedule, e.g., WH-1) | Water Heater Type | Manufacturer |  | Model # | Quantity | Energy Star Certificate Uploaded?1 | Equipment & Nameplate Photos Uploaded?1
4.0.1.1 |  | [Select Dropdown] |  |  |  |  | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE | Phius
4.0.1.2 |  | [Select Dropdown] |  |  |  |  | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.0.1.3 |  | [Select Dropdown] |  |  |  |  | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.0.1.4 |  | [Select Dropdown] |  |  |  |  | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
Notes:
4.1 | DHW Storage Tank (if Applicable) | [11 empty] | Verifer Confirmed | n/a | PROG. REQ.
4.1.1 | Tag Name (aligned with Plumbing Schedule, e.g., WH-1) |  | Manufacturer |  | Model # | Quantity | Energy Star Certificate Uploaded?1 | Equipment & Nameplate Photos Uploaded?1
4.1.1.1 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE | Phius
4.1.1.2 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.1.1.3 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.1.1.4 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
Notes:
4.2 | DHW Swing Tank (if Applicable) | [11 empty] | Verifer Confirmed | n/a | PROG. REQ.
4.2.1 | Tag Name (aligned with Plumbing Schedule, e.g., WH-1) |  | Manufacturer |  | Model # | Quantity | Energy Star Certificate Uploaded?1 | Equipment & Nameplate Photos Uploaded?1
4.2.1.1 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE | Phius
4.2.1.2 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.2.1.3 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
4.2.1.4 | [6 empty] | [Select Dropdown] | [Select Dropdown] |  |  |  |  | FALSE | FALSE
Notes:
4.3 | DHW Pumps associated with DHW System (if Applicable) | [11 empty] | Verifer Confirmed | n/a | PROG. REQ.
4.3.1 | Tag Name (aligned with Plumbing Schedule, e.g., WH-1) | DHW Configuration | DHW Recirculation Types | Manufacturer | Model # | Quantity | Pump Power
[7 empty] | Verified Flow Rate (gal/min) | Head (ft) from Plumbing Schedule | Efficiency (%) from datasheet | Power Rating (Watts) | or | Power Rating (Watts) on pump nameplate
4.3.1.1 |  | [Select Dropdown] | [Select Dropdown] | [9 empty] | FALSE | FALSE | Phius
4.3.1.2 |  | [Select Dropdown] | [Select Dropdown] | [9 empty] | FALSE | FALSE
4.3.1.3 |  | [Select Dropdown] | [Select Dropdown] | [9 empty] | FALSE | FALSE
4.3.1.4 |  | [Select Dropdown] | [Select Dropdown] | [9 empty] | FALSE | FALSE
4.3.1.5 | Review the Pump Schedule contained within the MEP drawings. Document any changes that have been made to the pump schedule, by identifying the manufacture, model, and power (wattage) of the new pump. | [11 empty] | Verifer Confirmed | n/a | PROG. REQ.
[13 empty] | FALSE | FALSE | Phius
4.3.1.6 | Provide Datasheet of pump manufacture and model that lists the Power (Watts), or Flow Rate, Head, and Efficiency. | [11 empty] | FALSE | FALSE
Notes:
4.4 | DHW Delivery Verification | [11 empty] | Verifer Confirmed | n/a | PROG. REQ.
4.4.1 | Using the Field Verification method, no more than 2 gallons (7.6 liters) of water is collected from the furthest hot water fixture before hot water is delivered. Alternatively, once the water reaches 2 gallons (7.6 liters), the temperature of the water flow must increase by ≥ 10 °F in comparison of the final to the initial temperature reading. | [11 empty] | FALSE | FALSE | ENH
Notes:
4.5 | DHW Pipe insulation | [11 empty] | Verifer Confirmed | No
4.5.1 | Confirm DHW pipes are insulated. | [11 empty] | FALSE | FALSE | ENH
Notes:
Footnotes:
1Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."
2https://www.ahrinet.org/search-standards/ahri-1230-i-p-performance-rating-variable-refrigerant-flow-vrf-multi-split-air-conditioning-and-heat

## 5-Appliances & Electrical Loads
Phius MF Quality Assurance Workbook 5-Appliances & Electrical Loads
5 | Appliances
5.0.1 | Refrigerators, Freezers, Wine Coolers
| Manufacturer | Model # | Location |  | Quantity | Appliance & Nameplate Photos Uploaded?1 | Energy Star Certificate Uploaded?1 | Verifier Confirmed | Prog Req.
5.0.1.1 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE | ENH
5.0.1.2 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE
5.0.1.3 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE
5.0.1.4 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE
5.0.1.5 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE
5.0.1.6 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE
5.0.2 | Dishwashers
| Manufacturer | Model # | Location |  | Quantity | Appliance & Nameplate Photos Uploaded?1 | Energy Star Certificate Uploaded?1 | Verifier Confirmed | Prog Req.
5.0.2.1 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE | ENH
5.0.2.2 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE
5.0.3 | Clothes Washers
| Manufacturer | Model # | Location |  | Quantity | Appliance & Nameplate Photos Uploaded?1 | Energy Star Certificate Uploaded?1 | Verifier Confirmed | Prog Req.
5.0.3.1 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE | ENH
5.0.3.2 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE
5.0.4 | Clothes Dryers
| Manufacturer | Model # | Location | Fuel Type | Quantity | Appliance & Nameplate Photos Uploaded?1 |  | Verifier Confirmed | Prog Req.
5.0.4.1 |  |  |  | [Select Dropdown] |  | [Select Dropdown] |  | FALSE | ENH
5.0.4.2 |  |  |  | [Select Dropdown] |  | [Select Dropdown] |  | FALSE
5.0.5 | Range/Oven Combinations
| Manufacturer | Model # | Location | Fuel Type | Quantity | Appliance & Nameplate Photos Uploaded?1 |  | Verifier Confirmed | Prog Req.
5.0.5.1 |  |  |  | [Select Dropdown] |  | [Select Dropdown] |  | FALSE | Phius
5.0.5.2 |  |  |  | [Select Dropdown] |  | [Select Dropdown] |  | FALSE
5.0.6 | Wall Ovens
| Manufacturer | Model # | Location | Fuel Type | Quantity | Appliance & Nameplate Photos Uploaded?1 |  | Verifier Confirmed | Prog Req.
5.0.6.1 |  |  |  | [Select Dropdown] |  | [Select Dropdown] |  | FALSE | Phius
5.0.6.2 |  |  |  | [Select Dropdown] |  | [Select Dropdown] |  | FALSE
5.0.7 | Cooktops
| Manufacturer | Model # | Location | Fuel Type | Quantity | Appliance & Nameplate Photos Uploaded?1 |  | Verifier Confirmed | Prog Req.
5.0.7.1 |  |  |  | [Select Dropdown] |  | [Select Dropdown] |  | FALSE | Phius
5.0.7.2 |  |  |  | [Select Dropdown] |  | [Select Dropdown] |  | FALSE
5.0.10 | Miscellaneous
| Manufacturer | Model # | Location | Fuel Type | Quantity | Appliance & Nameplate Photos Uploaded?1 | Energy Star Certificate Uploaded?1 | Verifier Confirmed | Prog Req.
5.0.10.1 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE | Phius
5.0.10.2 | [5 empty] | [Select Dropdown] | [Select Dropdown] | FALSE
5.1 | Additional Major Electrical/Other Loads
5.1.1 | Describe any other additional significant energy uses loads on the property, including items like pools, hot tubs, home automation systems, fire pits, etc. | [6 empty] | Verifier Confirmed | Prog Req.
[8 empty] | FALSE | Phius
Notes:
Footnotes:
1Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."

## 6-Renewables & Electrification
Phius MF Quality Assurance Workbook 6-Renewables & Electrification
6 | Renewable Energy Systems | [6 empty] | Array Photos Uploaded?1 | Verifier Confirmed | N/A | PROG. REQ.
6.0.1 | Solar thermal system installed? |  | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Manufacturer and Model: | [Select Dropdown] | FALSE | FALSE | N/A
6.0.2 | Solar photovoltaic system installed? | [7 empty] | FALSE | FALSE | N/A
| A | Array 1 | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Peak production (W): | [Select Dropdown] | FALSE |  | N/A
| B | Array 2 | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Peak production (W): | [Select Dropdown] | FALSE
| C | Array 3 | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Peak production (W): | [Select Dropdown] | FALSE
| D | Array 4 | [Select Dropdown] | Area: | Orientation°: | Tilt°: | Peak production (W): | [Select Dropdown] | FALSE
6.1 | Electric Vehicle (EV) Charging Infrastructure1 | [7 empty] | Verifier Confirmed | N/A | PROG. REQ.
6.1.1 | Electric Vehicle (EV) Charging Infrastructure complies with the U.S. DOE Efficient New Homes Multifamily EV-Ready Checklist Version 2 or newer. | [7 empty] | FALSE |  | ENH
Notes:
#REF!
#REF!
#REF!
Footnotes:
1Please place any Photos, Energy Star Certificates, AHRI Certificates, Manufacturer's Technical Datasheets, or Submittals in the corresponding appliance's/equipment's folder: "4. On-Site Verification / 3. Photos."

## Update Page
Workbook updates:
v1.1 - 2/3/17: Updated kitchen exhaust criteria, spelling updates, added solar/renewable ready criteria.
v2.2 - 2/9/19: Updated for PHIUS+ 2018 Standards, Footnote (2)
v2.3 - 2/20/2020: Updated for EPA Energy Star MFNCP
v2.3 - 7-20-2021: Updates for current RESNET Standards and Energy Star MFNCP
v2.3 - 01-06-2022: Various wording and formatting updates
v2.3 - 09-26-2022: Alignment with Phius 2021. Electrification Readiness, Electric Vehicle Readiness Requirements, Re-organized Building Envelope, Heat+Cool, and Ventilation tabs, DHW temperature rise sampling table added.
v2.3.1 - 01-26-2023: Updates to the 'Ventilation'. Corrections made to 'pass' and 'fail' criteria for ventilation rates on individual rooms.
v2.3.2 - 04-17-2023: Updates to the 'Ventilation'. Corrections made to 'pass' and 'fail' criteria for Bedroom Pressure Difference inputs. Also updated 'pass' and 'fail' criteria for Heat + Cool for ducted systems.
v2.3.3 - 05-16-2023: Updated formulas for the preliminary blower door test on the 'Building Envelope' tab.
3.0.1 (3-4-14)
1) Ventilation - cells AB42, AC42, AB51, AC51 - added formula to sum the individual branch measurements for reference only
2) Ventilation - cell AF2 - added comment describing the "in balance" specification (+/-20% or 5cfm, whichever is greater)
3) DHW+Lights+Appliances - added item #3 for DHW model #, AHRI certificate and photo
4) Renewable Energy Ready - For item #1, updated the PV Watts hyperlink to the new PV Watts site…and added screen shot examples over to the right from PV Watts
5) Heating-Cooling: added note to item 1 "HVAC installer is required to be an accredited installer approved by Energy Star (for example, ACCA) if the heating or cooling system is a split air conditioner, unitary (packaged outside) air conditioner, air-source heat pump, water/ground source ("geothermal") heat pump up to 65,000Btu/hr with a ducted distribution system or a furnace up to 225,000Btu/hr with a ducted distribution system. All other permutations of equipment (e.g. boilers, mini-split / multi-split systems) and distribution systems are exempt."
3.0.2 (3-13-14)
1) Added more footnotes to Building Envelope 6.2 and 6.3
4.0.2 (5/18/17)
1) Totally revamped workbook to reflect newest ENERGY STAR, IAP and ZERH requirements
4.0 (8/10/17)
1) Requirement to supply fresh air to all bedrooms
2) Revised the previous 10' requirement for 'stretched string' distance between exhaust/supply ports on exterior of building. Now, recommend 10', requirement is a minimum 5' separation but must follow manufacturer's recommendations.
4.1 (1/2019)
1) Updated entire workbook to coincide with PHIUS 2018 Standard; Energy Star V3.1, Rev09; Indoor AirPLUS v1, Rev04 & DOE ZERH Requirements
4.2 (7/2021)
1) Updated to add Electric Vehicle Readiness Checklist items
2) Updated to add Electrification Readiness Checklist items
3) Updated to Phius Certified Rater/Verifier from PHIUS+ Rater/Verifier
4) Updated to align with ENERGY STAR v3.1 (Rev11)
5) Aligned Ventilation tab limits with those outlined in the Guidebook in terms of tolerance and allowed difference in measured vs planned ventilation rates
4.2.1 (5/2023)
1) Revised Intro page layout
2) Revised Building Envelope section for blower door testing inputs
3) Added ability to include multiple ventilation systems and aligned tab limits with those outlined in the guidebook.
24.1.0 (7/2024)
Removed co-requisite requirements, where possible, to streamline the Workbook.
24.1 (8/2024)
1) Updated entire Workbook to coincide with Phius 2024 Standard; Energy Star MFNC v3.2, Indoor AirPLUS v1, REV04 & DOE ZERH Multifamily Version 2 Requirements
26.1 (5/2026)
| 1 | Tab 0 - Key documents. Added 0.1.3.1 If Multifamily, provide Whole Building Blower Door Testing Plan. 0.1.3.1 was made a Phius requirement.
| 2 | Tab 0 - Key documents. Added "For duplexes and townhomes" to 0.3.3 For duplexes and townhomes: Provide Energy Star SFNH National HVAC Commissioning Checklist, Version 3 / 3.1 / 3.2 (Rev. 13), and all items under line 4, "Air Balancing of Supply Registers & Return Grilles," are required.
| 3 | Tab 0 - Key documents. Deleted 0.3.4 If Energy Star Multifamily New Construction (MFNC): All items under Line 4, "Air Balancing of Supply Registers & Return Grilles," of the National HVAC Functional Testing Checklist, Version 1 / 1.1 / 1.2 (Rev. 04) are required.
| 4 | Tab 0 - Key documents. At all occurrences changed from, “Save photos in Section 4 of the Phius On-Site QA folder” to “Save photos into project folder: 4. PHIUS+ On-Site Verification.
| 5 | Tabs 2.1, 2.2, and 2.3 - Ventilation. Room type for exhaust airflow changed from "1/2 bath" to "Half-Bath, Toilet, Powder."
| 6 | Tabs 2.1, 2.2, and 2.3 - Ventilation. Equation for >= Minimum was corrected to remove equation to reference cells that were removed during the 24.1 update
| 7 | Tabs 2.1, 2.2, and 2.3 - Ventilation. The equation for" Within +5 cfm or + 20%" was changed to correct the multiple from 1.25 (25%) to 1.20 (20%).
| 8 | Tabs 2.1, 2.2, and 2.3 - Ventilation. The heading "Minimum" was changed for clarity to read ">= Minimum cfm (bath 20; kitchen 25).
| 9 | Tabs 2.1, 2.2, and 2.3 - Ventilation. A section for Ventilation Unit Total Airflow Rates (24/7) was inserted at sections 2.2.14, 2.2.15, and 2.3.13 at Tabs 2.1, 2.2, and 2.3. Each subsequent section was renumbered, correspondingly.
| 10 | Tab 0 - Key Documents. Line 0.6.4 Appendix N-13.3 (Renewable Energy) changed to N-4.3 (Off-Site Renewable Energy Requirements) to align with location and wording in the Guidebook.
| 11 | Tab 0 - Key Documents. Item 0.3.3 Inserted new line: Provide Heating & Cooling Testing and Balancing report for ducted heating and/or cooling systems. Phius, and renumbered this section.
| 12 | Tab 0 - Key Documents. Line 0.4.1 Changed "datasheet" to "Certificate"
| 13 | Tab 2.1, 2.2, 2.3 - Ventilation. Row: Supply Airflow (24/7) and Exhaust Airflow (24/7). Additional headings in these rows changed from "Status" to "Measured Airflow Status".
| 14 | Tab 6 - Renewables & Electrification. Section 6.1 Electric Vehicle Charging Infrastructure and line 6.1.1 has been added.
| 15 | Tab 1.1 - Building Envelope. All references made to "taped" were replaced with "durability" and "untaped" replaced with "operational".
| 16 | Tab 0 - Key Documents, Line 0.6.4 changed reference from Appendix N 13.3 to Appendix N 4.3
| 17 | Tab 4 - Domestic Hot Water. Added Section 4.1 for Domestic Hot Water Systems Storage Tank and Section 4.2 Domestic How Water Systems - Swing Tank (if Applicable).
| 18 | Tab 3 - Heating & Cooling - Added Footnote: Only one photo required per model number.
| 19 | Tab 5 - Appliances & Electrical Loads. 5.08 Range hoods. Added column: If Direct Exhaust Measured Exhaust Airflow at median cfm
| 20 | All tabs - changed references to DOE Zero Energy Home program (ZERH) to DOE Efficient New Homes program, and changed all acronyms from ZERH to DOE.
| 21 | Cover Sheet - Changed the Tab Names in the table "Responsible parties from completion" to include shortened descriptions.
| 22 | All Tabs - changed the tab name to a shortened description to match what was shown on Cover Sheet.
| 23 | Cover Sheet - added a naming convention under which files could be saved.
| 24 | Coversheet - added a dropdown to distinguish if project was reviewed by a Verifier with MF designation, or a Rater.
| 25 | Entire Workbook-changed color scheme to align with Phius standard colors
| 26 | Cover Sheet - Co-requisite Programs - added "compliance" option for non-US projects
| 27 | Cover sheet - changed the order and moved paragraph "Using This Workbook" in front of paragraph "Certification Criteria"
| 28 | Cover Sheet - clarified that either the SF or the MF QA Workbook can be used on a Townhouse project.
| 29 | Key Docs - Building Envelope. Combined 0.1.1.1 and 0.1.1.2 to: "Provide technical datasheets of any insulation type installed that was not uploaded to folder:"
| 30 | Key Docs - Building Envelope. Added requirement, "Provide Whole Building Blower Door Testing Plan if building is a duplex or townhouse."
| 31 | Key Docs - Removed all references to Multifamily projects to the MF QA Workbook.
| 32 | Key Docs - Added requirement to provide reflected ceiling plans if using custom lighting power densities.
| 33 | Cover Sheet - Added option to select "Performance" or "Prescriptive", depending on the Certification Path chosen.
| 34 | AirTight WB - Added option to connected to the CoverSheet, so when Performance Path is selected, the airtightness standard in 0.06 cfm50/ft2, and 0.04 cfm50/ft2 when Prescriptive Path is selected.
| 35 | Removed references to "taped" and "untaped" tests, and replaced these terms with "Durability" and "Operational", respectively.
| 36 | Vent ERV_HRV - Changed the format of this page to group all supply airflows and all exhaust airflows, and moved all Auxiliary supply only or exhaust only airflows to a separate tab, 2.2.
| 37 | Vent ERV_HRV - Added section for dehumidifier, if applicable.
| 38 | Vent ERV_HRV - Moved direct exhaust range fans from the Appliances & Electrical Loads tab to the Vent ERV_HRV tab.
| 39 | Vent Auxiliary - added option for make-up air supply or exhaust fan only as dropdown options.
| 40 | Heat & Cool - Divided worksheet into section for outdoor component and another section for indoor component, and added sections for ASHP fans and GSHP pumps.
| 41 | DHW - Added sections for DHW Storage Tank, DHW Swing Tank, DHW Delivery Verification, and DHW Pipe Insulation
| 42 | Appliances & Electrical Loads - Revised Page Layout. Range hood and Dehumidifier moved to Vent ERV_HRV tab.
| 43 | Renewables & Electrification - Added Photo confirmation for each Solar PV array.
| 44 | Renewables & Electrification - Removed Section 6.03 HERS® Index, as this section only applies to whole dwelling, single-family projects.
| 45 | Added header on each Worksheet as a legend to show: "required input cells", "select best option", "notes/Instructions", and "calculations"
| 46 | Building Envelope - Compartmentalization tab deleted from Workbook (Covered through the Energy Star Program)
| 47 | Ventliation Tabs: Centralized, Decentralized Dwelling Unit, Decentralized Common were combined as dropdown selections within tab Vent ERV_HRV.
26.2 (7/2026)
| 1 | Coversheet: Changed definition of multifamily projects to exclude "or townhouse": Multifamily projects are defined as anything residential other than "single-family" or "duplex" or "townhouse" and include residential or commercial dormitories, and the residential part of a mixed-use building. [Townhouse projects will use the SF QA Workbook]
| 2 | Coversheet: Deleted footnote 6 which referenced Townhouse projects. Changed footnotes 7,8 to footnotes 6,7

## Dropdown menus (hidden)
Cover Sheet |  |  | 1-Building Envelope (WB) | 2.1-Vent ERV_HRV | 2.2-Vent Exhaust Only | 3-Heating & Cooling | 4-Domestic Hot Water | 5-Appliances & Electrical Loads | 6-Renewables & Electrification
Country | State | Project Path | Building Height | ERV/HRV Types | Room Type | Heating/Cooling System Type | Hot Water System Type | Photos Uploaded | Solar Thermal Installed
[Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown] | [Select Dropdown]
United States | AK Alaska | Performance | Yes | Centralized - Common Spaces Only | Kitchen | air source heat pump | none | Yes | Yes
Canada | AL Alabama | Prescriptive | No | Centralized - Sleeping Units Only | Other | water source heat pump | HPWH (inside) | N/A | No
Mexico | AR Arkansas |  |  | Centralized - Common Spaces & Sleeping Units |  | ground source heat pump | HPWH (outside)
Afghanistan | AS American Samoa |  |  | Decentralized - Common Spaces Only |  | fan coil | Electric (tanked) | Energy Star Certificate Uploaded
Albania | AZ Arizona | Certification Path | Durability Test | Decentralized - Dwelling Units Only | Air Flow Type | furnace | Electric (tankless) | [Select Dropdown] | Solar Photovoltaic Installed
Andorra | CA California | [Select Dropdown] | [Select Dropdown] | Decentralized - Common Spaces & Dwelling Units | [Select Dropdown] | hydronic | Gas (tanked) | Yes | [Select Dropdown]
Angola | CT Connecticut | Phius CORE 2021 | Yes |  | Continuous |  | Gas (tankless) | N/A | Yes
Argentina | DC District of Columbia | Phius CORE 2024 | No |  | Intermittent |  |  |  | N/A
Armenia | DE Delaware | Phius ZERO 2021 |  | Vent System Type |  | Ducted/Non-Ducted
Australia | FL Florida | Phius ZERO 2024 |  | [Select Dropdown] |  | [Select Dropdown] | Energy Star Certificate | Clothes Dryer Fuel Type
Azerbaijan | GA Georgia |  |  | HRV | Conditioned Space? | Ducted | [Select Dropdown] | [Select Dropdown] | Photos Uploaded
Bahamas, The | HI Hawaii |  |  | ERV | [Select Dropdown] | Non-Ducted | Yes | Electric Heat Pump | [Select Dropdown]
Bahrain | IA Iowa | Rater or Verifier |  | Integrated | Yes | Mixed Ducted & Non-Ducted | N/A | Electric Condensing | Yes
Bangladesh | ID Idaho | [Select Dropdown] |  |  | No |  |  | Electric Exhaust Vented | N/A
Barbados | IL Illinois | Verifier (MF) | [5 empty] | Gas Exhaust Vented
Belgium | IN Indiana | Rater |  | ERV/HRV Defrost |  | Individual/Shared | Photos Uploaded
Benin | KS Kansas |  |  | [Select Dropdown] | Exhaust Hood Type | [Select Dropdown] | [Select Dropdown] | Range/Oven, Wall Oven Fuel Type
Bhutan | KY Kentucky |  |  | n/a | [Select Dropdown] | Individual | Yes | [Select Dropdown]
Bolivia | LA Louisiana |  |  | Electric | Direct Exhaust | Shared | N/A | Electric
Bosnia & Herzegovina | MA Massachusetts | Ducted heating/cooling |  | Hot Water Loop | Recirculation |  |  | Gas
Botswana | MD Maryland | [Select Dropdown] |  | Ground Loop
Brunei | MI Michigan | Yes |  | Earth Tube |  | AHRI Certificate Uploaded | DHW Configuration
Bulgaria | MN Minnesota | No |  |  | Equipment & Nameplate Photos Uploaded? | [Select Dropdown] | [Select Dropdown] | Cooktop Fuel Type
Burkina Faso | MO Missouri |  |  |  | [Select Dropdown] | Yes | Centralized | [Select Dropdown]
Burma | MS Mississippi |  |  | Airflows Measured by | Yes | N/A | Decentralized | Electric Induction
Burundi | MT Montana | Functional Testing Agent |  | [Select Dropdown] | N/A |  |  | Electric Resistance
Cambodia | NC North Carolina | [Select Dropdown] |  | Verifier |  |  |  | Gas
Cameroon | ND North Dakota | Credentialed per listing on www.energystar.gov/ftas |  | TAB Contractor, Verifier Observed |  | Photos Uploaded | DHW Recirculation Types
Cape Verde | NE Nebraska | Licensed Professional Mechanical Engineer |  |  | Auxiliary Supply Ventilation System Type | [Select Dropdown] | [Select Dropdown]
Cayman Islands | NH New Hampshire | Representative of the Original Equipment Manufacturer (OEM) |  |  | [Select Dropdown] | Yes | None
Central African Rep. | NJ New Jersey |  |  | Space Unit Type | Supply: Make-up Air | N/A | Continuous
Chad | NM New Mexico |  |  | [Select Dropdown] | Supply: Miscellaneous |  | Time based only
Chile | NV Nevada | Energy Star (Multifamily) |  | Studio | Exhaust: Trash Room |  | Temperature based only
China | NY New York | [Select Dropdown] |  | 1 Bdrm | Exhaust: Compactor Room |  | Temperature & Time based
Colombia | OH Ohio | National Program, Version 1.2 |  | 2 Bdrm | Exhaust: Computer Room |  | On Demand (adaptive/smart, occupancy sensor or occupant control)
Comoros | OK Oklahoma | National Program, Version 1.3 |  | 3 Bdrm | Exhaust: Elevator Machine Room
Congo, Dem. Rep. | OR Oregon | California Program, Version 1.4 |  | 4 Bdrm | Other
Congo, Repub. of the | PA Pennsylvania | California Program, Version 1.5 |  | 5 Bdrm |  |  | Tube Size (inches)
Cook Islands | PR Puerto Rico | n/a |  | Common Space |  |  | [Select Dropdown]
Costa Rica | RI Rhode Island | [5 empty] | < 1.5 inches
Cote d'Ivoire | SC South Carolina | [5 empty] | ≥ 1.5 inches
Croatia | SD South Dakota | Indoor Air Plus |  | Room Type - Supply
Cuba | TN Tennessee | [Select Dropdown] |  | [Select Room Type - Supply]
Cyprus | TX Texas | Indoor AirPlus Version 1, Rev.4 |  | Bedroom |  |  | Insulation Thickness
Czech Republic | UT Utah | Indoor AirPlus Version 2, Certified |  | Living Room |  |  | [Select Dropdown]
Denmark | VA Virginia | Indoor AirPlus Version 2, Gold |  | Dining Room |  |  | 1.5" (or R-10 minimum)
Djibouti | VT Vermont | n/a |  | Corridor |  |  | 2.0" (or R-12 minimum)
Dominica | WA Washington |  |  | Multipurpose
Dominican Republic | WI Wisconsin |  |  | Office
East Timor | WV West Virginia | ENH Program Version (MF) |  | Other
Ecuador | WY Wyoming | [Select Dropdown]
Egypt |  | Multifamily National Program Version 2
El Salvador | AB Alberta | Multifamily for California Program Version 2 |  | Room Type - Exhaust
Equatorial Guinea | BC British Columbia | n/a |  | [Select Room Type - Exhaust]
Eritrea | MB Manitoba |  |  | Bathroom
Estonia | NB New Brunswick |  |  | Half-Bath, Toilet, Powder
Ethiopia | NF Newfoundland |  |  | Kitchen
Faroe Islands | NT Northwest Territories |  |  | Laundry
Fiji | NU Nunavut |  |  | Trash
Finland | NS Nova Scotia |  |  | Mechanical
France | ON Ontario |  |  | Other
French Guiana | PE Prince Edward Island
French Polynesia | QC Quebec
Gabon | SK Saskatchewan |  |  | Project team has demonstrated the ground loop / earth tube control logic is set up properly.
Gambia, The | YT Yukon |  |  | [Select Dropdown]
Gaza Strip |  |  |  | Yes
Georgia |  |  |  | N/A
Germany
Ghana
Gibraltar |  |  |  | Equipment & Nameplate Photos Uploaded?
Greece |  |  |  | [Select Dropdown]
Greenland |  |  |  | Yes
Grenada |  |  |  | N/A
Guadeloupe
Guam
Guatemala
Guernsey
Guinea
Guinea-Bissau
Guyana
Haiti
Honduras
Hong Kong
Hungary
Iceland
India
Indonesia
Iran
Iraq
Ireland
Isle of Man
Israel
Italy
Jamaica
Japan
Jersey
Jordan
Kazakhstan
Kenya
Kiribati
Korea, North
Korea, South
Kuwait
Kyrgyzstan
Laos
Latvia
Lebanon
Lesotho
Liberia
Libya
Liechtenstein
Lithuania
Luxembourg
Macau
Macedonia
Madagascar
Malawi
Malaysia
Maldives
Mali
Malta
Marshall Islands
Martinique
Mauritania
Mauritius
Mayotte
Micronesia, Fed. St.
Moldova
Monaco
Mongolia
Montserrat
Morocco
Mozambique
Namibia
Nauru
Nepal
Netherlands
Netherlands Antilles
New Caledonia
New Zealand
Nicaragua
Niger
Nigeria
N. Mariana Islands
Norway
Oman
Pakistan
Palau
Panama
Papua New Guinea
Paraguay
Peru
Philippines
Poland
Portugal
Puerto Rico
Qatar
Reunion
Romania
Russia
Rwanda
Saint Helena
Saint Kitts & Nevis
Saint Lucia
St Pierre & Miquelon
Saint Vincent and the Grenadines
Samoa
San Marino
Sao Tome & Principe
Saudi Arabia
Senegal
Serbia
Seychelles
Sierra Leone
Singapore
Slovakia
Slovenia
Solomon Islands
Somalia
South Africa
Spain
Sri Lanka
Sudan
Suriname
Swaziland
Sweden
Switzerland
Syria
Taiwan
Tajikistan
Tanzania
Thailand
Togo
Tonga
Trinidad & Tobago
Tunisia
Turkey
Turkmenistan
Turks & Caicos Is
Tuvalu
Uganda
Ukraine
United Arab Emirates
United Kingdom
Uzbekistan
Vanuatu
Venezuela
Vietnam
Virgin Islands
Wallis and Futuna
West Bank
Western Sahara
Yemen
Zambia
Zimbabwe

## Templates (hidden)
Data entry cells are in blue. Checkbox cells are in teal and white. Notes cells are in light gray. Calculation cells are in lime. Do not change the calculation cells!
|  | Required input cells | Select best option | Notes / Instructions / Units | Calculations (do not change)
[Select Dropdown]
[Select Dropdown]
Conditional Formatting:
|  | #E5B8B7 |  | Fail
|  | #C2D69B |  | Pass
Ventilation Tab:
|  | #3D65A5 |  | Supply | https://www.datylon.com/blog/data-visualization-for-colorblind-readers#color-blind-palette
|  | #F05039 |  | Exhaust | https://www.datylon.com/blog/data-visualization-for-colorblind-readers#color-blind-palette

## Data entry Instr. (hidden)
Template for Cover Sheet, row 52:
Data entry cells are in blue. Checkbox cells are in teal and white. Notes cells are in light gray. Calculation cells are in lime. Do not change the calculation cells!
|  | Required input cells | Select best option | Notes / Instructions / Units | Calculations (do not change)
[Select Dropdown]
[Select Dropdown]
Colors
#B5E3E8
#DFFD61
|  | #3D65A5 |  | https://www.datylon.com/blog/data-visualization-for-colorblind-readers#color-blind-palette
|  | #F05039 |  | https://www.datylon.com/blog/data-visualization-for-colorblind-readers#color-blind-palette
#E5B8B7
#C2D69B